## Slide 1
ERCOT Update on UFLS Annual Survey with TSP/DSP
July 2015

## Slide 2: Background on UFLS Survey Requirement
ERCOT coordinated and conducted an annual survey on May 12, 2015 with the TSPs and DSPs to ensure that the required automatic under-frequency load shed circuits were configured to provide the appropriate load relief in an under-frequency event as required by table below from Operating Guides 2.6.1(1) Requirements for Under-Frequency Load Shedding:

## Slide 3: Results of UFLS Survey Requirement
Below is a list of dates and activities reflecting the timeline and coordination of this survey:
02/19/2015 - ERCOT announcement of survey timeline and effort to OWG
04/14/2015 - ERCOT email notification sent by Client Services to TSP/DSP Authorized Representatives
05/12/2015 @ 11:00 AM- Date and time of the Survey
06/12/2015 - Survey results due back to ERCOT
July/August - Results compiled and being reported to OWG/ROS/TAC
Notes: Weather 5/12/2015 at 11:00 was mild again this year.

## Slide 4: Execution of UFLS Survey Requirement
The results of the 2015 requirement were successful and are reflected below:
Frequency response block | Minimum Requirement | Survey measurement
Block 1 response at 59.3 | 5% | 6.98%
Block 2 response at 58.9 | 10% | 11.94%
Block 3 response at 58.5 | 10% | 12.30%
Total | 25% | 31.23%
ERCOT Reliability and Compliance did not have to contact any participants to request that their 5%, 10%, 10% breakdown be adhered to. All participants met the 25% total and had the proper load in the 5% and the two 10% brackets.
In reference last year’s(2014) 25% total was 29.8%

## Slide 5: Execution of UFLS Survey Requirement
The survey submitted by the participants indicated that they all could meet the 25% minimum requirement with the proper 5%, 10%, and 10% distribution of the loads to be interrupted.