## Slide 1: Emerging Technologies Working Group Update to WMS
September 02, 2015
Contents
PVGR Forecasting Stats
Distributed Generation Outflow Report
Other Business: Requested Energy Storage Update
Next ETWG Meeting

## Slide 2: I. PVGR Forecasting Stats

## Slide 3: Three Hour Ahead
Chart: Error by MW Ranges
| <10 | 10<x<50 | 50<x<100 | 100< | 120<
Company A STPVPF | 0.027054 | 0.070253 | 0.095882 | 0.073793 | 0.073716
Company B STPVPF | 0.0071303 | 0.054836 | 0.095037 | 0.056158 | 0.034063
 | Company A STPVPF | Company A PVGRPP | Company B STPVPF | Company B PVGRPP
Average | 6.985% | 19.181% | 5.703% | 8.481%
Under | 7.321% | 20.269% | 4.253% | 9.450%
Over | -6.691% | -2.310% | -6.516% | -3.786%
Count Under | 220 | 459 | 172 | 390
Count Over | 290 | 29 | 329 | 111
Max | 26.712% | 41.647% | 30.227% | 32.349%
<10 | 2.52% | 1.56% | 0.66% | 0.68%
10<x<50 | 6.54% | 6.87% | 5.10% | 5.61%
50<x<100 | 8.92% | 17.58% | 8.84% | 9.62%
100< | 6.87% | 29.64% | 5.23% | 10.94%
120< | 6.86% | 33.34% | 3.17% | 9.28%
*Only forecasts where the real-time output above 0.5 MW were used.
Company B more accurate at high and low output.
Notes: <10 14%
10<x<50 13%
50<x<100 23%
100< 35%
120< 14%

## Slide 4: Six Hour Ahead
 | Company A STPVPF | Company A PVGRPP | Company B STPVPF | Company B PVGRPP
Average | 7.257% | 19.400% | 5.862% | 7.923%
Under | 7.583% | 20.613% | 4.052% | 8.859%
Over | -6.950% | -2.530% | -6.802% | -3.712%
Count Under | 228 | 456 | 164 | 385
Count Over | 282 | 31 | 337 | 116
Max | 26.738% | 41.300% | 26.695% | 30.120%
<10 | 2.71% | 1.75% | 0.68% | 0.65%
10<x<50 | 7.19% | 7.21% | 5.33% | 5.31%
50<x<100 | 9.43% | 18.25% | 9.13% | 9.26%
100< | 6.83% | 29.50% | 5.31% | 10.00%
120< | 6.32% | 32.88% | 3.29% | 9.07%
*Only forecasts where the real-time output above 0.5 MW were used.
Chart: Error by MW Ranges
| <10 | 10<x<50 | 50<x<100 | 100< | 120<
Company A STPVPF | 0.027127 | 0.071919 | 0.09429 | 0.068331 | 0.063195
Company B STPVPF | 0.0067692 | 0.05334 | 0.091332 | 0.053109 | 0.032901
Notes: <10 14%
10<x<50 13%
50<x<100 23%
100< 35%
120< 14%

## Slide 5: Day Ahead
 | Company A STPVPF | Company A PVGRPP | Company B STPVPF | Company B PVGRPP
Average | 7.281% | 19.684% | 5.671% | 8.043%
Under | 7.370% | 20.873% | 4.204% | 8.845%
Over | -7.183% | -3.113% | -6.381% | -4.117%
Count Under | 237 | 441 | 151 | 377
Count Over | 256 | 30 | 334 | 108
Max | 25.620% | 41.086% | 29.690% | 32.773%
<10 | 3.08% | 2.03% | 0.65% | 0.74%
10<x<50 | 7.23% | 7.11% | 4.74% | 5.87%
50<x<100 | 8.90% | 18.10% | 8.63% | 9.91%
100< | 7.14% | 30.02% | 5.54% | 9.66%
120< | 7.26% | 33.80% | 3.06% | 9.78%
*Only forecasts where the real-time output above 0.5 MW were used.
Chart: Error by MW Ranges
| <10 | 10<x<50 | 50<x<100 | 100< | 120<
Company A STPVPF | 0.030826 | 0.072257 | 0.089043 | 0.071434 | 0.072575
Company B STPVPF | 0.0065266 | 0.047405 | 0.086292 | 0.055372 | 0.030556
Notes: <10 14%
10<x<50 13%
50<x<100 23%
100< 35%
120< 14%

## Slide 6: STPVPF Comparison
 | Three Hour | Six Hour | Day Ahead
Company A | 6.985% | 7.257% | 7.281%
Company B | 5.703% | 5.862% | 5.671%
Chart: 
| Company A | Company B
Three Hour | 0.06985 | 0.05703
Six Hour | 0.07257 | 0.05862
Day Ahead | 0.07281 | 0.05671
 | Three Hour | Six Hour | Day Ahead
Company A | 8.405% | 8.807% | 8.446%
Company B | 6.112% | 6.272% | 7.870%
Hours Ending 17-19
All Hours

## Slide 7: Sunrise & Sunset
 | Company A | Company B
Sunrise: HE7 | 0.31% | 0.07%
Sunset: HE21 | 5.09% | 0.71%
*Three hour ahead

## Slide 8: Bias
The following numbers are the percentage of forecasts that were under-forecasted.
 | Company A STPVPF | Company B STPVPF | Company A PVGRPP | Company B PVGRPP
Three Hour | 43% | 34% | 94% | 78%
Six Hour | 45% | 33% | 94% | 77%
Day Ahead | 48% | 31% | 94% | 78%

## Slide 9: Expected timeline for PVGRR forecast

## Slide 10: II. Distributed Generation Outflow Report

## Slide 12
Chart: Registered Distributed Generation
| Q1-2011 | Q2-2011 | Q3-2011 | Q4-2011 | Q1-2012 | Q2-2012 | Q3-2012 | Q4-2012 | Q1-2013 | Q2-2013 | Q3-2013 | Q4-2013 | Q1-2014 | Q2-2014 | Q3-2014 | Q4-2014 | Q1-2015 | Q2-2015
MWH | 150734.1724 | 150540.457 | 140592.8295 | 145338.1897 | 159120.5362 | 170834.8395 | 186493.225 | 178715.1509 | 173588.5022 | 181077.481 | 171304.7329 | 175411.3749 | 173652.5633 | 187405.7478 | 177518.9504 | 165667.6177 | 174190.7372 | 183841.1487
ERCOT PERCENTAGE (secondary axis) | 0.0020936 | 0.0017569 | 0.0013468 | 0.0020209 | 0.002297 | 0.0020077 | 0.0018972 | 0.0024715 | 0.0024768 | 0.0021822 | 0.0017052 | 0.0022431 | 0.0022358 | 0.0022555 | 0.0017519 | 0.0021231 | 0.0021956 | 0.0021666

## Slide 13
Chart: Registered Distributed Generation Capacity (MW)
| Q1-2011 | Q2-2011 | Q3-2011 | Q4-2011 | Q1-2012 | Q2-2012 | Q3-2012 | Q4-2012 | Q1-2013 | Q2-2013 | Q3-2013 | Q4-2013 | Q1-2014 | Q2-2014 | Q3-2014 | Q4-2014 | Q1-2015 | Q2-2015
MW | 161 | 165 | 176 | 176 | 204 | 255 | 255 | 245 | 240 | 390 | 402 | 412 | 431 | 435 | 439 | 460 | 480 | 503

## Slide 14
Chart: Un-Registered Distributed Generation
| Q1-2011 | Q2-2011 | Q3-2011 | Q4-2011 | Q1-2012 | Q2-2012 | Q3-2012 | Q4-2012 | Q1-2013 | Q2-2013 | Q3-2013 | Q4-2013 | Q1-2014 | Q2-2014 | Q3-2014 | Q4-2014 | Q1-2015 | Q2-2015
MWH | 964.0631 | 1489.0021 | 1094.371 | 1283.9097 | 1832.1776 | 2483.825 | 2136.3805 | 2214.7214 | 2910.7471 | 3404.0114 | 2694.9122 | 2594.1426 | 3772.8048 | 5684.4002 | 4295.9692 | 5135.4618 | 6042.0609 | 7027.1712
ERCOT PERCENTAGE (secondary axis) | 1.339e-05 | 1.7378e-05 | 1.0484e-05 | 1.7853e-05 | 2.6448e-05 | 2.9191e-05 | 2.1733e-05 | 3.0628e-05 | 4.1532e-05 | 4.1022e-05 | 2.6826e-05 | 3.3173e-05 | 4.8575e-05 | 6.8415e-05 | 4.2396e-05 | 6.5812e-05 | 7.6159e-05 | 8.2817e-05

## Slide 15: III. Other Business: Requested Energy Storage Request
Some parties have expressed an interest in having ETWG do a “score-card” review of storage issues that have been addressed over the past few years, and those remaining to be addressed
Lack of certainty expressed by some may indicate a need to update the ERCOT website under Grid Information | Emerging Technology Tracking System
ETWG will welcome market participants that want to volunteer to present on these topics

## Slide 16: IV. Next ETWG Meeting September 17
Logistics
September 17, 1:00PM – 3:30PM
Room 206B
Note that this afternoon session follows the DSWG morning session
Agenda Items
Update on PVGR RFP
Energy Storage Discussion?
Other items as directed

## Slide 17: APPENDICES

## Slide 18: Requested WMS Motion
n/a