

**July 2015 ERCOT Monthly Operations Report**

**Reliability and Operations Subcommittee Meeting**

**September 3, 2015**

# Table of Contents

[1 Report Highlights 3](#_Toc427736354)

[2 Frequency Control 4](#_Toc427736355)

[2.1 Frequency Events 4](#_Toc427736356)

[2.2 Responsive Reserve Events 5](#_Toc427736357)

[2.3 Load Resource Events 5](#_Toc427736358)

[3 Reliability Unit Commitment 6](#_Toc427736359)

[4 Wind Generation as a Percent of Load 6](#_Toc427736360)

[5 Congestion Analysis 7](#_Toc427736361)

[5.1 Notable Constraints for July 7](#_Toc427736362)

[5.2 Generic Transmission Constraint Congestion 8](#_Toc427736363)

[5.3 Manual Overrides for July 8](#_Toc427736364)

[5.4 Congestion Costs for Calendar Year 2015 8](#_Toc427736365)

[6 System Events 9](#_Toc427736366)

[6.1 ERCOT Peak Load 9](#_Toc427736367)

[6.2 Load Shed Events 9](#_Toc427736368)

[6.3 Stability Events 9](#_Toc427736369)

[6.4 Notable PMU Events 10](#_Toc427736370)

[6.5 TRE/DOE Reportable Events 10](#_Toc427736371)

[6.6 New/Updated Constraint Management Plans 10](#_Toc427736372)

[6.7 New/Modified/Removed SPS 10](#_Toc427736373)

[6.8 New Procedures/Forms/Operating Bulletins 10](#_Toc427736374)

[7 Emergency Conditions 10](#_Toc427736375)

[7.1 OCNs 10](#_Toc427736376)

[7.2 Advisories 10](#_Toc427736377)

[7.3 Watches 10](#_Toc427736378)

[7.4 Emergency Notices 10](#_Toc427736379)

[8 Application Performance 11](#_Toc427736380)

[8.1 TSAT/VSAT Performance Issues 11](#_Toc427736381)

[8.2 Communication Issues 11](#_Toc427736382)

[8.3 Market System Issues 11](#_Toc427736383)

[9 Net-Forecast Bias Applied to NSRS Procurement for July 2015 11](#_Toc427736384)

[Appendix A: Real-Time Constraints 12](#_Toc427736385)

# Report Highlights

* The unofficial ERCOT peak for July was 67,624 MW. This was a record for the month of July.
* There were six frequency events in July. PMU data indicates the ERCOT system transitioned well in each case.
* There were six instances where Responsive Reserves were deployed, all of which were the result of frequency events.
* There were two RUC commitments in July. Both in the Southern region due to local congestion.
* The level of reportable SCED congestion increased in July. This congestion was due primarily to planned outages and area load/gen patterns. There were thirteen days of activity on the Zorillo - Ajo Generic Transmission Constraint (GTC) in July as well as one day on the North to Houston GTC.
* There were no significant system events for the month of July.
* ERCOT Applications performed well throughout the month. There were no ERCOT related application performance issues.
* Issued a new Generic Transmission Constraint due to outages in the panhandle region.
* 07/03/15 – ERCOTs initial indications showed approximately 317 MW tripped due to low voltage and loss of transmission southern region. This load was lost as a result of a multiple contingencies and NOT as a result of an ERCOT instruction.
* 07/29/15 – The simultaneous loss of three generators in the central region resulted in the loss of approximately 1507 MW.
* 07/30/15 - ERCOT issued a Media Appeal for energy conservation as a precautionary measure to ensure system reliability due to hot weather causing high ERCOT demands and reduced generation capability due to unplanned generation outages.

# Frequency Control

## Frequency Events


The ERCOT Interconnection experienced six frequency events in July, all of which resulted from Resource trips. The average event duration was approximately 0:04:39.

When analyzing frequency events, ERCOT evaluates PMU data according to industry standards. Events with an oscillating frequency of less than 1 Hz are considered to be inter-area, while higher frequencies indicate local events. Industry standards specify that damping ratio for inter-area oscillations should be 3.0% or greater. All events listed below indicate the ERCOT system met these standards and transitioned well after each disturbance.

Reported frequency events will include both frequency events where frequency was outside the range of 60±0.1 Hz as well as those determined to be Frequency Measurable Events (FME) as defined by BAL-001-TRE-1. Delta Frequency is defined as the difference between the pre-perturbation and post-perturbation frequency. The Duration of Event is defined as the time it takes for the frequency to recover to lesser/greater of the frequency at the time of the frequency event (*t(0)* or “A*-point*”) for low/high-frequency events, respectively. Further details on FMEs can be found in the MIS posted BAL-001-TRE-1 PDCWG Unit Performance reports. A summary of the frequency events is provided below:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Date and Time** | **Delta Frequency** | **Max/Min Frequency** | **Duration of Event** | **PMU Data** | | **Comments** |
| **(Hz)** | **(Hz)** | **Oscillation Mode (Hz)** | **Damping Ratio** |
| 7/1/2015 1:15 | 0.06 | 59.85 | 0:04:09 | 0.68 | 10% | Unit Trip of 748 MW |
| 7/5/2015 10:30 | 0.10 | 59.86 | 0:03:52 | 0.71 | 20% | Unit Trip of 845 MW |
| 7/19/2015 13:35 | 0.07 | 59.85 | 0:04:07 | 0.6 | 7% | Unit Trip of 683 MW |
| 7/21/2015 11:41 | 0.04 | 59.90 | 0:04:52 | PMU Data Not Available. | | Unit Trip of 430 MW |
| 7/21/2015 21:06 | 0.03 | 59.90 | 0:04:18 | PMU Data Not Available. | | Unit Trip of 447 MW |
| 7/29/2015 18:16 | 0.20 | 59.72 | 0:06:00 | 0.63 | 12% | Unit Trip of 1507 MW |

(Note: frequency events highlighted in blue have been identified as FMEs per BAL-001-TRE-1 and the Performance Disturbance Compliance Working group.)



Note on 07/29/15 – The simultaneous loss of three generators in the central region resulted in the loss of approximate 1507 MW.

## Responsive Reserve Events

There were five events where Responsive Reserve MWs were released to SCED in July. The events highlighted in blue were related to frequency events reported in section 2.1 above.

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Date and Time**  **Released to SCED** | **Date and Time**  **Recalled** | **Duration of Event** | **Maximum MWs Released** | **Comments** |
| 7/1/2015 1:15:14 | 7/1/2015 1:18:58 | 00:03:44 | 535.72 |  |
| 7/5/2015 10:30:34 | 7/5/2015 10:33:26 | 00:02:52 | 171.02 |  |
| 7/19/2015 13:35:36 | 7/19/2015 13:39:12 | 00:03:36 | 667.81 |  |
| 7/21/2015 11:42:08 | 7/21/2015 11:45:24 | 00:03:16 | 434.69 |  |
| 7/21/2015 21:06:28 | 7/21/2015 21:09:52 | 00:03:24 | 369.33 |  |
| 7/29/2015 18:16:50 | 7/29/2015 18:22:14 | 00:05:24 | 1364.74 |  |

## Load Resource Events

There were no load resource deployment events in July.


# Reliability Unit Commitment

ERCOT reports on Reliability Unit Commitments (RUC) on a monthly basis. Commitments are reported grouped by operating day and weather zone. The total number of hours committed is the sum of the hours for all the units in the specified region. Additional information on RUC commitments can be found on the MIS secure site at Grid 🡪 Generation 🡪 Reliability Unit Commitment.

There were no DRUC commitments in July.

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **HRUC Commitments** | | | | | |
| **Resource Location** | **# of Resources** | **Operating Day** | **Total # of Hours Committed** | **Total MWhs** | **Reason for commitment** |
| Southern | 2 | 7/5/2015 | 7 | 280 | Local Congestion |
| Southern | 1 | 7/17/2015 | 4 | 161 | Local Congestion |

# Wind Generation as a Percent of Load



# Congestion Analysis

The number of congestion events experienced by the ERCOT system increased in July due to planned outages and area load/gen patterns. There were fourteen days of activity on the Generic Transmission Constraints (GTCs) in July.

## Notable Constraints for July

Nodal protocol section 3.20 specifies that ERCOT shall identify transmission constraints that are active or binding three or more times within a calendar month. As part of this process, ERCOT reports congestion that meets this criterion to ROS. In addition ERCOT also highlights notable constraints that have an estimated congestion rent exceeding $1,000,000 for a calendar month. These constraints are detailed in the table below. Rows highlighted in blue indicate the congestion was affected by one or more outages. For a list of all constraints activated in SCED for the month of July, please see Appendix A at the end of this report.

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Contingency** | **Overload** | **# of Days Constraint Active** | **Estimated Congestion Rent** | **Transmission Project** |
| DCKT Flewellen - Obrien and Mason Road 138 kV | Hockley - Betka 138 kV | 8 | $7,352,306 | 3682A, 3682B May-17 |
| San Angelo North 138\_69T1 138/69kV | San Angelo College Hills 138\_69T1 138/69 kV | 6 | $6,609,018 | 3663 May-17 |
| San Angelo College Hills 138\_69T1 138/69 kV | SA Power 69T1 138/69 kV | 10 | $4,409,778 |  |
| DKCT Roans Prarie-Rothwood & Singleton-Tomball 345kV | Singleton - Zenith 345 kV (SNGZEN99) | 12 | $2,473,607 | 2013-R63 |
| San Angelo North 138\_69T1 138/69kV | SA Power 69T1 138/69 kV | 4 | $2,185,652 |  |
| Eagle Mountain SES - Parker Switch and Hicks Switch 345 kv | Calmont Switch - Western Hills 138 kV | 1 | $1,949,390 |  |
| Skidmore - Chase Field 69 kV | Orange Grove 69 Sub - Casa Blanca 69 kV | 5 | $1,662,002 | 16TPIT0037 |
| Euless - Liggett Switch 138 kV | Roanoke Switch - McPhereson 138 kV | 1 | $1,598,473 |  |
| La Palma - Rio Hondo 138 kV | Rio Hondo - East Rio Hondo 138 kV | 2 | $1,540,910 | 3267A Jun-15 |
| Lewisville Switch - Krum West Switch and Roanoke Switch 345 kV | Teasley Substaion - Pockrus Substation 138 k | 10 | $1,355,618 |  |
| Basecase | Zorillo - Ajo GTC | 22 | $607,124 |  |
| Lobo - San Miguel 345\_138 kV Switchyards 345 kV | Laquinta - Lobo 138 kV | 7 | $584,616 |  |
| DCKT Jewett - Singleton 345 kV | Twin Oak Switch - Btu\_Jack\_Creek 345 kV | 18 | $576,410 | 2013-R63 |
| Laquinta - Lobo 138 kV | Bruni 138\_69\_1 138/69 kV | 13 | $393,925 |  |
| DCKT Marion - Zorn and Clear Springs 345 kV | Comal - Loop 337 138 kV | 20 | $320,509 | 4464 Dec -15 |
| Riley - Tesla and Jim Treece 345 kV | Edith Clarke - Gauss 345 kV | 4 | $295,151 |  |
| DCKT Whitepoint - Lon Hill and South Texas Project 345 kV | Rincon - Bonnieview 69 kV | 7 | $185,840 |  |
| Basecase | Sinton - Skidmore 69 kV | 3 | $107,569 |  |
| Coleto Creek - Pawnee Switching Station 345 KV | Coleto Creek - Kenedy Switch 138 kV | 3 | $73,549 |  |
| DCKT Ferguson - Granite Mountain and Wirtz - Starcke - Paleface 138 kV | Wirtz - Flat Rock Lcra 138 kV | 11 | $69,620 | 4465 May-19 |
| Uvalde Aep - Odlaw Switchyard 138 kV | Hamilton Road - Maverick 138 kV | 3 | $48,595 | 16TPIT0024 May-18 |
| Laquinta - Lobo 138 kV | Falfurria 138/69 kV | 6 | $20,306 | 16TPIT0024 May-18 |

## Generic Transmission Constraint Congestion

There were thirteen days of activity on the Zorillo - Ajo GTC and one day on the North to Houston GTC in July. There was no activity on the remaining GTCs during the Month of July.

A new GTC for the panhandle was created July 31st 2015. This GTC has been created to address voltage stability concerns in the Panhandle that currently occur during transmission outages in the region. This GTC will also be used in the future to manage system strength issues in the Panhandle region if those system strength issues are more restrictive than the voltage stability limits.

## Manual Overrides for July

There were no manual overrides for the month of July 2015

## Congestion Costs for Calendar Year 2015

The following table represents the top twenty active constraints for the calendar year based on the estimated congestion rent attributed to the congestion. ERCOT updates this list on a monthly basis.

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Contingency** | **Binding Element** | **# of 5-min SCED Intervals** | **Estimated Congestion Rent** | **Transmission Project** |
| DKCT Roans Prarie - Rothwood & Singleton - Tomball 345 kV | Singleton - Zenith 345 kV | 2102 | $  20,279,531.83 | 2013-R63 |
| San Angelo North 138/69kV | San Angelo College Hills 138/69 kV | 1099 | $  13,957,273.25 | 3663 |
| Topeka Termination - West Levee Switch 345 kV | Cedar Hill Switch - Mountain Creek 138 kV | 275 | $    8,199,322.66 | 13TPIT0060 |
| San Angelo College Hills 138/69 kV | SA Power 138/69 kV | 1446 | $    7,978,305.53 |  |
| DCKT Hill Country - Marion and Elmcreek 345 kV | Marion - Skyline 345 kV | 1188 | $    7,610,819.02 | 4081 |
| DCKT Flewellen - Obrien and Maso Road 138 kV | Hockley - Betka 138 kV | 444 | $    7,352,306.17 | 3682A, 3682B |
| DCKT Lost Pines - Austrop & Dunlop 345 kV | Fayette Plant 1 - Fayette Plant 2 345 kV | 2972 | $    6,624,462.39 |  |
| Bevo Substation - Asherton 138 kV | Hamilton Road - Maverick 138 kV | 320 | $    6,277,749.92 | 16TPIT0024 |
| DCKT Jewett - Singleton 345 kV | Twin Oak Switch - Btu\_Jack\_Creek 345 kV | 4648 | $    6,150,063.48 |  |
| Orange Grove Switching Station - Lon Hill 138 kV | Lon Hill - Smith 69 kV | 4192 | $    6,052,131.26 | 16TPIT0026 |
| Los Fresnos - Loma Alta Substation 138 kV | La Palma - Villa Cavazos 138 kV | 587 | $    5,485,885.25 |  |
| Hutto Switch Axfmr 1 345/138 kV | Gilleland - Pflugerville 138 kV | 565 | $    5,340,238.22 | 16TPIT0062 |
| Rio Hondo Axfmr 345/138 kV | Aderhold - Elsa 138 kV | 121 | $    4,745,657.61 |  |
| Falcon Seaboard - Midland East 345 kV | Odessa to Glenhaven 138 kV | 70 | $    4,268,830.85 | 4173 |
| DCKT West Levee Switch - 800/900 Network 138 kV | East Levee Switch - Reagan Street 138 kV | 366 | $    4,170,639.70 | 2014-NC28 |
| Bates - Frontera 138 kV | Frontera - Goodwin 138 kV | 249 | $    4,074,787.83 |  |
| Falcon Seaboard - Morgan Creek Ses 345 KV | Glenhaven - Crmwd 8 Tap 138 kV | 65 | $    4,063,954.92 | 4173 |
| DCKT Calaveras - Hotwells & Laredo1 138 kV | Calaveras - Streich 138 kV | 737 | $    3,750,145.76 | 16TPIT0011 |
| South Mission to Frontera 138/138 kV | South Mission to Frontera 138/138 kV | 70 | $    3,335,332.47 |  |
| Eagle Mountain SES - Parker Switch and Hicks Switch 345 kV | Calmont Switch - Western Hills 138 kV | 77 | $    3,180,678.24 |  |

# System Events

## ERCOT Peak Load

The unofficial ERCOT peak load for the month was 67,630 MW and occurred on July 30th during hour ending 17:00.

## Load Shed Events

07/03/15 – ERCOTs initial indications showed approximately 317 MW tripped due to low voltage and loss of transmission southern region. This load was lost as a result of a multiple contingencies and NOT as a result of an ERCOT instruction.

## Stability Events

None.

## Notable PMU Events

ERCOT analyzes PMU data for any significant system disturbances that do not fall into the Frequency Events category reported in section 2.1. The results are summarized in this section once the analysis has been completed.

There were no reportable events in July.

## TRE/DOE Reportable Events

07/03/15 – ERCOTs initial indications showed approximately 317 MW tripped due to low voltage and loss of transmission southern region. This load was lost as a result of a multiple contingencies and NOT as a result of an ERCOT instruction.

07/29/15 – The simultaneous loss of three generators in the central region resulted in the loss of approximately 1507 MW.

07/30/15 - ERCOT issued a Media Appeal for energy conservation as a precautionary measure to ensure system reliability due to hot weather causing high ERCOT demands and reduced generation capability due to unplanned generation outages.

## New/Updated Constraint Management Plans

None.

## New/Modified/Removed SPS

None.

## New Procedures/Forms/Operating Bulletins

None.

# Emergency Conditions

## OCNs

|  |  |
| --- | --- |
| **Date and Time** | **Description** |
| 07/30/15 06:36 | ERCOT issued an OCN due a capacity insufficiency. |
| 07/31/15 15:12 | ERCOT issued an OCN due to the development of a new Generic Transmission Constraint (GTC) due to transmission outages in the region. |

## Advisories

|  |  |
| --- | --- |
| **Date and Time** | **Description** |
| 07/29/15 18:28 | ERCOT issued an Advisory due to Physically Responsive Capability being less than 3,000 MW. |
| 07/31/15 15:12 | ERCOT issued an Advisory due to Physically Responsive Capability being less than 3,000 MW. |

## Watches

None.

## Emergency Notices

None.

# Application Performance

ERCOT system applications performed well in July. There were no issues to report.

## TSAT/VSAT Performance Issues

None.

## Communication Issues

None.

## Market System Issues

None.

# Net-Forecast Bias Applied to NSRS Procurement for July 2015

Each month, ERCOT calculates a net Forecast Bias pursuant to the ERCOT Ancillary Services Methodology for procurement of Non-Spinning Reserve Service (NSRS). The table below indicates the amount of net Forecast Bias that was applied to the NSRS procurement for specified blocks of time for the month of July, 2015.

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **Blocks** | **Negative Net Load Forecast Average Error - By Weather Zone for the 5 Largest Zones** | | | | |
| **Coast** | **East** | **North Central** | **South Central** | **Southern** |
| **1-2** | 0 | 0 | 0 | 0 | 0 |
| **3-6** | 0 | 0 | 0 | 0 | 0 |
| **7-10** | 0 | 0 | 0 | 0 | 0 |
| **11-14** | 0 | 0 | 0 | 0 | 0 |
| **15-18** | -155 | -25 | -182 | -91 | -46 |
| **19-22** | -141 | -23 | -167 | -84 | -43 |
| **23-24** | 0 | 0 | 0 | 0 | 0 |

# Appendix A: Real-Time Constraints

The following is a complete list of constraints activated in SCED for the month of July. Full contingency descriptions can be found in the Standard Contingencies List located on the MIS secure site at Grid 🡪 Generation 🡪 Reliability Unit Commitment.

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Contingency** | **Constrained Element** | **From Station** | **To Station** | **# of Days Constraint Active** |
| DFL\_MAR8 | BETHK\_66\_A | HK | BET | 8 |
| XSA2N89 | SACH\_69T1 | SACH | SACH | 6 |
| XSA2C89 | SAPOWER\_69T1 | SAPOWER | SAPOWER | 10 |
| DRNS\_TB5 | SNGZEN99\_A | SNG | ZEN | 12 |
| XSA2N89 | SAPOWER\_69T1 | SAPOWER | SAPOWER | 4 |
| DEMSHCK5 | 6185\_\_A | CMTSW | WSTHL | 1 |
| SSKISIN9 | CSA\_ORN\_1 | ORNGRVS | CASA\_BLA | 5 |
| DEULLIG8 | 1060\_\_F | RNKSW | MCPHERSN | 1 |
| SLA\_RIO8 | RIOHND\_ERIOHND\_1 | RIOHONDO | MV\_RIOHO | 2 |
| DLWSRNK5 | POC\_TEAS\_1 | TEASLEY | POCKRUSC | 10 |
| BASE CASE | ZO\_AJO |  |  | 22 |
| SLOBSAN5 | LAQUIN\_LOBO1\_1 | LAQUINTA | LOBO | 7 |
| DJEWSNG5 | JK\_TOKSW\_1 | TOKSW | JK\_CK | 18 |
| SJNSWNT8 | OLSE\_BOS\_1 | BOSQUESW | OLSEN | 1 |
| DLEOTRU8 | E1\_R2\_1 | E1 | R2 | 1 |
| SLEOS18 | E1\_R2\_1 | E1 | R2 | 1 |
| SLAQLOB8 | BRUNI\_69\_1 | BRUNI | BRUNI | 13 |
| DWLV89N8 | 3410\_\_A | ELVSW | REGST | 1 |
| DMARZOR5 | 91T335\_1 | COMAL | LOP337 | 20 |
| DALNREN5 | 853\_\_A | ALNSW | PCUST | 2 |
| DRILTES5 | EDITHC\_GAUSS2\_1 | EDITHCLA | GAUSS | 4 |
| DWH\_STP5 | BONIVI\_RINCON1\_1 | RINCON | BONIVIEW | 7 |
| DGARHIC8 | CKT\_1027\_1 | DUNLAP | DECKER | 3 |
| SAVMBSP8 | 6610\_\_D | BSPSW | BSCTP | 1 |
| SL\_FLA\_8 | RIOHND\_ERIOHND\_1 | RIOHONDO | MV\_RIOHO | 1 |
| XOKL58 | VERS\_69\_1 | VERS | VERS | 3 |
| SENSENW8 | 940\_\_C | ENWSW | WXHCH | 1 |
| BASE CASE | SINTON\_SKIDMO1\_1 | SINTON | SKIDMORE | 3 |
| XBLE89 | BROOKH\_P\_LAVA1\_1 | P\_LAVACA | BROOKHOL | 2 |
| SGEOGEO8 | CSA\_ORN\_1 | ORNGRVS | CASA\_BLA | 2 |
| SCOLPAW5 | COLETO\_KENEDS1\_1 | COLETO | KENEDSW | 3 |
| DFERPAL8 | 38T365\_1 | WIRTZ | FLATRO | 11 |
| DDUNLOS5 | AUSTRO\_AT2H | AUSTRO | AUSTRO | 2 |
| SVEROK28 | VERS\_69\_1 | VERS | VERS | 2 |
| BASE CASE | N\_TO\_H |  |  | 1 |
| DSNGZEN5 | BETHK\_66\_A | HK | BET | 1 |
| SFRAVL8 | BLESSI\_PALACI1\_1 | BLESSING | PALACIOS | 1 |
| DRNS\_TB5 | SNGZEN98\_A | SNG | ZEN | 1 |
| SBRAUVA8 | HAMILT\_MAVERI1\_1 | HAMILTON | MAVERICK | 3 |
| DALNRYS5 | 1646\_\_A | BNDVS | PKRMX | 1 |
| SVICCOL8 | COLETO\_VICTOR1\_1 | COLETO | VICTORIA | 1 |
| BASE CASE | CEDH\_69\_1 | CEDH | CEDH | 1 |
| SVICCO28 | COLETO\_VICTOR2\_1 | COLETO | VICTORIA | 3 |
| SFORYEL8 | FORTMA\_MASN1\_1 | FORTMA | MASN | 1 |
| SGARROM8 | GARZA\_69A1 | GARZA | GARZA | 1 |
| DLONOR58 | ALICE\_SAN\_DI1\_1 | ALICE | SAN\_DIEG | 2 |
| SLAQLOB8 | FALFUR\_69A1 | FALFUR | FALFUR | 6 |
| SVLDO2W8 | BLESSI\_PALACI1\_1 | BLESSING | PALACIOS | 1 |
| XLWS158 | 589\_C\_1 | CRLNW | LWSVS | 1 |
| SLOBSAN5 | FREER\_SAN\_DI1\_1 | SAN\_DIEG | FREER | 3 |
| SFT\_BAL8 | CEDH\_69\_1 | CEDH | CEDH | 1 |
| SRDODES8 | 940\_\_C | ENWSW | WXHCH | 3 |
| DSC\_SL28 | CO\_WAS84\_A | CO | WAS | 1 |
| SBELHIG8 | 163T232\_1 | CHAPHI | WALLER | 1 |
| SBRAUVA8 | EAGLHY\_ESCOND1\_1 | EAGLHYTP | ESCONDID | 1 |
| SGERCLE8 | 99T203\_1 | ZORN | YORKCR | 1 |
| XLOB58 | FREER\_SAN\_DI1\_1 | SAN\_DIEG | FREER | 1 |
| SRICGRS8 | NVKSW\_FMR1 | NVKSW | NVKSW | 1 |
| DBIGKEN5 | BONDRO\_SONR1\_1 | SONR | BONDROAD | 1 |
| XDOW58 | BLESSI\_PALACI1\_1 | BLESSING | PALACIOS | 1 |
| SVCAMIL8 | RIOHND\_ERIOHND\_1 | RIOHONDO | MV\_RIOHO | 1 |
| SSONFRI8 | SONR\_69-1 | SONR | SONR | 1 |
| DHUTGAB8 | 211T147\_1 | GILLCR | MCNEIL\_ | 1 |
| DEULLIG8 | 1140\_\_C | DFWD1 | DFWCE | 3 |
| SLAULA\_8 | LA\_PAL\_VCAVAZ1\_1 | LA\_PALMA | VCAVAZOS | 1 |
| XHUT58 | 1666\_\_B | GILLCR | PFLGV | 2 |
| SGILNU78 | GILA\_MORRIS1\_1 | GILA | MORRIS | 5 |
| XJEW58 | 1240\_\_K | TRSES | WINKLER | 1 |
| DFERPAL8 | 318T313\_1 | WIRTZ | JOHNCI | 1 |
| SMARZOR5 | 419T419\_1 | CLEASP | MARION | 2 |
| SDAFAUS8 | CKT\_1027\_1 | DUNLAP | DECKER | 2 |
| SFERZ48 | Y1\_C4\_1 | C4 | Y1 | 1 |
| XBL2U58 | BLUF\_CRK\_T1\_H | BLUF\_CRK | BLUF\_CRK | 1 |
| SJMCW\_D8 | POC\_TEAS\_1 | TEASLEY | POCKRUSC | 2 |
| DODEQAL5 | 6511\_\_A | MDLNE | WNDWD | 1 |
| DGIBSNG5 | 240\_\_A | JEWET | SNG | 11 |
| DFMRMNS5 | 205\_\_A | MNSES | SSPSW | 1 |
| SGIBSNG5 | SNGXGC99\_1 | GIBCRK | SNG | 2 |
| SLAULA\_8 | LOMA\_A\_L\_FRES1\_1 | L\_FRESNO | LOMA\_ALT | 1 |
| DOLIELM8 | OLI\_BEN1\_1 | OLINGR | BNDVS | 2 |
| XWI2N89 | WINKS\_FMR1 | WINKS | WINKS | 1 |
| SDFWLI28 | 1140\_\_C | DFWD1 | DFWCE | 1 |
| BASE CASE | FALFUR\_69A1 | FALFUR | FALFUR | 1 |