## Slide 1
Ancillary Services Methodology Changes for 2016
Bill Blevins
Manager Operations Planning
QMWG
04-SEPTEMBER-2015

## Slide 2: Items for discussion
  Schedule
  Proposed changes to Regulation Service
  Proposed changes to Non-Spin Reserve Service (NSRS)
  Postings of AS Requirements

## Slide 3: Schedule for discussion with Stakeholders
4-Sept | QMWG
17-Sept | OWG
7-Oct | WMS
8-Oct | ROS
29-Oct | TAC
08-Dec | BOD
Notes: 3.16 Standards for Determining Ancillary Service Quantities
The ERCOT Board shall review and approve ERCOT's methodology for determining the minimum Ancillary Service requirements, the monthly percentage of Load Resources, Controllable Load Resources and DC Ties allowed to provide RRS, and the maximum amount of Reg-Up and Reg-Down that can be provided by Resources providing FRRS-Up and FRRS-Down.
Last done by BOD Dec 2014.

## Slide 4: Regulation Performance-CPS1 Score
ERCOT has to maintain rolling 12 months average CPS1 Score above 100% Per NERC standard BAL-001-1

## Slide 5: Drivers for changes to Regulation Requirements
CPS1 is significantly higher than required and on an increasing trend.
By using last 30 days, transition months tend to drive requirements for the following month. (e.g. April is used to set quantity for June)
Extreme events tend to drive over-procurement for a particular hour in subsequent months, even though the event is unlikely to repeat.
Significant changes in regulation requirements from one hour to the next which may not be necessary.

## Slide 6: Possible Changes to Regulation Service
  Remove last 30 days approach from Regulation Analysis which is used currently and instead use the Regulation data using previous two years same month. (e.g. April 2014 and April 2015 to calculate April 2016 requirements)
  Use five minute average instead of one minute average regulation deployment for exhaustion ratio.
  Use 95th percentile of 5 minute net-load/deployments instead of 98.8th percentile.
  Increase CPS1 trigger to CPS1 Score of 140% instead of 100%
  Update the GE Tables
Notes: Item D. is a metric so that using the 95th percentile will not decrease regulation if CPS1 scores significantly . This adjustment will be applied to the month that scored below 140% unless the rolling average goes below 140% and then it will be applied to the next month until the rolling 12 month CPS1 average increases above 140%.

## Slide 7: Reg-Up Requirement for Jan. 2015
A: Use data from the same month of last 2 years
B: 5-min exhaustion rate
C: 95th percentile
Chart: Jan. 2015 Reg-Up Requirement (MW)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Current | 363 | 294 | 283 | 299 | 420 | 597 | 830 | 475 | 413 | 408 | 400 | 416 | 370 | 420 | 295 | 306 | 400 | 593 | 464 | 273 | 313 | 361 | 515 | 475
A | 425 | 262 | 282 | 349 | 407 | 585 | 817 | 564 | 444 | 452 | 501 | 432 | 324 | 634 | 250 | 296 | 345 | 643 | 562 | 313 | 341 | 342 | 436 | 395
A+B | 355 | 262 | 282 | 291 | 407 | 585 | 817 | 470 | 404 | 452 | 501 | 432 | 324 | 634 | 250 | 269 | 345 | 643 | 562 | 313 | 310 | 342 | 436 | 395
A+B+C | 262 | 258 | 252 | 326 | 423 | 478 | 647 | 342 | 308 | 282 | 312 | 295 | 279 | 253 | 200 | 207 | 221 | 319 | 475 | 239 | 199 | 305 | 314 | 369

## Slide 8: Reg-Up Requirement for Apr. 2015
Chart: April 2015 Reg-up Requirement (MW)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Current | 453 | 458 | 327 | 327 | 412 | 558 | 803 | 397 | 494 | 395 | 414 | 387 | 443 | 395 | 365 | 338 | 356 | 378 | 536 | 445 | 529 | 454 | 557 | 575
A | 546 | 451 | 359 | 349 | 400 | 525 | 746 | 404 | 501 | 430 | 508 | 481 | 452 | 437 | 428 | 395 | 351 | 427 | 471 | 445 | 465 | 428 | 530 | 606
A+B | 546 | 376 | 326 | 349 | 400 | 525 | 746 | 404 | 501 | 430 | 508 | 481 | 452 | 437 | 389 | 359 | 351 | 388 | 392 | 445 | 465 | 428 | 530 | 606
A+B+C | 409 | 266 | 218 | 253 | 297 | 446 | 618 | 304 | 402 | 338 | 380 | 413 | 356 | 374 | 301 | 288 | 289 | 286 | 263 | 335 | 382 | 310 | 387 | 493
A: Use data from the same month of last 2 years
B: 5-min exhaustion rate
C: 95th percentile

## Slide 9: Reg-Up Requirement for June 2015
Chart: June 2015 Reg-up Requirement (MW)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Current | 659 | 428 | 410 | 352 | 494 | 525 | 738 | 459 | 510 | 481 | 681 | 509 | 422 | 397 | 392 | 379 | 311 | 454 | 356 | 472 | 448 | 536 | 559 | 611
A | 633 | 477 | 362 | 307 | 318 | 486 | 622 | 455 | 465 | 557 | 604 | 507 | 493 | 463 | 415 | 404 | 332 | 366 | 380 | 438 | 404 | 490 | 562 | 631
A+B | 633 | 398 | 329 | 307 | 318 | 486 | 622 | 455 | 465 | 557 | 604 | 507 | 493 | 463 | 377 | 368 | 332 | 332 | 317 | 438 | 404 | 490 | 562 | 631
A+B+C | 437 | 321 | 215 | 246 | 237 | 367 | 502 | 358 | 405 | 460 | 455 | 425 | 373 | 356 | 284 | 286 | 248 | 241 | 248 | 314 | 311 | 361 | 467 | 421
A: Use data from the same month of last 2 years
B: 5-min exhaustion rate
C: 95th percentile

## Slide 10: Proposed Regulation-Up Requirement
Chart: Regulation-Up Daily Total (MW)
| 42005 | 42036 | 42064 | 42095 | 42125 | 42156 | 42186 | 42217 | 41883 | 41913 | 41944 | 41974
Current | 9983 | 10197 | 10783 | 10796 | 10696 | 11583 | 11346 | 10481 | 11336 | 10714 | 10751 | 9430
A | 10401 | 10033 | 10514 | 11135 | 10826 | 11171 | 10974 | 9250 | 11823 | 10315 | 9992 | 9976
A+B | 10081 | 9825 | 10228 | 10834 | 10605 | 10888 | 10322 | 9060 | 11223 | 9910 | 9520 | 9716
A+B+C | 7476 | 7565 | 8194 | 8408 | 8283 | 8338 | 8166 | 8291 | 8903 | 7632 | 6921 | 7546
A: Use data from the same month of last 2 years
B: 5-min exhaustion rate
C: 95th percentile

## Slide 11: Proposed Regulation-Down Requirement
Chart: Regulation-Down Daily Total (MW)
| 42005 | 42036 | 42064 | 42095 | 42125 | 42156 | 42186 | 42217 | 41883 | 41913 | 41944 | 41974
Current | 9089 | 8891 | 9429 | 9515 | 9805 | 10988 | 10809 | 10118 | 10160 | 10524 | 10083 | 8664
A | 9387 | 8859 | 8938 | 9576 | 10436 | 10657 | 9832 | 9275 | 10448 | 9254 | 8547 | 9116
A+B | 8921 | 8599 | 8869 | 9441 | 10397 | 10506 | 9735 | 9239 | 10329 | 9220 | 8459 | 8878
A+B+C | 6841 | 6790 | 6925 | 7293 | 7877 | 8078 | 7483 | 7705 | 7961 | 7144 | 6271 | 7447
A: Use data from the same month of last 2 years
B: 5-min exhaustion rate
C: 95th percentile

## Slide 12: Drivers for NSRS Changes
Feedback we received last year to revisit NSRS Methodology
Incorporate effects of net load ramps

## Slide 13: Suggested Changes to Non-Spin Service
  Use the 3-Hour ahead net forecast error instead of 6-hour ahead
  Use net forecast error only on the under-forecast side
  Remove last 30 days from NSRS Analysis and instead use the same month for previous three years.
  Use dynamic percentile between 70th and 95th percentile based on the risk of net load ramp

## Slide 14: Possible Changes to Non-Spin Reserve Service(NSRS)
 | Current Methodology | Proposed Methodology
Data Used |  | 
Forecast | 6hour-ahead Net Load Error | 3hour-ahead Net Load Error
Over & Under Forecast | Both | Under Forecast
Percentile | 95th | Dynamically determined based on risk of net load ramp
Cap | 2000MW | No Cap
Floor | 1375 MW (Peak Hours) | 1375 MW (Peak Hours)
Target Period
Same Period
Previous Year
15 days
Not considered
30days prior to study
30
30
15
30
Target Period
Same Period
Previous 3 Years
30
30
30
30
NSRS+ Reg-Up procured > ‘X’ Percentile of Net-Load Forecast Error

## Slide 15: Comparison NSRS Procurement change
Current Methodology
Proposed Methodology
Notes: Font sizes should be increased if possible

## Slide 16: Posting of AS Requirements
  Responsive Reserve is already posted in December for the next year.
  Regulation for each month can be posted for the next year in December.
  NSRS for each month can be posted for the next year in December.
Notes: Font sizes should be increased if possible

## Slide 17
Discussion

## Slide 18: NSRS Net Load Ramp – Up and Risk Factor
Net Load Ramp-Up is the increase in Net Load over an hour.
The Net Load Ramp–Up Risk Factor is calculated by normalizing hourly ramp-up values by seasonal peak value
The Net Load Ramp-Up Risk Factor is averaged over 4 hour blocks.

## Slide 19: How is Risk Factor Used
Chart: Percentile- Risk Factor Mapping Function
Higher Risk Factor corresponds to a higher Percentile value for the Net Load Forecast Error.
Notes: Give example
Select one high risk
One low risk