| NPRR Number | 713 | NPRR Title | Reactive Power Testing Requirements |
| --- | --- | --- | --- |
| Date |  | September 14, 2015 |  |
| Submitter’s Information |  |  |  |
| Name |  | John Palen |  |
| E-mail Address |  | john.palen@nrg.com |  |
| Company |  | NRG Texas Power LLC |  |
| Phone Number |  | 713-537-3706 |  |
| Cell Number |  | 713-545-3415 |  |
| Market Segment |  | Independent Generator |  |

Comments

During the Reactive Power Testing Requirements Workshop, language was added which recommended changing the reference point at which Market participants shall specify their reactive capability, from nominal system voltage, to the voltage profile established by ERCOT.  Voltage profiles are generated for two time periods during the year (Summer/Fall, and Winter/Spring).  The current language however, fails to specify which one should be used.

NRG is recommending that lagging reactive capability be specified using the Summer/Fall voltage profile, and leading reactive capability use the Winter/Spring profile.  This change should result in providing ERCOT and Transmission Providers with the most limiting values during those seasonal periods when that particular capability is most likely to be needed.

Deleted language requiring that the Automatic Voltage Regulator (AVR) be in service during testing, as it is redundant to the Nodal Operating Guide, where this type of information is more appropriate.

Revised Cover Page Language

None

Revised Proposed Protocol Language

8.1.1.2.1.4	Voltage Support Service Qualification

(1)	The Resource Entity must verify and maintain its stated Reactive Power capability for each of its Generation Resources providing Voltage Support Service (VSS), as required by the Operating Guides.  Generation Resources providing VSS reactive capability limits shall be specified as follows:  lagging reactive capability should be specified using the Summer/Fall voltage profile, and leading capability specified using the Winter/Spring voltage profile.

(2)	The Resource Entity shall conduct reactive capacity qualification tests to verify the maximum leading and lagging reactive capability of all Generation Resources required to provide VSS.  Reactive capability tests are performed during the resource commissioning process and at a minimum of once every five years or within 12 months following the discovery of a change that affects its Real Power or Reactive Power capability by more than 10 percent of the last RARF submittal and is expected to last more than 6 months.  Mothballed Generation Resources that have not been tested within the last five years shall be verified within 12 calendar months upon return to service.  ERCOT may require additional testing if it has information indicating that current data is inaccurate.  The Resource Entity is not obligated to place Generation Resources On-Line solely for the purposes of testing.  The reactive capability tests must be conducted at a time agreed to in advance by the Resource Entity, its QSE, the applicable TSP, and ERCOT.

(3)	Leading and lagging reactive operating limits must be demonstrated following  the reactive power verification test procedure as more fully described in Nodal Operating Guides Section 3.3.2, Unit Reactive Capability Requirements.

(4)	The Resource Entity shall perform the Automatic Voltage Regulator (AVR) tests and shall supply AVR data as specified in the Operating Guides.  The AVR tests must be performed on initial qualification.  The AVR tests must be conducted at a time agreed on in advance by the Resource Entity, its QSE, the applicable TSP and ERCOT.