## Slide 1
Ancillary Services Requirements for Future Ancillary Services
Cost Benefit Analysis
FAS/SIRS Meeting
September 21, 2015

## Slide 2: Proposed Future Ancillary Services
Regulation Up
Fast-Responding Regulation Up
Current
Proposed
Fast Frequency Response 1
Primary Frequency Response
Contingency Reserves 1
Synchronous Inertial Response
Supplemental Reserves 1
Mostly unchanged
59.8 Hz, Limited duration
59.7 Hz, Longer duration
Fast Frequency Response 2
Contingency Reserves 2
SCED-dispatched
Manually dispatched
Supplemental Reserves 2
SCED-dispatched
Manually dispatched
Ongoing development
Non-Spin
Responsive
Regulation Down
Fast-Responding Regulation Down
Regulation Up
Regulation Down
Fast-Responding Regulation Up
Fast-Responding Regulation Down

## Slide 3: CBA Study design
  Objective: Evaluate the net benefits of FAS proposal
  Tools: PLEXOS, modeling DA market as a single zone
  Evaluation metrics: total resource cost savings (TRC), where
    TRC = production cost savings - incremental capital costs - implementation cost, and
    Production cost savings includes avoided fuel, VOM and startup costs

## Slide 4: Scenario information
Scenario | Thermal and Other Cap., MW | Wind Capacity, MW | Solar Capacity, MW
2016 Base Case | 74,223 | 17,293 | 146
2024 Current Trends | 87,082 | 17,800 | 3,446
2024 Stringent Environmental | 80,247 | 28,557 | 9,146
Scenario | Peak Load, MW | Min. Load, MW | Max Renew., MW | Min Renew., MW
2016 BC | 74,700 | 28,221 | 16,638 | 269
2024 CT | 82,220 | 33,489 | 19,314 | 465
2024 SE | 81,230 | 33,279 | 34,042 | 865
Hourly shapes for Load, Wind, and Solar profiles are taken from 2010 actual profiles
Peak Load and Capacities include PUN Load and Pun Capacities

## Slide 5: Scenario Information
 | Date | Renew., MW | Load, MW | Net Load, MW | Inertia, GWs | Penetr.
Current | 3/29/2015 2 am | 10,308 | 25,400 | 15,092 | 135 | 41%
2016 | 4/1 3 am | 15,012 | 29,628 | 14,616 | 120 | 51%
2024 CT | 3/27 12 pm | 15,805 | 37,947 | 22,142 | 130 | 42%
2024 SE | 4/29 10 am | 32,898 | 45,922 | 13,024 | 103 | 72%
 | Date | Renew., MW | Load, MW | Net Load, MW | Inertia, GWs | Penetr.
Current | 3/12/2011 2 am | 5,668 | 23,518 | 17,850 | 111 | 24%
2016 | 4/29 3 am | 14,819 | 29,748 | 14,929 | 114 | 50%
2024 CT | 4/29 12 pm | 15,260 | 38,424 | 23,164 | 122 | 40%
2024 SE | 4/29 2 am | 24,108 | 35,808 | 11,700 | 90 | 67%
Lowest Inertia Hour
Maximum Renewable Penetration Hour

## Slide 6: Provision of FAS Products
Product | Resources that Can Provide It
Regulation—4 products | Same as under CAS
FFR1 (59.8 Hz, limited duration) | Batteries, flywheels, loads with short duration
FFR2 (59.7 Hz, longer duration) | Existing Load Resources + new ones
PFR | Same as those providing Gen RRS under CAS; potentially wind and batteries
CRS1 (dispatchable 10-min) | Any online/offline gen, dispatchable load
CRS2 (manual 10-min) | Existing and new Load Resources, DG
SRS1 (dispatchable 30-min) | Any online/offline gen, dispatchable load
SRS2 (manual 30-min) | Existing and new Load Resources, DG

## Slide 7: Methodology for reserve determination
Run a scenario with initial reserve requirements:
2800 MW RRS (min 1240 MW of RRS from Gen);
Load Resources providing RRS based on 2014 participation;
Regulation and Non-Spin requirements based on the scenario.
Obtain hourly system inertia values from initial Plexos run

## Slide 8: Inertia plots
Jan-May 2014

## Slide 9: PFR (no FFR) and Ratio
Based on inertia values for every hour determine PFR (with no FFR) and Equivalency Ratio, using 14 dynamic study cases.
Minimum RRS from Generation or minimum PFR is based on NERC BAL-003 IFRO
 | Case -1 | Case 0 | Case1 | Case2 | Case3 | Case4 | Case5 | Case6 | Case7 | Case8 | Case9 | Case10 | Case11 | Case12
Inertia, GWs | 80 | 100 | 120 | 136 | 152 | 177 | 202 | 230 | 256 | 278 | 297 | 316 | 332 | 350
Eq. Ratio | 2.67 | 2.35 | 2.2 | 2 | 1.5 | 1.4 | 1.3 | 1.25 | 1.13 | 1.08 | 1 | 1 | 1 | 1
PFR Requirement (no FFR), MW | 8730 | 7360 | 5200 | 4700 | 3750 | 3370 | 3100 | 3040 | 2640 | 2640 | 2240 | 2280 | 2140 | 2140
Min PFR Requirement, MW | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240 | 1240

## Slide 10: CAS RRS Requirement
In CAS load participation in RRS is limited to 50% of total RRS requirement;
It is assumed that, if MW limit for load participation increases, more Load Resources will participate;
There is uncertainty with regard to Load Resource participation in RRS;
If RRS participation is less than 50% of total RRS requirement and Equivalency Ratio is higher than 1, we will be short of RRS.

## Slide 11: CAS RRS Requirement
Based on analysis of 2014 Load participation in RRS average participation factors is calculated for hours 1-24 for each month (as % of MW limit)
Expected Load Resource Participation is estimated applying these participation factors to the new MW limit in the scenario;
A buffer is calculated to meet needs 95% of time (given the distribution of load for each month and hour)
The buffer is adjusted to account for increase in load participation and the equivalency ratio

## Slide 12: FAS PFR/FFR Requirement
Based on initial inertia values for every hour determine PFR (with no FFR) and Equivalency Ratio, using 14 dynamic study cases (same as in CAS) .
Minimum 1240 MW should come from PFR
The remainder can be supplied by Resources providing FFR. This determines FFR participation limit.
Load Resource participation factors from historic data are applied to this limit to calculate expected load participation.

## Slide 13: Regulation Quantities (FAS/Current)
Regulation quantities are determined for hours 1-24 for every month, as per current AS methodology;
Hourly Load/Wind/Solar outputs in the 2016-basecase were interpolated into minute-by-minute profiles
Regulation requirement is based on 98.8th percentile of 5-minute change in net load (load-wind generation-solar generation)
Regulation quantities are identical for Current and Future AS framework

## Slide 14: Contingency Reserve Service – FAS Only
For 14 inertia cases ERCOT identified the lowest settling frequency (point B) based on a single unit trip, with frequency nadir above 59.7 Hz, i.e. no tripping Load Resources on UFR
CRS requirements are calculated as amount of reserves required to restore frequency within normal bounds
For each hour, based on inertia conditions identify CRS requirement as:
CRS Req=(freset-fpoint B)*bias*10
 | Case -1 | Case 0 | Case1 | Case2 | Case3 | Case4 | Case5 | Case6 | Case7 | Case8 | Case9 | Case10 | Case11 | Case12
Inertia, GWs | 80 | 100 | 120 | 136 | 152 | 177 | 202 | 230 | 256 | 278 | 297 | 316 | 332 | 350
Eq. Ratio | 2.67 | 2.35 | 2.2 | 2 | 1.5 | 1.4 | 1.3 | 1.25 | 1.13 | 1.08 | 1 | 1 | 1 | 1
Point B frequency, Hz | 59.8 | 59.8 | 59.8 | 59.79 | 59.79 | 59.79 | 59.77 | 59.78 | 59.77 | 59.78 | 59.76 | 59.75 | 59.75 | 59.76
Notes: Bias is assumed as 1% of system load at the time

## Slide 15: 2016 and 2024 CT NSRS - Current AS
NSRS is determined for 6 four-hourly blocks for each month as per current AS methodology
NSRS is determined as 95th percentile of net load forecast error (load forecast error- wind forecast error) minus corresponding regulation-up requirement
The maximum of NSRS is set at 2000 MW and with a floor at 1375MW for peak hours.
Notes: Peak hours - H7-H22 in each month

## Slide 16: 2024 SE NSRS - Current AS
Projected wind forecast errors considering the accuracy improvement (7.6% MAPE for 6-hour ahead wind forecast in 2014 v.s. 4.2% MAPE for 6-hour ahead wind forecast in 2024)
Dynamically determined the percentile of net-load forecast error based on the net-load ramp risk factor
No cap is applied

## Slide 17: SRS – FAS Only
SRS is determined based on net load forecast error (as in NSRS) minus the other upwards ancillary service capacity.
No concept of floors
Out of 8760 Hours, 270-280 hours have non-zero SRS requirements (in 2016 and 2024 CT)