| NPRR Number | 725 | NPRR Title | Modifications to CDR PUN Capacity Forecasting and PUN Net Capacity Reporting Requirements |
| --- | --- | --- | --- |
| Date of Decision |  | September 10, 2015 |  |
| Action |  | Tabled |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | To be determined. |  |
| Priority and Rank Assigned |  | To be determined. |  |
| Nodal Protocol Sections Requiring Revision |  | 3.2.6.2.2, Total Capacity Estimate 10.3.2.4, Reporting of Net Generation Capacity 22, Attachment L, Declaration of Private Use Network Net Generation Capacity Availability (New) |  |
| Related Documents Requiring Revision/ Related Revision Requests |  | None. |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) makes improvements to the forecasting of Private Use Network net generation capacity available to the ERCOT Region for use in the Report on Capacity, Demand and Reserves (CDR) and other ERCOT Resource adequacy assessments. A proposed Declaration of Private Use Network Net Generation Capacity Availability for collecting annual Private Use Network capacity forecast information is attached. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | - Aligns Protocol language with existing defined terms. - Improves the accuracy of Private Use Network capacity forecasts for Resource adequacy reporting and analysis. - Modifies a current data reporting requirement in Section 10.3.2.4 for industrial consumers that have a Private Use Network - Implements suggested improvements discussed by the Supply Analysis Working Group (SAWG) |  |
| Credit Work Group Review |  | To be determined. |  |
| PRS Decision |  | On 9/10/15, PRS unanimously voted to table NPRR725 and refer the issue to WMS. All Market Segments were present for the vote. |  |
| Summary of PRS Discussion |  | On 9/10/15, it was explained that NPRR725 improves the forecasting of Private Use Network net generation capacity by using historial data as well as change in capacity available to the ERCOT Region. Some participants requested that implementation of NPRR725 be further discussed by the SAWG. It was requested that particpants be cognizant of delaying NPRR725 as ERCOT would like to incorporate this data in the 2016 CDR. |  |

| Sponsor |  |
| --- | --- |
| Name | Peter Warnken |
| E-mail Address | pwarnken@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6705 |
| Cell Number | 512-585-2246 |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brian Manning |
| E-Mail Address | Brian.manning@ercot.com |
| Phone Number | 512-248-3937 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None. |  |

Market Rules Notes

Please note that baseline Protocol language in Section 3.2.6.2.2 has been updated due incorporation of administrative changes into the September 1, 2015 Nodal Protocols.

Proposed Protocol Language Revision

3.2.6.2.2	Total Capacity Estimate

The total capacity estimate shall be determined based on the following equation:

TOTCAP s ,i	=	INSTCAP s, i + PUNCAP s, i + WINDCAP s, i, r  + HYDROCAP s, i + SOLARCAPs, i + RMRCAP s, i + DCTIECAP s, i + SWITCHCAP s, i + MOTHCAP s, i + PLANNON s, i + PLANIRR s, i, r – UNSWITCH s, i – RETCAP s, i

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| TOTCAP s, i | MW | Total Capacity—Estimated total capacity available during the Peak Load Season s for the year i. |
| INSTCAP s, i | MW | Seasonal Net Max Sustainable Rating—The Seasonal net max sustainable rating for the Peak Load Season s as reported in the approved Resource Registration process for each operating Generation Resource for the year i excluding WGRs, hydro Generation Resource capacity, solar unit capacity, Resources operating under RMR Agreements, and Generation Resources capable of “switching” from the ERCOT Region to a non-ERCOT Region. |
| PUNCAP s, i | MW | Private Use Network Capacity—The forecasted generation capacity available to the ERCOT Transmission Grid, net of self-serve load, from All-Inclusive Generation Resources in Private Use Networks for Peak Load Season s and year i. The capacity forecasts are developed as follows. First, a base capacity forecast, determined from Settlement data, is calculated as the average net generation capacity available to the ERCOT Transmission Grid during the 20 highest system-wide peak Load hours for each preceding three year period for Peak Load Season s and year i. The base capacity forecast is then adjusted by adding the aggregated incremental forecasted annual changes in net generation capacity as of the start of the summer Peak Load Season s for forecast year i reported for Private Use Networks pursuant to Section 10.3.2.4, Reporting of Net Generation Capacity. |
| WINDPEAKPCT s, r | % | Seasonal Peak Average Wind Capacity as a Percent of Installed Capacity—The average wind capacity available for the summer and winter Peak Load Seasons s and region r, divided by the installed capacity for region r, expressed as a percentage. The Seasonal Peak Average, derived from Settlement data, is first calculated as the average capacity during the 20 highest system-wide peak Load hours for a given year’s summer and winter Peak Load Seasons. The final value is the average of the previous ten eligible years of Seasonal Peak Average values. Eligible years include 2009 through the most recent year for which COP data is available for the summer and winter Peak Load Seasons. If the number of eligible years is less than ten, the average shall be based on the number of eligible years available. This calculation is limited to WGRs that have been in operation as of January 1 for each year of the period used for the calculation. |
| WINDCAP s, i, r | MW | Existing WGR Capacity—The capacity available for all existing WGRs for the summer and winter Peak Load Seasons s, year i, and region r, multiplied by WINDPEAKPCT for summer and winter Peak Load Seasons s and region r. |
| HYDROCAPs, i | MW | Hydro Unit Capacity—The average hydro Generation Resource capacity available, as determined from the COP, during the highest 20 peak Load hours for each preceding three year period for Peak Load Season s and year i. |
| SOLARCAPs, i | MW | Solar Unit Capacity—100% of the nameplate capacity for operational solar units until a threshold value of 200 MWs of registered wholesale installed solar capacity is reached for Peak Load Season s and year i. Once the 200 MW threshold value is reached, the average solar unit capacity available, as determined from the COP, during the highest 20 peak Load hours for each preceding three year period for Peak Load Season s and year i. |
| RMRCAP s, i | MW | Seasonal Net Max Sustainable Rating for Generation Resource providing RMR Service—The Seasonal net max sustainable rating for the Peak Load Season s as reported in the approved Resource Registration process for each Generation Resource providing RMR Service for the year i until the approved exit strategy for the RMR Resource is expected to be completed. |
| DCTIECAP s, i | MW | Seasonal Net Max Sustainable Rating for DC Tie Resource—The average DC Tie capacity imported into the ERCOT Region during the highest 20 peak Load hours for each preceding three year period for Peak Load Season s and year i. |
| SWITCHCAP s, i | MW | Seasonal Net Max Sustainable Rating for Switchable Generation Resource—The Seasonal net max sustainable rating for the Peak Load Season s as reported in the approved Resource asset registration process for each Generation Resource for the year i that can electrically connect (i.e., “switch”) from the ERCOT Region to another power region. |
| MOTHCAP s, i | MW | Seasonal Net Max Sustainable Rating for Mothballed Generation Resource—The Seasonal net max sustainable rating for the Peak Load Season s as reported in the approved Resource Registration process for each Mothballed Generation Resource for the year i based on the lead time and probability information furnished by the owners of Mothballed Generation Resources pursuant to Section 3.14.1.9, Generation Resource Status Updates. If the value furnished by the owner of a Mothballed Generation Resource pursuant to Section 3.14.1.9 is greater than or equal to 50%, then use the Seasonal net max sustainable rating for the Peak Load Season s as reported in the approved Resource registration process for the Mothballed Generation Resource for the year i. If the value furnished by the owner of a Mothballed Generation Resource pursuant to Section 3.14.1.9 is less than 50%, then exclude that Resource from the Total Capacity Estimate. |
| PLANNON s, i | MW | New, non-Wind Generating Capacity—The amount of new, non-wind generating capacity for the Peak Load Season s and year i that: (a) has a Texas Commission on Environmental Quality (TCEQ)-approved air permit, (b) has a federal Greenhouse Gas permit, if required, (c) has obtained water rights sufficient to operate the Resource, and (d) has a signed Standard Generation Interconnect Agreement (SGIA), or a public, financially-binding agreement between the Resource owner and TSP under which generation interconnection facilities would be constructed; or for a Municipally Owned Utility (MOU) or Electric Cooperative (EC), a public commitment letter to construct a new Resource. Exclude new, non-wind generating capacity that has met the requirements of (a), (b), (c) and (d) above in which ERCOT has received written Notification from the developer that the new capacity will not proceed with construction. [NPRR588: Replace the variable definition above with the following upon system implementation:] New, non-IRR Generating Capacity—The amount of new, non-IRR generating capacity for the Peak Load Season s and year i that: (a) has a Texas Commission on Environmental Quality (TCEQ)-approved air permit, (b) has a federal Greenhouse Gas permit, if required, (c) has obtained water rights sufficient to operate the Resource, and (d) has a signed Standard Generation Interconnect Agreement (SGIA), or a public, financially-binding agreement between the Resource owner and TSP under which generation interconnection facilities would be constructed; or for a Municipally Owned Utility (MOU) or Electric Cooperative (EC), a public commitment letter to construct a new Resource. Exclude new, non-IRR generating capacity that has met the requirements of (a), (b), (c) and (d) above in which ERCOT has received written Notification from the developer that the new capacity will not proceed with construction.. |
| PLANIRR s, i, r | MW | New IRR Capacity—For new WGRs, the capacity available for the summer and winter Peak Load Seasons s, year i, and region r, multiplied by WINDPEAKPCT for summer and winter Load Season s and region r. For new solar units, 100% of the nameplate capacity units until a threshold value of 200 MWs of registered wholesale installed solar capacity is reached for summer Peak Load Season s and year i. Once the 200 MW threshold value is reached, the average solar unit capacity available, as determined from the COP, during the highest 20 peak Load hours for each preceding three-year period for summer Peak Load Season s and year i. New IRRs must have an SGIA or other public, financially binding agreement between the Resource owner and TSP under which generation interconnection facilities would be constructed or, for a MOU or EC, a public commitment letter to construct a new IRR. |
| UNSWITCH s, i | MW | Capacity of Unavailable Switchable Generation Resource—The amount of capacity reported by the owners of a switchable Generation Resource that will be unavailable to ERCOT during the Peak Load Season s and year i pursuant to paragraph (2) of Section 16.5.4, Maintaining and Updating Resource Entity Information. |
| RETCAP s, i | MW | Capacity Pending Retirement—The amount of capacity in Peak Load Season s of year i that is pending retirement based on information submitted on a Notification of Suspension of Operations form (Section 22, Attachment E, Notification of Suspension of Operations) pursuant to Section 3.14.1.11, Budgeting Eligible Costs, but is under review by ERCOT pursuant to Section 3.14.1.2, ERCOT Evaluation, that has not otherwise been considered in any of the above defined categories. |
| i | None | Year. |
| s | None | Summer and winter Peak Load Seasons for year i. |
| r | None | Coastal and non-coastal wind regions. WGRs are classified into regions based on the county that contains their Point of Interconnection (POI). The coastal region is defined as the following counties: Cameron, Willacy, Kenedy, Kleberg, Nueces, San Patricio, Refugio, Aransas, Calhoun, Matagorda, and Brazoria. The non-coastal region consists of all other counties in the ERCOT Region. |

10.3.2.4	Reporting of Net Generation Capacity

Each Resource Entity with an All-Inclusive Generation Resource in a Private Use Network shall complete and submit the declaration in Section 22, Attachment L, Declaration of Private Use Network Net Generation Capacity Availability, to ERCOT by February 1st of each year, stating its projected annual changes in net generation capacity available to the ERCOT Transmission Grid for May 31 of the previous calendar year to May 31 of the current calendar year, and annual changes as of May 31 for the next ten subsequent years.  ERCOT will use the aggregated capacity forecasts for the Report on Capacity, Demand and Reserves, pursuant to Section 3.2.6.2.2, Total Capacity Estimate.

- ERCOT Nodal Protocols

- Section 22

- Attachment L:  Declaration of Private Use Network Net Generation Capacity Availability

- [Date]

Declaration of Private Use Network Net Generation Capacity Availability

A Private Use Network is an electric network connected to the ERCOT Transmission Grid that contains load that is not directly metered by ERCOT (i.e., load that is typically netted with internal generation). A Resource Entity with an All-Inclusive Generation Resource in a Private Use Network shall use this form to provide ERCOT with information required by ERCOT Protocol Section 10.3.2.4, Reporting of Net Generation Capacity. This form must be submitted to ERCOT by February 1 of each year. ERCOT shall treat this information as Protected Information in accordance with paragraph (x) of Section 1.3.1.1.

Please fill out this form electronically, print and sign. The form can be sent to ERCOT via email to mpappl@ercot.com (.pdf), via facsimile to (512) 225-7079, or via mail to ERCOT, Attention: Market Participant Registration, 7620 Metro Center Drive, Austin, Texas 78744.

Date of Notice: _________

| Resource Entity: ________________________ | DUNS Number: __________________ |
| --- | --- |

Facility Name: _____________________________

In the table below, enter the incremental forecasted changes in net generation capacity (in Megawatts) available to the ERCOT Transmission Grid for May 31 of the previous calendar year to May 31 of the current calendar year, and year-on-year changes as of May 31 for the next 10 subsequent years. The capacity forecasts should account for changes in both process loads and self-generation capability. Example: If the capacity change is -75 MW from May 31 of the previous calendar year to May 31 of the current year, enter -75 MW in line 1. If the capacity change is 100 MW from May 31 of the current calendar year to May 31 of the next calendar year, enter 100 MW in line 2. DO NOT enter cumulative annual changes. (For this example, do not enter 25 MW in line 2).

| Line# | Annual Forecast Periods | Expected Change in Net Generation Capacity Available to the ERCOT Grid, MW |
| --- | --- | --- |
| 1 | May 31 of previous calendar year to May 31 of current calendar year |  |
| 2 | May 31 of current calendar year to May 31 of forecast year 1 |  |
| 3 | May 31 of forecast year 1 to May 31 of forecast year 2 |  |
| 4 | May 31 of forecast year 2 to May 31 of forecast year 3 |  |
| 5 | May 31 of forecast year 3 to May 31 of forecast year 4 |  |
| 6 | May 31 of forecast year 4 to May 31 of forecast year 5 |  |
| 7 | May 31 of forecast year 5 to May 31 of forecast year 6 |  |
| 8 | May 31 of forecast year 6 to May 31 of forecast year 7 |  |
| 9 | May 31 of forecast year 7 to May 31 of forecast year 8 |  |
| 10 | May 31 of forecast year 8 to May 31 of forecast year 9 |  |
| 11 | May 31 of forecast year 9 to May 31 of forecast year 10 |  |

Describe any future load expansions, equipment shutdowns, or new self-generation associated with the capacity changes reported above.

By signing below, I certify that I am authorized to execute and submit this Notice on behalf of the above Resource Entity, and that the data and statements contained herein are true and correct to the best of my knowledge.

Signature of Authorized Signatory:

Name:  ________________

Title:    ________________

Phone:  ________________

Date:   _________________