| NPRR Number | 708 | NPRR Title | Clarifying ERCOT Actions During Energy Emergency Alerts |
| --- | --- | --- | --- |
| Date of Decision |  | October 15, 2015 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | Upon system implementation of NPRR706, Restore the ability to use Physical Responsive Reserve Capability as an Indicator of Available Frequency Responsive Capacity |  |
| Priority and Rank Assigned |  | Not applicable |  |
| Nodal Protocol Sections Requiring Revision |  | 6.5.9.4.2, EEA Levels |  |
| Related Documents Requiring Revision/Revision Requests |  | NOGRR146, Clarifying ERCOT Actions During Energy Emergency Alerts |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) revises the Energy Emergency Alert (EEA) steps to include concepts discussed during the 4/2/15 EEA workshop # 3 which will improve the management of EEA. Specifically, this NPRR explicitly adds the ability for operators to consider whether sufficient Resources are available to recover reserves within an acceptable timeframe following a disturbance before declaring an EEA; separates and clarifies the triggers for entering each step of the EEA plan from the operational goals while operating within each level of EEA; and formalizes an amount of Physical Responsive Capactiy (PRC) for operators to target when determining Load shed amounts in EEA Level 3. This NPRR also removes the requirement to notify the Southwest Power Pool Reliabilty Coordinator when an EEA is declared as this is a North American Electric Reliability Copropration (NERC) requirement and is covered in the Operating Procedures. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | This NPRR provides clarity to the Market Participant about actions that ERCOT may take during the EEAs; addresses comments and issues raised related to the EEA steps during the three EEA workshops; and provides clarity to all Market Participants regarding ERCOT actions during EEA. |  |
| Credit Work Group Review |  | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR708 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |
| PRS Decision |  | On 6/11/15, PRS unanimously voted to table NPRR708 and refer the issue to ROS and WMS. All Market Segments were present for the vote. On 7/16/15, PRS unanimously voted to table NPRR708. All Market Segments were present for the vote. On 9/10/15, PRS voted to recommend approval of NPRR708 as amended by the 7/15/15 ERCOT comments. There was one opposing vote from the Consumer Market Segment and one abstention from the Independent Power Marketer (IPM) Market Segment. All Market Segments were present for the vote. On 10/15/15, PRS voted to endorse and forward to TAC the 9/10/15 PRS Report and Impact Analysis for NPRR708. There were two abstentions from the Independent Generator and Consumer Market Segments. All Market Segments were present for the vote. |  |
| Summary of PRS Discussion |  | On 6/11/15, participants agreed that additional review and discussion at ROS and WMS would be beneficial in finalizing the language. On 7/16/15, participants acknowledged the 7/9/15 ROS comments and 7/15/15 ERCOT comments, but agreed that NPRR708 should remain tabled until WMS can review the language as the issue was also previously referred to WMS. On 9/10/15, it was emphasized that NPRR708 facilitated changes to meet NERC requirements; that ROS had provided its input endorsing the 7/15/15 ERCOT comments; and that NPRR708 should move forward. On 10/15/15, participants acknowledged the 8/10/15 ERCOT Steel Mill comments. |  |

| Sponsor |  |
| --- | --- |
| Name | Bill Blevins |
| E-mail Address | bblevins@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6691 |
| Cell Number | 512-912-6314 |
| Market Segment | Not applicable. |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brian Manning |
| E-Mail Address | Brian.manning@ercot.com |
| Phone Number | 512-248-3937 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ROS 070915 | Provided additional clarifying language. |
| ERCOT 071515 | Incorporated recommendations from the 7/10/15 Qualified Scheduling Entities Working Group (QMWG) meeting. |
| WMS 080615 | Recommended that PRS continue to table NPRR708 for one month to allow for further discussion. |
| ERCOT Steel Mills 081015 | Proposed language changes to EEA Level 3 language to clarify when and how EEA Level 3 is to be implemented and when ERCOT is authorized to recall firm Load after voluntary curtailment. |
| OWG 090315 | Endorsed NPRR708 as amended by the 7/15/15 ERCOT comments. |

Market Rules Notes

Please note that the following NPRR also proposes revisions to Section 6.5.9.4.2:

- NPRR667, Ancillary Service Redesign

Proposed Protocol Language Revision

6.5.9.4.2	EEA Levels

(1)	ERCOT will declare an EEA Level 1 when Physical Responsive Capacity (PRC) falls below 2,300 MW and is not projected to be recovered above 2,300 MW within 30 minutes without the use of the following actions that are prescribed for EEA Level 1:

(a)	ERCOT shall take the following steps to maintain steady state system frequency near 60 Hz and maintain PRC above 1,750 MW:

(i)	Request available Generation Resources that can perform within the expected timeframe of the emergency to come On-Line by initiating manual HRUC or through Dispatch Instructions;

(ii)	Use available DC Tie import capacity that is not already being used;

(iii)	Issue a Dispatch Instruction for Resources to remain On-Line which, before start of emergency, were scheduled to come Off-Line; and

(iv)	At ERCOT’s discretion, deploy available contracted ERS-30 via an XML message followed by a VDI to the all-QSE Hotline.  The ERS-30 ramp period shall begin at the completion of the VDI.

(A)	If less than 500 MW of ERS-30 is available for deployment, ERCOT shall deploy it as a single block.

(B)	If the amount of ERS-30 available for deployment equals or exceeds 500 MW, ERCOT, at its discretion, may deploy ERS-30 as a single block or by group designation.  ERCOT shall develop a random selection methodology for determining how to place ERS Resources in ERS-30 into groups, and shall describe the methodology in a document posted to the MIS Public Area.  Prior to the start of an ERS Contract Period for ERS-30, ERCOT shall notify QSEs representing ERS Resources in ERS-30 of their ERS Resources’ group assignments.

(C)	ERS-30 may be deployed at any time in a Settlement Interval.

(D)	Upon deployment, QSEs shall instruct their ERS Resources in ERS-30 to perform at contracted levels consistent with the criteria described in Section 8.1.3.1.4, Event Performance Criteria for Emergency Response Service Resources, until either ERCOT releases the ERS-30 deployment or the ERS-30 Resources have reached their maximum deployment time.

(E)	ERCOT shall notify QSEs of the release of ERS-30 via an XML message followed by VDI to the all-QSE Hotline.  The VDI shall represent the official notice of ERS-30 release.  ERCOT may release ERS-30 as a block or by group designation.

(F)	Upon release, an ERS Resource in ERS-30 shall return to a condition such that it is capable of meeting its ERS performance requirements as soon as practical, but no later than ten hours following the release.

(b)	QSEs shall:

(i)	Ensure COPs and telemetered HSLs are updated and reflect all Resource delays and limitations; and

(ii)	Suspend any ongoing ERCOT required Resource performing testing.

(2)	ERCOT will declare an EEA Level 2 when steady state system frequency cannot be maintained at a minimum of 59.91 Hz or when  PRC falls below 1,750 MW and is not projected to be recovered above 1,750 MW within 30 minutes without the use of the following actions that are prescribed for EEA Level 2:

(a)	In addition to the measures associated with EEA Level 1, ERCOT shall take the following steps to maintain steady state system frequency at a minimum of 59.91 Hz and maintain PRC above 1,000 MW:

(i)	Instruct TSPs and DSPs or their agents to reduce Customer Load by using distribution voltage reduction measures, if deemed beneficial by the TSP, DSP, or their agents.

(ii)	Instruct TSPs and DSPs to implement any available Load management plans to reduce Customer Load.

(iii)	Instruct QSEs to deploy available contracted ERS-10 Resources, undeployed ERS-30 and/or deploy RRS supplied from Load Resources (controlled by high-set under-frequency relays).  ERCOT may deploy ERS-10, ERS-30, or RRS simultaneously or separately, and in any order.  ERCOT shall issue such Dispatch Instructions in accordance with the deployment methodologies described in paragraphs (iv) and (v) below and, if deploying ERS-30, the methodologies described in paragraph (1)(a)(iv) above.

(iv)	ERCOT shall deploy ERS-10 via an XML message followed by a VDI to the all-QSE Hotline.  The ERS-10 ramp period shall begin at the completion of the VDI.

(A)	If less than 500 MW of ERS-10 is available for deployment, ERCOT shall deploy all ERS-10 Resources as a single block.

(B)	If the amount of ERS-10 available for deployment equals or exceeds 500 MW, ERCOT, at its discretion, may deploy ERS-10 Resources as a single block or by group designation.  ERCOT shall develop a random selection methodology for determining how to place ERS-10 Resources into groups, and shall describe the methodology in a document posted to the MIS Public Area.  Prior to the start of an ERS-10 Contract Period, ERCOT shall notify QSEs representing ERS-10 Resources of their ERS-10 Resources’ group assignments.

(C)	ERS-10 may be deployed at any time in a Settlement Interval.

(D)	Upon deployment, QSEs shall instruct ERS-10 Resources to perform at contracted levels consistent with the criteria described in Section 8.1.3.1.4 until ERCOT releases the ERS-10 deployment or the ERS-10 Resources have reached their maximum deployment times.

(E)	ERCOT shall notify QSEs of the release of ERS-10 via an XML message followed by VDI to the all-QSE Hotline.  The VDI shall represent the official notice of ERS-10 release.  ERCOT may release ERS-10 as a block or by group designation.

(F)	Upon release, an ERS-10 Resource shall return to a condition such that it is capable of meeting its ERS performance requirements as soon as practical, but no later than ten hours following the release.

(v)	ERCOT shall deploy RRS capacity supplied by Load Resources (controlled by high-set under-frequency relays) in accordance with the following:

(A)	Instruct QSEs to deploy half of the RRS that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt Group 1 Load Resources providing Responsive Reserve.  QSEs shall deploy Load Resources according to the group designation and will be given some discretion to deploy additional Load Resources from Group 2 if Load Resource operational considerations require such.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;

(B)	At the discretion of the ERCOT Operator, instruct QSEs to deploy the remaining Responsive Reserve that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt Group 2 Load Resources providing Responsive Reserve. ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;

(C)	The ERCOT Operator may deploy both of the groups of Load Resources providing Responsive Reserves at the same time.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period; and

(D)	ERCOT shall post a list of Load Resources on the MIS Certified Area immediately following the DRUC for each QSE with a Load Resource obligation which may be deployed to interrupt under paragraph (A), Group 1 and paragraph (B), Group 2.  ERCOT shall develop a process for determining which individual Load Resource to place in Group 1 and which to place in Group 2.  ERCOT procedures shall select Group 1 and Group 2 based on a random sampling of individual Load Resources.  At ERCOT’s discretion, ERCOT may deploy all Load Resources at any given time during EEA Level 2.

(vi)	Unless a media appeal is already in effect, ERCOT shall issue an appeal through the public news media for voluntary energy conservation; and

(vii)	With the approval of the affected non-ERCOT Control Area, TSPs, DSPs, or their agents may implement BLTs, which transfer Load from the ERCOT Control Area to non-ERCOT Control Areas in accordance with BLTs as defined in the Operating Guides.

(b)	Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability.

(3)	ERCOT will declare an EEA Level 3 when steady state system frequency cannot be maintained at a minimum of 59.8 Hz or when PRC falls below 1,000 MW and is not projected to be recovered above 1,000 MW within 30 minutes without the use of the following actions that are prescribed for EEA Level 3:

(a)	In addition to measures associated with EEA Levels 1 and 2, ERCOT shall direct all TSPs and DSPs or their agents to shed firm Load, in 100 MW blocks, distributed as documented in the Operating Guides in order to maintain a steady state system frequency at a minimum of 59.8 Hz and to recover 1,000 MW of PRC within 30 minutes.

(b)	In addition to measures associated with EEA Levels 1 and 2, TSPs and DSPs or their agents will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens.  Whenever possible, TSPs and DSPs or their agents shall not manually drop Load connected to under-frequency relays during the implementation of the EEA.