## Slide 1: Material for 10/23/2015 PGDTF Meeting
Michael Juricek
Notes: 1

## Slide 2: Outline
  GMD Model
  GMD Assessment Process
    Transmission System
    Transformer Thermal Assessment

## Slide 3: GIC Data File Contents
  Required Data
    Geographic location of substations (longitude and latitude)
    Grounding resistance data for substations
    DC resistance of transformer windings
    Identification of GIC blocking device in the grounding connection
    Transformer vector group
  Optional Data for Transformers
    Number of cores
    K Factor

## Slide 4: GIC Data File Contents
  Three group records, with each group containing a particular type of data
    Substation Data
    Bus Substation Data
    Transformer Data

## Slide 5: Substation Data

## Slide 6: Substation Data Example

## Slide 7: Bus Substation Data

## Slide 8: Bus Substation Data Example

## Slide 9: Transformer Data
Notes: DC resistances, if left blank, will be calculated based on power flow data
User can choose to enter, CORE, KFACTOR, or enter “0” for both and k-factor will be determined based on base kV of transformer windings (as shown on next slide)

## Slide 10: Transformer MVAR Scaling Factors

## Slide 11: Transformer Data Example

## Slide 12: Outline
  GMD Model
  GMD Assessment Process
    Transmission System
    Transformer Thermal Assessment

## Slide 13: GMD Assessment Process Overview
Assemble model and equipment data
Create dc model of the system
Calculate GIC for each transformer
Calculate transformer reactive losses
Investigate mitigation options
Standard TPL Planning
GMD-specific Planning Steps
Identify voltage and system issues
Run ac power flow w/ reactive losses included
Conduct transformer thermal assessment

## Slide 14: Outline
  GMD Model
  GMD Assessment Process
    Transmission System
    Transformer Thermal Assessment

## Slide 15: TPL-007-1 Summary
R6 requires a Transformer Thermal Impact Assessment to ensure high-side, wye grounded BES transformers connected at 200kV or higher will not overheat based on the benchmark event
    Applies to transformers where effective GIC identified in GIC studies 75 A per phase or greater (not 75 A continuous). Effective 75 A per phase is a conservative screening criterion
    Approaches for conducting the assessment are presented in the Transformer Thermal Impact Assessment white paper posted on the project page http://www.nerc.com/pa/Stand/Pages/Project-2013-03-Geomagnetic-Disturbance-Mitigation.aspx
    Performed once every five years with GMD Vulnerability Assessment
    Applicability: Generator Owners, Transmission Owners