## Slide 1: Temperature Assumptions for Dynamic Ratings in ERCOT CRR Auctions Proposal to differentiate between Day (PeakWD & PeakWE) and Night (Off-peak)
October 23, 2015

## Slide 2: Contents
Current Methodology
Temperature Difference between Peak (Day) and Off-peak (Night)
Benefits
Is over-selling in the auction a risk? A look into nodal history
Proposed Changes
Appendix

## Slide 3: Current Methodology
According to ERCOT Nodal Protocols Section 7.5.5.4.3:
  (f) Thermal operating limits (including estimates for Dynamic Ratings) for transmission lines;
    (i) For a CRR Long-Term Auction Sequence, ERCOT shall use Dynamic Ratings based on a historical analysis of the maximum peak-hour temperatures for the previous ten years; and
    (ii) For the CRR Monthly Auction, ERCOT shall use Dynamic Ratings for the maximum peak-hour temperature forecast for the month;

## Slide 4: Peak vs. Off-Peak Temperatures
WZ | Mo | D* | N** | Current |  | D vs. N
COAST | Jan | 76.5 | 67.9 | 75 |  | 8.6
 | Feb | 78 | 69.1 | 80 |  | 8.9
 | Mar | 81.9 | 71.8 | 80 |  | 10.1
 | Apr | 85.8 | 76.4 | 85 |  | 9.4
 | May | 90.6 | 79.8 | 90 |  | 10.8
 | Jun | 96.2 | 84.9 | 95 |  | 11.3
 | Jul | 96.2 | 84.9 | 95 |  | 11.3
 | Aug | 98.2 | 85.8 | 100 |  | 12.4
 | Sep | 94.4 | 83.5 | 95 |  | 10.9
 | Oct | 90.1 | 79.8 | 90 |  | 10.3
 | Nov | 83.5 | 73.7 | 85 |  | 9.8
 | Dec | 78.2 | 70.9 | 80 |  | 7.3
Chart: Month
D | 76.5 | 78 | 81.9 | 85.8 | 90.6 | 96.2 | 96.2 | 98.2 | 94.4 | 90.1 | 83.5 | 78.2
N | 67.9 | 69.1 | 71.8 | 76.4 | 79.8 | 84.9 | 84.9 | 85.8 | 83.5 | 79.8 | 73.7 | 70.9
Current | 75 | 80 | 80 | 85 | 90 | 95 | 95 | 100 | 95 | 90 | 85 | 80
Coastal Weather Zone Example
* Day Hours defined as HE 700-2200 ** Night Hours defined as HE 100-600 and 2300-2400 Additional data for all other Weather Zones is in the Appendix A

## Slide 5: Benefits
  Representing the Off-peak system closer to Day-Ahead market expectation would better correlate CRRs as a hedging instrument for Loads and Generators in the Market for Off-peak hours
  Historical congestion in monthly auctions and Day-Ahead market show congestion during peak hours is ~16% more in the auctions than in Day-Ahead. However, the congestion in Off-peak hours is 49% higher in the auctions than in the Day-Ahead market. This causes an over valuation of Off-peak congestions risks, and therefore effectively increasing hedging costs in the Off-peak hours
  If we were to assume that the Day (PeakWD and PeakWE) “hedging premium” of 16% is correct, then the implied Off-peak congestion in the auctions should only be $2.34B, which is $65M less than what it is now for four years of history, that is roughly ~$16M per year for the market
* Data used is Jun 21st 2011 to September 28th 2015 for Day-Ahead
** July 2011 to September 2015 CRR auction results
CONGESTION RENTS ($M) |  |  |  | 
MARKET | DAY | NIGHT |  | TOTAL
DAY-AHEAD * | 1,824 | 195 |  | 2,019
MONTHLY AUCTION ** | 2,114 | 291 |  | 2,405
 | 16% | 49% |  | 19%
Better value expected Day-Ahead market in the Rolling/Monthly Auctions:

## Slide 6: Benefits
* Data used is Jun 21st 2011 to September 28th 2015 for Day-Ahead
** July 2011 to September 2015 CRR auction results
Better value expected Day-Ahead market in the Rolling/Monthly Auctions:
  Even though overvaluation of Off-peak for all history is ~49%, for given months it can reach up to 600% and most recent 12-month moving average shows it to be ~77%. Much higher than the trend observed for the “Day” (WD and WE) group

## Slide 7: Benefits
  This would allow to better represent the available capacity of the system given a forecasted (DAM) or telemetered (RTM) temperatures
    The Day-Ahead Market uses a temperature forecast for every weather zone and every hour to determine the expected dynamic rating of all dynamically rated equipment
    In Real-Time operations, ERCOT telemeters temperatures in the system every 15-minutes for every weather zone
Align the CRR models Day-Ahead and Real-Time Markets:

## Slide 8: Benefits
* Weather Assumptions (MIS Report ID 12325)
** Forecasted Temperature Adjusted Dynamic Ratings (MIS Report ID: 12346)
*** Real Time Dynamic Rating Data (MIS Report ID: 11024) **** Seq1 rolling and Monthly auction for Sep 2015 used the same temperature (and rating) assumption
Dynamic Ratings in Day-Ahead, Real-Time and Auction (With New Methodology)
Chart: Lukfin to Nacagdoches 138kV Line (East WZ) on Sep 29th, 2015

## Slide 9: Is over-selling in the auction a risk?
HISTORICAL DAM CONGESTION RENTS BY EQUIPMENT TYPE ($M)* |  |  |  | 
EQUIPMENT | DAY | NIGHT |  | TOTAL
INTERFACE | 58 | 31 |  | 90
XF | 426 | 50 |  | 476
LINE (STATIC) | 642 | 81 |  | 723
LINE (DYNAMIC) | 698 | 32 |  | 730
TOTAL: | 1,824 | 195 |  | 2,019
Chart: 
| INTERFACE | XFMR | LINE (STATIC) | LINE (DYNAMIC) | INTERFACE | XFMR | LINE (STATIC) | LINE (DYNAMIC)
 | 58.3869 | 426.1544 | 642.0456 | 697.5915 | 31.3671 | 50.1897 | 81.0044 | 32.4307
* Data used is Jun 21st 2011 to September 28th 2015
  Only $32M (~1.6%) of Historical Day-Ahead Market Congestion was on Dynamically Rated Lines during Off-peak hours
A look into DA Congestion in ERCOT for the last four years:

## Slide 10
* Summation of Rating B for equipment in CIM SEP ML4
  According to table below, dynamically rated lines would have in average 5% more capacity in the Off-peak auction for the entire year. The highest change would be in the summer months with ~5.7% increase
  As for the entire system, the additional capacity is ~2.2% for the annual average, with its peak in the summer of about 2.6%
Percentage increase in System Capacity* for the Off-peak (Night) Cases with this new methodology:
PCNT INCREASE CAPACITY FOR OFF-PEAK COMPARED TO PEAK RATINGS (%) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
SCENARIO |  | INCLUDED IN CALCULATION? |  |  |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Avg
 |  | XFMR | LINE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  |  | STATIC | DYNAMIC |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
ALL SYSTEM |  | YES | YES | YES |  | 1.9 | 2.1 | 2.3 | 2.3 | 2.3 | 2.4 | 2.4 | 2.7 | 2.5 | 2.2 | 2.0 | 1.9 |  | 2.2
TRANS. LINES ONLY |  | NO | YES | YES |  | 2.3 | 2.6 | 2.8 | 2.8 | 2.8 | 3.0 | 3.0 | 3.3 | 3.0 | 2.6 | 2.5 | 2.3 |  | 2.7
DYNAMIC LINES ONLY |  | NO | NO | YES |  | 4.1 | 4.7 | 5.1 | 5.1 | 5.2 | 5.5 | 5.5 | 6.2 | 5.6 | 4.8 | 4.5 | 4.1 |  | 5.0
Is over-selling in the auction a risk?

## Slide 11: Proposed Changes
  Utilize different temperature assumptions between Day (PeakWD and PeakWE) and Night (Off-peak) CRR cases
  The methodology to derive the Day** and Night** temperature assumptions uses the same analysis as the current methodology, except that it uses two datasets, one for Day (HE 700 to 2200) and another one for Night (HE 100-600 and 2300-2400)
 | Methodology to choose Temperatures for Auction Models |  |  |  |  |  | 
 | Currently |  |  |  | Proposed |  | 
Auction | PeakWD | PeakWE | Off-peak |  | PeakWD | PeakWE | Off-peak
Rolling | 10Y Historical Analysis (No day/night distinction)* |  |  |  | 10Y Historical Analysis (DAY**) |  | 10Y Historical Analysis (NIGHT***)
Monthly | ERCOT Fcst* |  |  |  | ERCOT On-Peak Fcst |  | ERCOT Off-Peak Fcst? Same method as rolling? A combination between ERCOT Peak Fcst and 10Y Historical DAY to derive a NIGHT “multiplier” or “adder”
*ERCOT Nodal Protocols Section 7.5.5.4.3 |  |  |  |  |  |  | 
**Day Hours defined as HE 700-2200 |  |  |  |  |  |  | 
*** Night Hours defined as HE 100-600 and 2300-2400 |  |  |  |  |  |  | 

## Slide 12: Appendix A

## Slide 13: Appendix A – Weather Zone Temperature Day vs. Night
WZ | Mo | D | N | Current |  | D vs. N
COAST | Jan | 76.5 | 67.9 | 75 |  | 8.6
 | Feb | 78 | 69.1 | 80 |  | 8.9
 | Mar | 81.9 | 71.8 | 80 |  | 10.1
 | Apr | 85.8 | 76.4 | 85 |  | 9.4
 | May | 90.6 | 79.8 | 90 |  | 10.8
 | Jun | 96.2 | 84.9 | 95 |  | 11.3
 | Jul | 96.2 | 84.9 | 95 |  | 11.3
 | Aug | 98.2 | 85.8 | 100 |  | 12.4
 | Sep | 94.4 | 83.5 | 95 |  | 10.9
 | Oct | 90.1 | 79.8 | 90 |  | 10.3
 | Nov | 83.5 | 73.7 | 85 |  | 9.8
 | Dec | 78.2 | 70.9 | 80 |  | 7.3
Chart: Month
D | 76.5 | 78 | 81.9 | 85.8 | 90.6 | 96.2 | 96.2 | 98.2 | 94.4 | 90.1 | 83.5 | 78.2
N | 67.9 | 69.1 | 71.8 | 76.4 | 79.8 | 84.9 | 84.9 | 85.8 | 83.5 | 79.8 | 73.7 | 70.9
Current | 75 | 80 | 80 | 85 | 90 | 95 | 95 | 100 | 95 | 90 | 85 | 80
Coastal:

## Slide 14: Appendix A – Weather Zone Temperature Day vs. Night
WZ | Mo | D | N | Current |  | D vs. N
EAST | Jan | 77 | 67.3 | 75 |  | 9.7
 | Feb | 78.4 | 68.3 | 80 |  | 10.1
 | Mar | 84 | 71.3 | 85 |  | 12.7
 | Apr | 87.8 | 75.5 | 90 |  | 12.3
 | May | 92.2 | 79.8 | 95 |  | 12.4
 | Jun | 97.8 | 85 | 100 |  | 12.8
 | Jul | 99.6 | 86.5 | 100 |  | 13.1
 | Aug | 101.1 | 87.2 | 100 |  | 13.9
 | Sep | 96.6 | 82.9 | 95 |  | 13.7
 | Oct | 90.4 | 77.7 | 90 |  | 12.7
 | Nov | 82.7 | 71.4 | 85 |  | 11.3
 | Dec | 77 | 69.9 | 80 |  | 7.1
Eastern:
Chart: 
D | 77 | 78.4 | 84 | 87.8 | 92.2 | 97.8 | 99.6 | 101.1 | 96.6 | 90.4 | 82.7 | 77
N | 67.3 | 68.3 | 71.3 | 75.5 | 79.8 | 85 | 86.5 | 87.2 | 82.9 | 77.7 | 71.4 | 69.9
Current | 75 | 80 | 85 | 90 | 95 | 100 | 100 | 100 | 95 | 90 | 85 | 80

## Slide 15: Appendix A – Weather Zone Temperature Day vs. Night
WZ | Mo | D | N | Current |  | D vs. N
FWEST | Jan | 78.8 | 59.6 | 80 |  | 19.2
 | Feb | 82.6 | 64.4 | 85 |  | 18.2
 | Mar | 90.2 | 72.4 | 90 |  | 17.8
 | Apr | 95.8 | 78.3 | 95 |  | 17.5
 | May | 102.1 | 85.7 | 105 |  | 16.4
 | Jun | 106.7 | 90.8 | 105 |  | 15.9
 | Jul | 103.1 | 90.6 | 105 |  | 12.5
 | Aug | 102.9 | 90 | 105 |  | 12.9
 | Sep | 99.1 | 84.9 | 100 |  | 14.2
 | Oct | 93.6 | 78 | 95 |  | 15.6
 | Nov | 84.7 | 66.3 | 85 |  | 18.4
 | Dec | 79.4 | 59.3 | 80 |  | 20.1
Far West:
Chart: 
D | 78.8 | 82.6 | 90.2 | 95.8 | 102.1 | 106.7 | 103.1 | 102.9 | 99.1 | 93.6 | 84.7 | 79.4
N | 59.6 | 64.4 | 72.4 | 78.3 | 85.7 | 90.8 | 90.6 | 90 | 84.9 | 78 | 66.3 | 59.3
Current | 80 | 85 | 90 | 95 | 105 | 105 | 105 | 105 | 100 | 95 | 85 | 80

## Slide 16: Appendix A – Weather Zone Temperature Day vs. Night
WZ | Mo | D | N | Current |  | D vs. N
NCENT | Jan | 77.5 | 65.8 | 80 |  | 11.7
 | Feb | 80.9 | 67.8 | 80 |  | 13.1
 | Mar | 85.7 | 72.9 | 85 |  | 12.8
 | Apr | 89.8 | 77.7 | 90 |  | 12.1
 | May | 94 | 82.4 | 95 |  | 11.6
 | Jun | 99.5 | 87.9 | 100 |  | 11.6
 | Jul | 102.1 | 90.4 | 100 |  | 11.7
 | Aug | 104 | 91.1 | 105 |  | 12.9
 | Sep | 99.2 | 86.9 | 100 |  | 12.3
 | Oct | 91.5 | 80.5 | 90 |  | 11
 | Nov | 84.1 | 72.4 | 85 |  | 11.7
 | Dec | 79.3 | 66.5 | 80 |  | 12.8
North Central:
Chart: 
D | 77.5 | 80.9 | 85.7 | 89.8 | 94 | 99.5 | 102.1 | 104 | 99.2 | 91.5 | 84.1 | 79.3
N | 65.8 | 67.8 | 72.9 | 77.7 | 82.4 | 87.9 | 90.4 | 91.1 | 86.9 | 80.5 | 72.4 | 66.5
Current | 80 | 80 | 85 | 90 | 95 | 100 | 100 | 105 | 100 | 90 | 85 | 80

## Slide 17: Appendix A – Weather Zone Temperature Day vs. Night
WZ | Mo | D | N | Current |  | D vs. N
NORTH | Jan | 74.9 | 62.8 | 75 |  | 12.1
 | Feb | 77.7 | 64.7 | 80 |  | 13
 | Mar | 84.5 | 71.1 | 85 |  | 13.4
 | Apr | 88.1 | 75.2 | 90 |  | 12.9
 | May | 93.3 | 80.4 | 95 |  | 12.9
 | Jun | 99.6 | 85.2 | 100 |  | 14.4
 | Jul | 102.3 | 87.6 | 100 |  | 14.7
 | Aug | 103.5 | 88.8 | 105 |  | 14.7
 | Sep | 98.1 | 84 | 100 |  | 14.1
 | Oct | 89.7 | 76.5 | 90 |  | 13.2
 | Nov | 82 | 70 | 80 |  | 12
 | Dec | 74.5 | 63.4 | 75 |  | 11.1
Northern:
Chart: 
D | 74.9 | 77.7 | 84.5 | 88.1 | 93.3 | 99.6 | 102.3 | 103.5 | 98.1 | 89.7 | 82 | 74.5
N | 62.8 | 64.7 | 71.1 | 75.2 | 80.4 | 85.2 | 87.6 | 88.8 | 84 | 76.5 | 70 | 63.4
Current | 75 | 80 | 85 | 90 | 95 | 100 | 100 | 105 | 100 | 90 | 80 | 75

## Slide 18: Appendix A – Weather Zone Temperature Day vs. Night
WZ | Mo | D | N | Current |  | D vs. N
SCENT | Jan | 79.5 | 67.8 | 80 |  | 11.7
 | Feb | 84.2 | 69.3 | 85 |  | 14.9
 | Mar | 87.7 | 72.1 | 90 |  | 15.6
 | Apr | 91.7 | 77.4 | 90 |  | 14.3
 | May | 94.3 | 80.9 | 95 |  | 13.4
 | Jun | 99.5 | 87.4 | 100 |  | 12.1
 | Jul | 99.6 | 87.5 | 100 |  | 12.1
 | Aug | 102.5 | 89.1 | 100 |  | 13.4
 | Sep | 99.3 | 86.5 | 100 |  | 12.8
 | Oct | 92 | 80.1 | 90 |  | 11.9
 | Nov | 85.2 | 73.4 | 85 |  | 11.8
 | Dec | 80.1 | 69.8 | 80 |  | 10.3
South Central:
Chart: 
D | 79.5 | 84.2 | 87.7 | 91.7 | 94.3 | 99.5 | 99.6 | 102.5 | 99.3 | 92 | 85.2 | 80.1
N | 67.8 | 69.3 | 72.1 | 77.4 | 80.9 | 87.4 | 87.5 | 89.1 | 86.5 | 80.1 | 73.4 | 69.8
Current | 80 | 85 | 90 | 90 | 95 | 100 | 100 | 100 | 100 | 90 | 85 | 80

## Slide 19: Appendix A – Weather Zone Temperature Day vs. Night
WZ | Mo | D | N | Current |  | D vs. N
SOUTH | Jan | 82.5 | 71 | 85 |  | 11.5
 | Feb | 86 | 71.9 | 85 |  | 14.1
 | Mar | 90.8 | 74.5 | 90 |  | 16.3
 | Apr | 93.8 | 79.5 | 95 |  | 14.3
 | May | 94.7 | 82.1 | 95 |  | 12.6
 | Jun | 97.8 | 85.1 | 100 |  | 12.7
 | Jul | 97.2 | 84.9 | 95 |  | 12.3
 | Aug | 99.7 | 85.9 | 100 |  | 13.8
 | Sep | 97.6 | 84.7 | 100 |  | 12.9
 | Oct | 93.5 | 82.1 | 95 |  | 11.4
 | Nov | 87.2 | 76.2 | 85 |  | 11
 | Dec | 82.7 | 71.7 | 85 |  | 11
Southern:
Chart: 
D | 82.5 | 86 | 90.8 | 93.8 | 94.7 | 97.8 | 97.2 | 99.7 | 97.6 | 93.5 | 87.2 | 82.7
N | 71 | 71.9 | 74.5 | 79.5 | 82.1 | 85.1 | 84.9 | 85.9 | 84.7 | 82.1 | 76.2 | 71.7
Current | 85 | 85 | 90 | 95 | 95 | 100 | 95 | 100 | 100 | 95 | 85 | 85

## Slide 20: Appendix A – Weather Zone Temperature Day vs. Night
WZ | Mo | D | N | Current |  | D vs. N
WEST | Jan | 80.5 | 62.2 | 80 |  | 18.3
 | Feb | 83.7 | 66.8 | 85 |  | 16.9
 | Mar | 89.4 | 72.3 | 90 |  | 17.1
 | Apr | 94.2 | 78.8 | 95 |  | 15.4
 | May | 98.4 | 83.6 | 100 |  | 14.8
 | Jun | 100.6 | 87.4 | 100 |  | 13.2
 | Jul | 101.5 | 88.9 | 100 |  | 12.6
 | Aug | 102.3 | 89.1 | 100 |  | 13.2
 | Sep | 98.4 | 84.6 | 100 |  | 13.8
 | Oct | 92 | 77.8 | 90 |  | 14.2
 | Nov | 84.2 | 68.9 | 85 |  | 15.3
 | Dec | 80.4 | 62.7 | 80 |  | 17.7
Western:
Chart: 
D | 80.5 | 83.7 | 89.4 | 94.2 | 98.4 | 100.6 | 101.5 | 102.3 | 98.4 | 92 | 84.2 | 80.4
N | 62.2 | 66.8 | 72.3 | 78.8 | 83.6 | 87.4 | 88.9 | 89.1 | 84.6 | 77.8 | 68.9 | 62.7
Current | 80 | 85 | 90 | 95 | 100 | 100 | 100 | 100 | 100 | 90 | 85 | 80