| NOGRR Number | 147 | NOGRR Title | Reactive Power Testing Requirements |
| --- | --- | --- | --- |
| Date of Decision |  | October 22, 2015 |  |
| Action |  | Tabled |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | To be determined. |  |
| Priority and Rank Assigned |  | To be determined. |  |
| Guide Sections Requiring Revision |  | 3.3.2.1, Corrected Unit Reactive Limits (CURL) 3.3.2.2, Non-Coordinated Reactive Testing 3.3.2.3, Coordinated Reactive Testing (delete) 3.5, ERCOT Implementation |  |
| Related Documents Requiring Revision/Revision Requests |  | Nodal Protocol Revision Request (NPRR) 713, Reactive Power Testing Requirements. |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) revises the language in Section 3.3.2.1, Corrected Unit Reactive Limits (CURL), to harmonize the ERCOT reactive testing requirements with the recently approved North American Electric Reliability Corporation (NERC) Reliability Standards. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | Implementation of these changes will eliminate the need to have duplicative reactive test procedures for satisfying the regulatory requirements of both the ERCOT Protocols and Operating Guides and the NERC Reliability standards. These duplicative procedures would cause confusion in training and operating procedures for the plant personnel who perform the testing in the field. The change of the periodicity of testing from two to five years will decrease the probable number of hours when Generation Resources may be required to run uneconomically to comply with testing requirements. |  |
| OWG Decision |  | On 7/23/15, the Operations Working Group (OWG) was in consensus to table NOGRR147. On 9/17/15, OWG was in consensus to recommend approval of NOGRR147 as amended by the 9/8/15 Reactive Power Testing Requirements Workshop comments. On 10/22/15, OWG was in consensus to table NOGRR147. |  |
| Summary of OWG Discussion |  | On 7/23/15, participants agreed that additional time for submission of comments from Market Participants would be beneficial. On 9/17/15, participants discussed the 9/15/15 Oncor comments but agreed the language in the 9/8/15 Reactive Power Testing Requirements Workshop comments was sufficient. On 10/22/15, participants reviewed the 10/15/15 ERCOT comments. |  |

| Sponsor |  |
| --- | --- |
| Name | Sherry K. Looney |
| E-mail Address | Sherry.looney@luminant.com |
| Company | Luminant Energy Company LLC |
| Phone Number | 214-875-9278 |
| Cell Number | 469-688-7607 |
| Market Segment | Independently Owned Utility (IOU) |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brian Manning |
| E-Mail Address | Brian.manning@ercot.com |
| Phone Number | 512-248-3937 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Oncor 081315 | Aligned the language in NOGRR147 with the associated NPRR713. |
| CenterPoint Energy 081915 | Proposed additional posting requirements and that OWG form a workshop to facilitate the changes proposed in NOGRR147 and associated NPRR713. |
| Reactive Power Testing Requirements WS 090315 | Provided additional edits to the 8/19/15 CenterPoint Energy comments. |
| Reactive Power Testing Requirements WS 090815 | Corrected the previous comments submitted by the Reactive Power Testing Requirements Workshop. |
| Oncor 091515 | Proposed additional clarifying edits to Intermittent Renewable Resource (IRR) testing requirements. |
| ERCOT 101515 | Requested additional time for development of a revised Impact Analysis. |

Market Rules Notes

None.

Proposed Guide Language

- 3.3.2.1	Corrected Unit Reactive Limits (CURL)

A reactive capability curve and associated data for each unit on the ERCOT System shall be submitted to ERCOT through the Market Information System (MIS) Certified Area and must contain the most limiting elements for the leading and lagging reactive output.  The limiting factors such as under-excitation limiters, over-excitation limiters, ambient temperature limitations across the MW range of the unit at the unit terminals or any other factor that limits the reactive output of the unit and is verifiable through engineering calculations or testing shall be updated and provided on the corrected reactive capability curve.  The corrected reactive capability curve establishes the Corrected Unit Reactive Limits (CURL) at the unit terminals that ERCOT Planning and ERCOT Operations, and TSPs will use for their studies. For IRR’s the CURL data shall be reported at the low side of the generator step up transformer to the Point of Interconnection (POI).  Resources will provide these updated curves and associated test data to ERCOT by submitting test information to the Net Dependable Capability and Reactive Capability (NDCRC) application located on the Market Information System (MIS) Secure Area.  Once approved by ERCOT per Section 3.5, ERCOT Implementation, Resources will provide updated data by submitting changes to the appropriate ERCOT Resource Asset Registration Forms (RARF) in accordance with the Planning Guide, Resource Registration Process. Prior to including the submitted data into the Network Operations Model, ERCOT will notify the TSP to which the Resource Entity is interconnected that the test data is posted on the MIS Secure Area.  ERCOT and TSPs may review the data and provide any comments within ten Business Days.  ERCOT  will include these changes in the future Network Operations Model and forward the changes to the TSPs and the Steady State Working Group (SSWG) for use in their studies. The CURL should be available in the Resource Entities control room where the tests are conducted and at the QSEs Real Time generation dispatch desk.  During any test, the Generation Resource must maintain its generator cooling system at normal operating conditions, the automatic voltage regulator in service and all auxiliary equipment in service that’s needed for expected normal operation.

- 3.3.2.2	Reactive Testing Requirements

(1)	Reactive testing may be performed as either “Coordinated”, or “Non-Coordinated”, the difference being the amount of notification provided to ERCOT and the TO, and level of their involvement in testing.

(a)	Coordinated Testing

(i)	Coordinated testing is the preferred method for new or larger-capacity units, as it provides a greater amount of coordination with ERCOT and the TO, allowing testing impacts and any potential adjustments to local voltage levels to be studied in advance.

(ii)	The Resource Entity requesting a Coordinated test must submit a test request to ERCOT and the TO via their QSE, by no later than 15:00, one day prior to the proposed test date.  ERCOT and the TO then have until 17:00 of the day prior to the proposed test date, to either approve or disapprove the test request.

(iii)	Both ERCOT and the TO have the right to deny or cancel a test at any time, if they feel that system reliability may be adversely impacted by the test.

(iv)	The test requests should contain the proposed time and date of the test, type of test (leading or lagging), expected unit MW and MVAR output range during the test, and a copy of the reactive capability curve.

(b)	Non-Coordinated Testing

(i)	The Resource Entity representing the resource requesting a Non-Coordinated test must inform ERCOT and the TO via their QSE at least two hours prior to the proposed start of the test.

(ii)	Both ERCOT and the TO have the right to deny or cancel a test at any time, if they feel that system reliability may be adversely impacted by the test.

(2)	Lagging Reactive Testing

(a)	It is recommended, but not required, that lagging reactive tests be performed when system voltage is within the voltage profile, such as during high load periods.

(b)	Lagging tests should meet the following performance criteria:

(i)	Lagging Test 1:  Test at or above 95% of the unit’s High Sustained Limit (HSL) for at least 15 minutes.  Intermittent Renewable Resources (IRRs) should test at or above 60% of their HSL.  Testing acceptance criteria is met if the unit achieved  no less than 90% of the unit’s most recent CURL.

(ii)	Lagging Test 2:  Test at the unit’s HSL for at least 1 hour. IRRs should test with at least 90% of photovoltaic inverters or wind turbines on-line. Testing acceptance criteria is met if the unit achieved at least 50% of the units CURL for one hour.

(iii)	Lagging Test 3:  Test at the unit’s normally expected minimum real power output during system light load conditions for at least 1 minute.  IRRs and Nuclear units are exempt from this test. Testing acceptance criteria is met if the unit achieved  at least 50% of the unit’s CURL.

(3)	Leading Reactive Testing

(a)	It is recommended, but not required, that leading reactive tests be performed when system voltage is within the voltage profile, such as during low load periods.

(b)	Leading tests should meet the following performance criteria:

(i)	Leading Test 1:  Test at the unit’s normally expected maximum real power output during system light load conditions for at least 15 minutes.  IRRs should test at or below 60% of their HSL. Testing acceptance criteria is met if the unit achieved  no less than 90% of the units original manufacturer reactive curve or most recent CURL.

(ii)	Leading Test 2:  Test at the unit’s HSL for at least 1 minute.  IRR units are exempt from this test.  Testing acceptance criteria is met if the unit achieved  at least 50% of the units CURL.

(iii)	Leading Test 3:  Test at the unit’s normally expected minimum real power output during system light load conditions for at least 1 minute.  IRRs and Nuclear units are exempt from this test. Testing acceptance criteria is met if the unit achieved  at least 50% of the units CURL.

(4)	The Resource Entity shall measure the tested reactive capability on the generator output terminals for non-IRR Generation Resources  The value recorded shall represent the gross MVAr output of the Generation Resource.  Additionally, the net reactive capability shall be measured at the high side of the GSU transformer and at the POI, if metering is available.  The high side values shall have the Generation Resource’s auxiliary reactive consumption and the GSU losses deducted from the Generation Resource’s gross reactive output.  The POI values shall have the plant’s auxiliary load and any additional load deducted from the Generation Resource’s gross reactive output. If metering is not available at the high side, the Resource Entity shall calculate the reactive capability at the high side and at the POI.  These values are required and must be submitted through the MIS Certified Area.  CURLs shall be attached to the test results submitted, and shall be clearly defined.  All applicable test data shall be submitted on the form in the NDCRC application.

(5)	The QSE representing a Generation Resource shall be responsible for scheduling reactive verification tests when requested by the Resource Entity in accordance with the conditions outlined above.  If ERCOT does not issue a specific request for a Generation Resource reactive capability verification, the Generation Resource shall complete a reactive verification test at least every five years.

(6)	ERCOT shall have the option to waive the requirement to perform Leading Test 1 for any Generation Resource that seldom runs during such light Load periods.  The granting of such a waiver shall be effective for five years.

(7)

The Resource Entity representing a Generation Resource shall be responsible for the timely and accurate reporting of test results to ERCOT  and to the QSE representing the Generation Resource.  The Resource Entity representing a Generation Resource must properly complete all required data fields in the NDCRC application for a test to be considered valid.

3.5	ERCOT Implementation

(1)	Reactive test results shall be reviewed by ERCOT to validate the accuracy and consistency of the test data provided, and to determine the appropriateness of unit loading and system conditions during the test.  ERCOT shall have the right to order a re-test of the unit, if it determines there are significant discrepancies with the test data.

(2)	Reactive test results shall be reviewed by ERCOT to determine if test results met the acceptance criteria of Section 3.3.2.2, Reactive Testing Requirements.  If the test results fail to meet the acceptance criteria of Section 3.3.2.2, ERCOT shall have the right to either order the Resource Entity to produce a new CURL, or to order a re-test of the unit.

(3)	Reactive test results shall be reviewed by ERCOT against the most recent CURL for the unit.  If unit reactive capability appears to fail the acceptance criteria of Section 3.3.2.2 , ERCOT shall contact the Resource Entity and attempt to resolve the limitation.  ERCOT shall have the right to order the Resource Entity to produce a new CURL that reflects current operating limits.

(4)	Any new CURL produced by a Resource Entity in response to new operating limits, shall be submitted by the Resource via the Resource Asset Registration Form (RARF)  within four weeks of ERCOT’s approval of the test. ERCOT will notify TSPs after RARF submittal as described in Section 3.3.2.1, Corrected Unit Reactive Limits (CURL).