## Summary
Release Date: November 2, 2015
FINAL
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Winter 2015/2016
SUMMARY
The ERCOT Region is expected to have sufficient installed generating capacity to serve forecasted peak demands in the upcoming winter season (December 2015 - February 2016). Based on the results of this study, an extreme higher-than-normal number of forced generation outages occurring during a period of unusually high demand would be unlikely to result in insufficient resources being available to serve those demands. Even if those conditions coincide with extremely low temperatures and associated capacity reductions resulting from natural gas curtailments, current information indicates that there would be sufficient generation available on a systemwide basis.
This capacity outlook includes the same peak forecast used for the preliminary winter SARA report released September 1, 2015, reflecting our peak forecast expectations based on customer demand experienced during recent winter season cold-weather events and current expectations for average weather in the upcoming winter season. Total resource capacity also increased by nearly 1,100 MW relative to capacity reported in the preliminary winter SARA. The increase was due to the return to service of coal units previously in seasonal mothball status, as well as several wind and gas resources recategorized from planned to operational status.
ERCOT will continue to monitor the potential effect of future drought conditions on generation capacity and ongoing changes to environmental regulations.

## Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Winter 2015/2016 - Final
Release Date: November 2, 2015
Forecasted Capacity and Demand
|  | Operational Resources (excluding wind), MW | 68063.34 | Based on current ratings reported through the unit registration process
|  | Switchable Capacity Total, MW | 3702 | Rated capacity of resources that can interconnect with other regions and are available to ERCOT
|  | less Switchable Capacity Unavailable to ERCOT, MW | -470 | Based on survey responses of Switchable Resource owners
|  | Mothball Resources, MW | 0 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
|  | Private Use Network Capacity Contribution, MW | 4433 | Average capability of the top 20 hours in the winter peak seasons for the past three years
|  | Non-Coastal Wind Resources Capacity Contribution, MW | 2286.972 | Based on 18% of rated capacity for non-coastal wind resources per Nodal Protocols Section 3.2.6.2.2
|  | Coastal Wind Resources Capacity Contribution, MW | 621.748 | Based on 37% of rated capacity for coastal wind resources per Nodal Protocols Section 3.2.6.2.2
|  | RMR Resources to be under Contract, MW | 0 | No RMR resources currently under contract
|  | Non-Synchronous Ties Capacity Contribution, MW | 371.4 | Average capability of the top 20 hours in the winter peak seasons for the past three years
|  | Planned Resources (not wind), MW | 7.4 | Based on projected dates provided by developers of generation resources
|  | Planned Non-Coastal Wind, MW | 189 | Based on projected dates and 18% of rated capacity for non-coastal wind resources
|  | Planned Coastal Wind, MW | 135.79 | Based on projected dates and 37% of rated capacity for coastal wind resources
| [a] Total Resources, MW |  | 79340.65
| [b] Peak Demand, MW |  | 57400 | Peak forecast is based on expected demand and weather conditions for winter 2015
| [c] Reserve Capacity [a - b], MW |  | 21940.65
Range of Potential Scenarios
|  |  | Forecasted Season Peak Load | Extreme Peak Load / Typical Generation Outages | Extreme Peak Load / Extreme Generation Outages
|  | Peak Load Adjustment (1) | 0 | 3434 | 3434
|  | Typical Maintenance Outages (2) | 4061 | 4061 | 4061
|  | Typical Forced Outages (2) | 3756 | 5268 | 5268
|  | Extreme Forced Outages (4) | 0 | 0 | 4584
| [d] Total Uses of Reserve Capacity |  | 7817 | 12763 | 17347
| [e] Capacity Available for Operating Reserves (c-d), MW |  | 14123.65 | 9177.65 | 4593.65
Less than 2,300 MW indicates risk of EEA1
(1) Winter Peak Load Extreme Forecast is 60,834 MW based on the 90th percentile level.
(2) Maintenance Outages and Forced Outages based on average of historical outage data for December, January and February weekdays, hours ending 7 am to 10 am (starting in 2010).
(3) Includes typical outages/derates due to natural gas curtailments during extreme peak load hours.
(4) Extreme Forced Outages include forecasted derates due to natural gas curtailments at low ambient temperatures during extreme peak load hours.
(3)
(3)

## Winter_Capacities
Unit Capacities - Winter
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | ZONE | START YEAR | CAPACITY (MW)
Operational Resources
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1235
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1225
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1350
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1354
8 | BIG BROWN U1 |  | BBSES_UNIT1 | FREESTONE | COAL | NORTH | 1971 | 606
9 | BIG BROWN U2 |  | BBSES_UNIT2 | FREESTONE | COAL | NORTH | 1972 | 602
10 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 660
11 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 603
12 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 605
13 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 449
14 | GIBBONS CREEK U1 |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 470
15 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560
16 | J K SPRUCE U2 | 09INR0002 | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 775
17 | J T DEELY U1 |  | CALAVERS_JTD1 | BEXAR | COAL | SOUTH | 1977 | 420
18 | J T DEELY U2 |  | CALAVERS_JTD2 | BEXAR | COAL | SOUTH | 1978 | 420
19 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 831
20 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 858
21 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 820
22 | MONTICELLO U1 |  | MNSES_UNIT1 | TITUS | COAL | NORTH | 1974 | 580
23 | MONTICELLO U2 |  | MNSES_UNIT2 | TITUS | COAL | NORTH | 1975 | 580
24 | MONTICELLO U3 |  | MNSES_UNIT3 | TITUS | COAL | NORTH | 1978 | 795
25 | OAK GROVE SES U1 | 09INR0006a | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 840
26 | OAK GROVE SES U2 | 09INR0006b | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 825
27 | OKLAUNION U1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650
28 | SAN MIGUEL U1 |  | SANMIGL_SANMIGG1 | ATASCOSA | COAL | SOUTH | 1982 | 391
29 | SANDOW U5 | 08INR0003 | SD5SES_UNIT5 | MILAM | COAL | SOUTH | 2010 | 600
30 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 970
31 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 158
32 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 158
33 | W A PARISH U5 |  | WAP_WAP_G5 | FT. BEND | COAL | HOUSTON | 1977 | 659
34 | W A PARISH U6 |  | WAP_WAP_G6 | FT. BEND | COAL | HOUSTON | 1978 | 658
35 | W A PARISH U7 |  | WAP_WAP_G7 | FT. BEND | COAL | HOUSTON | 1980 | 577
36 | W A PARISH U8 |  | WAP_WAP_G8 | FT. BEND | COAL | HOUSTON | 1982 | 610
37 | ARTHUR VON ROSENBERG 1 CTG 1 | 00INR0017 | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 149
38 | ARTHUR VON ROSENBERG 1 CTG 2 | 00INR0017 | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 149
39 | ARTHUR VON ROSENBERG 1 STG | 00INR0017 | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 160
40 | BARNEY M DAVIS REPOWER CTG 3 | 09INR0038 | B_DAVIS_B_DAVIG3 | NUECES | GAS | COASTAL | 2010 | 165
41 | BARNEY M DAVIS REPOWER CTG 4 | 09INR0038 | B_DAVIS_B_DAVIG4 | NUECES | GAS | COASTAL | 2010 | 165
42 | BARNEY M DAVIS REPOWER STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | COASTAL | 1976 | 325
43 | BASTROP ENERGY CENTER CTG 1 | 01INR0021 | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 167
44 | BASTROP ENERGY CENTER CTG 2 | 01INR0021 | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 167
45 | BASTROP ENERGY CENTER STG | 01INR0021 | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 234
46 | BOSQUE ENERGY CENTER CTG 1 | 00INR0018 | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 170.9
47 | BOSQUE ENERGY CENTER STG 4 | 00INR0028 | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 85.2
48 | BOSQUE ENERGY CENTER CTG 2 | 00INR0018 | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 170.9
49 | BOSQUE ENERGY CENTER CTG 3 | 00INR0018 | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 168.5
50 | BOSQUE ENERGY CENTER STG 5 | 08INR0046 | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 226.7
51 | BRAZOS VALLEY CTG 1 | 01INR0031 | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 168
52 | BRAZOS VALLEY CTG 2 | 01INR0031 | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 168
53 | BRAZOS VALLEY STG 3 | 01INR0031 | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 270
54 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 77.5
55 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 77.5
56 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 74
57 | CEDAR BAYOU 4 CTG 1 | 08INR0035 | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 173
58 | CEDAR BAYOU 4 CTG 2 | 08INR0035 | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 173
59 | CEDAR BAYOU 4 STG | 08INR0035 | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 186
60 | COLORADO BEND ENERGY CENTER CTG 1 | 06INR0035b | CBEC_GT1 | WHARTON | GAS | SOUTH | 2007 | 79
61 | COLORADO BEND ENERGY CENTER CTG 2 | 06INR0035b | CBEC_GT2 | WHARTON | GAS | SOUTH | 2007 | 72
62 | COLORADO BEND ENERGY CENTER STG 1 | 06INR0035b | CBEC_STG1 | WHARTON | GAS | SOUTH | 2007 | 102
63 | COLORADO BEND ENERGY CENTER CTG 3 | 06INR0035a | CBEC_GT3 | WHARTON | GAS | SOUTH | 2008 | 77
64 | COLORADO BEND ENERGY CENTER CTG 4 | 06INR0035a | CBEC_GT4 | WHARTON | GAS | SOUTH | 2008 | 73
65 | COLORADO BEND ENERGY CENTER STG 2 | 06INR0035a | CBEC_STG2 | WHARTON | GAS | SOUTH | 2008 | 108
66 | CVC CHANNELVIEW CTG 1 | 02INR0004 | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 191
67 | CVC CHANNELVIEW CTG 2 | 02INR0004 | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 189
68 | CVC CHANNELVIEW CTG 3 | 02INR0004 | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 189
69 | CVC CHANNELVIEW STG 5 | 02INR0004 | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 146
70 | DEER PARK ENERGY CENTER CTG 1 | 02INR0020 | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 203
71 | DEER PARK ENERGY CENTER CTG 2 | 02INR0020 | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 215
72 | DEER PARK ENERGY CENTER CTG 3 | 02INR0020 | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 203
73 | DEER PARK ENERGY CENTER CTG 4 | 02INR0020 | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 215
74 | DEER PARK ENERGY CENTER STG | 02INR0020 | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 290
75 | DEER PARK ENERGY CENTER CTG 6 | 14INR0015 | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 190
76 | ENNIS POWER STATION CTG 2 | 01INR0008 | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 231
77 | ENNIS POWER STATION STG 1 | 01INR0008 | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 127
78 | FERGUSON REPLACEMENT CTG1 | 13INR0021 | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 186.1
79 | FERGUSON REPLACEMENT CTG2 | 13INR0021 | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 186.1
80 | FERGUSON REPLACEMENT STG | 13INR0021 | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 194.9
81 | FORNEY ENERGY CENTER CTG 11 | 01INR0007 | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 192
82 | FORNEY ENERGY CENTER CTG 12 | 01INR0007 | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 184
83 | FORNEY ENERGY CENTER CTG 13 | 01INR0007 | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 184
84 | FORNEY ENERGY CENTER CTG 21 | 01INR0007 | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 192
85 | FORNEY ENERGY CENTER CTG 22 | 01INR0007 | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 184
86 | FORNEY ENERGY CENTER CTG 23 | 01INR0007 | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 184
87 | FORNEY ENERGY CENTER STG 10 | 01INR0007 | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 420
88 | FORNEY ENERGY CENTER STG 20 | 01INR0007 | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 420
89 | FREESTONE ENERGY CENTER CTG 1 | 01INR0009 | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 160.7
90 | FREESTONE ENERGY CENTER CTG 2 | 01INR0009 | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 160.7
91 | FREESTONE ENERGY CENTER STG 3 | 01INR0009 | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 179.8
92 | FREESTONE ENERGY CENTER CTG 4 | 01INR0009 | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 161.1
93 | FREESTONE ENERGY CENTER CTG 5 | 01INR0009 | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 161.1
94 | FREESTONE ENERGY CENTER STG 6 | 01INR0009 | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 179.7
95 | GUADALUPE ENERGY CENTER CTG 1 | 01INR0004 | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 167
96 | GUADALUPE ENERGY CENTER CTG 2 | 01INR0004 | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 167
97 | GUADALUPE ENERGY CENTER CTG 3 | 01INR0004 | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 167
98 | GUADALUPE ENERGY CENTER CTG 4 | 01INR0004 | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 167
99 | GUADALUPE ENERGY CENTER STG 5 | 01INR0004 | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 203
100 | GUADALUPE ENERGY CENTER STG 6 | 01INR0004 | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 203
101 | HAYS ENERGY FACILITY CSG 1 | 01INR0003 | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 237
102 | HAYS ENERGY FACILITY CSG 2 | 01INR0003 | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 237
103 | HAYS ENERGY FACILITY CSG 3 | 01INR0003 | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 247
104 | HAYS ENERGY FACILITY CSG 4 | 01INR0003 | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 247
105 | HIDALGO ENERGY CENTER CTG 1 | 00INR0006 | DUKE_DUKE_GT1 | HIDALGO | GAS | SOUTH | 2000 | 150
106 | HIDALGO ENERGY CENTER CTG 2 | 00INR0006 | DUKE_DUKE_GT2 | HIDALGO | GAS | SOUTH | 2000 | 150
107 | HIDALGO ENERGY CENTER STG | 00INR0006 | DUKE_DUKE_ST1 | HIDALGO | GAS | SOUTH | 2000 | 176
108 | JACK COUNTY GEN FACILITY CTG 1 | 05INR0010 | JACKCNTY_CT1 | JACK | GAS | NORTH | 2005 | 165
109 | JACK COUNTY GEN FACILITY CTG 2 | 05INR0010 | JACKCNTY_CT2 | JACK | GAS | NORTH | 2005 | 165
110 | JACK COUNTY GEN FACILITY STG 1 | 05INR0010 | JACKCNTY_STG | JACK | GAS | NORTH | 2005 | 310
111 | JACK COUNTY GEN FACILITY CTG 3 | 10INR0010 | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 165
112 | JACK COUNTY GEN FACILITY CTG 4 | 10INR0010 | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 165
113 | JACK COUNTY GEN FACILITY STG 2 | 10INR0010 | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 310
114 | JOHNSON COUNTY GEN FACILITY CTG |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 177
115 | JOHNSON COUNTY GEN FACILITY STG |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106
116 | LAMAR ENERGY CENTER CTG 11 | 00INR0008 | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 186
117 | LAMAR ENERGY CENTER CTG 12 | 00INR0008 | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 176
118 | LAMAR ENERGY CENTER CTG 21 | 00INR0008 | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 176
119 | LAMAR ENERGY CENTER CTG 22 | 00INR0008 | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 186
120 | LAMAR ENERGY CENTER STG 1 | 00INR0008 | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 204
121 | LAMAR ENERGY CENTER STG 2 | 00INR0008 | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 204
122 | LOST PINES POWER CTG 1 | 02INR0005 | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 183
123 | LOST PINES POWER CTG 2 | 02INR0005 | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 183
124 | LOST PINES POWER STG | 02INR0005 | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 192
125 | MAGIC VALLEY STATION CTG 1 | 00INR0009 | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 218.6
126 | MAGIC VALLEY STATION CTG 2 | 00INR0009 | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 218.6
127 | MAGIC VALLEY STATION STG | 00INR0009 | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 257.9
128 | MIDLOTHIAN ENERGY FACILITY CS 1 | 00INR0012 | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 240
129 | MIDLOTHIAN ENERGY FACILITY CS 2 | 00INR0012 | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 240
130 | MIDLOTHIAN ENERGY FACILITY CS 3 | 00INR0012 | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 240
131 | MIDLOTHIAN ENERGY FACILITY CS 4 | 00INR0012 | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 240
132 | MIDLOTHIAN ENERGY FACILITY CS 5 | 02INR0008 | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 257
133 | MIDLOTHIAN ENERGY FACILITY CS 6 | 02INR0008 | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 257
134 | NUECES BAY REPOWER CTG 8 | 09INR0039 | NUECES_B_NUECESG8 | NUECES | GAS | COASTAL | 2010 | 165
135 | NUECES BAY REPOWER CTG 9 | 09INR0039 | NUECES_B_NUECESG9 | NUECES | GAS | COASTAL | 2010 | 165
136 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | COASTAL | 1972 | 325
137 | ODESSA-ECTOR POWER CTG 11 | 01INR0026 | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 162.6
138 | ODESSA-ECTOR POWER CTG 12 | 01INR0026 | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 151.2
139 | ODESSA-ECTOR POWER CTG 21 | 01INR0026 | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 155.8
140 | ODESSA-ECTOR POWER CTG 22 | 01INR0026 | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 153.3
141 | ODESSA-ECTOR POWER STG 1 | 01INR0026 | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 216
142 | ODESSA-ECTOR POWER STG 2 | 01INR0026 | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 216
143 | PANDA SHERMAN POWER CTG1 | 10INR0021 | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 218.5
144 | PANDA SHERMAN POWER CTG2 | 10INR0021 | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 218.5
145 | PANDA SHERMAN POWER STG | 10INR0021 | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 333.6
146 | PANDA TEMPLE I POWER CTG1 | 10INR0020a | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 218.5
147 | PANDA TEMPLE I POWER CTG2 | 10INR0020a | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 218.5
148 | PANDA TEMPLE I POWER STG | 10INR0020a | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 333.6
149 | PANDA TEMPLE II POWER CTG1 | 10INR0020b | PANDA_T2_TMPL2CT1 | BELL | GAS | NORTH | 2015 | 218.5
150 | PANDA TEMPLE II POWER CTG2 | 10INR0020b | PANDA_T2_TMPL2CT2 | BELL | GAS | NORTH | 2015 | 218.5
151 | PANDA TEMPLE II POWER STG | 10INR0020b | PANDA_T2_TMPL2ST1 | BELL | GAS | NORTH | 2015 | 333.6
152 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 87
153 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 87
154 | PARIS ENERGY CENTER STG |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 89
155 | PASADENA COGEN FACILITY CTG 2 | 00INR0014 | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 176
156 | PASADENA COGEN FACILITY CTG 3 | 00INR0014 | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 176
157 | PASADENA COGEN FACILITY STG 2 | 00INR0014 | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 169
158 | QUAIL RUN ENERGY CTG 1 | 06INR0036b | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 84
159 | QUAIL RUN ENERGY CTG 2 | 06INR0036b | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 86
160 | QUAIL RUN ENERGY STG 1 | 06INR0036b | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98
161 | QUAIL RUN ENERGY CTG 3 | 06INR0036a | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 81
162 | QUAIL RUN ENERGY CTG 4 | 06INR0036a | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 81
163 | QUAIL RUN ENERGY STG 2 | 06INR0036a | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98
164 | RIO NOGALES POWER CTG 1 | 02INR0001 | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 175
165 | RIO NOGALES POWER CTG 2 | 02INR0001 | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 175
166 | RIO NOGALES POWER CTG 3 | 02INR0001 | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 175
167 | RIO NOGALES POWER STG 4 | 02INR0001 | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 323
168 | SAM RAYBURN POWER CTG 7 | 03INR0014 | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50
169 | SAM RAYBURN POWER CTG 8 | 03INR0014 | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 51
170 | SAM RAYBURN POWER CTG 9 | 03INR0014 | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50
171 | SAM RAYBURN POWER STG 10 | 03INR0014 | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40
172 | SANDHILL ENERGY CENTER CTG 5A | 03INR0033 | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 170
173 | SANDHILL ENERGY CENTER STG 5C | 03INR0033 | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 160
174 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | COASTAL | 1962 | 21
175 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | COASTAL | 1996 | 49
176 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 57
177 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 57
178 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 57
179 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 57
180 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 104
181 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 57
182 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 57
183 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 57
184 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 57
185 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 104
186 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 102.4
187 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 102.4
188 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 102.4
189 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 131.5
190 | VICTORIA POWER CTG 6 | 08INR0050 | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 171
191 | VICTORIA POWER STG 5 | 08INR0050 | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 1963 | 132
192 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 20
193 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 20
194 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 20
195 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 16
196 | WISE-TRACTEBEL POWER CTG 1 | 02INR0009 | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 275
197 | WISE-TRACTEBEL POWER CTG 2 | 02INR0009 | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 275
198 | WISE-TRACTEBEL POWER STG 1 | 02INR0009 | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 290
199 | WOLF HOLLOW POWER CTG 1 | 01INR0015 | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 249
200 | WOLF HOLLOW POWER CTG 2 | 01INR0015 | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 249
201 | WOLF HOLLOW POWER STG | 01INR0015 | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 293
202 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 20
203 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 48
204 | DANSBY CTG 3 | 09INR0072 | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 50
205 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 54
206 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 54
207 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 54
208 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 54
209 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS | NORTH | 1990 | 80
210 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS | NORTH | 1990 | 79
211 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS | NORTH | 1990 | 78
212 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS | NORTH | 1990 | 77
213 | ECTOR COUNTY ENERGY CTG 1 | 14INR0039 | ECEC_G1 | ECTOR | GAS | WEST | 2015 | 170.4
214 | ECTOR COUNTY ENERGY CTG 2 | 14INR0039 | ECEC_G2 | ECTOR | GAS | WEST | 2015 | 170.4
215 | EXTEX LAPORTE GEN STN CTG 1 | 01INR0044 | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 45
216 | EXTEX LAPORTE GEN STN CTG 2 | 01INR0044 | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 45
217 | EXTEX LAPORTE GEN STN CTG 3 | 01INR0044 | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 45
218 | EXTEX LAPORTE GEN STN CTG 4 | 01INR0044 | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 45
219 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 54
220 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 54
221 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 54
222 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 58
223 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 64
224 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 54
225 | GREENVILLE IC ENGINE PLANT | 10INR0070 | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.4
226 | GREENVILLE IC ENGINE PLANT | 10INR0070 | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.4
227 | GREENVILLE IC ENGINE PLANT | 10INR0070 | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.4
228 | LAREDO CTG 4 | 08INR0064 | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 97.4
229 | LAREDO CTG 5 | 08INR0064 | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 94.4
230 | LEON CREEK PEAKER CTG 1 | 04INR0009 | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 48
231 | LEON CREEK PEAKER CTG 2 | 04INR0009 | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 48
232 | LEON CREEK PEAKER CTG 3 | 04INR0009 | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 48
233 | LEON CREEK PEAKER CTG 4 | 04INR0009 | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 48
234 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 81
235 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 81
236 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 81
237 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 81
238 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 81
239 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 81
240 | PEARSALL IC ENGINE PLANT A | 09INR0079a | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.6
241 | PEARSALL IC ENGINE PLANT B | 09INR0079a | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.6
242 | PEARSALL IC ENGINE PLANT C | 09INR0079b | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.6
243 | PEARSALL IC ENGINE PLANT D | 09INR0079b | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.6
244 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 71
245 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 71
246 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 74
247 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 75
248 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 75
249 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 2000 | 115
250 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 2000 | 115
251 | RAY OLINGER CTG 4 | 00INR0024 | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 84
252 | SAM RAYBURN CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 13.5
253 | SAM RAYBURN CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 13.5
254 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 81
255 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 81
256 | SANDHILL ENERGY CENTER CTG 1 | 01INR0041 | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 48
257 | SANDHILL ENERGY CENTER CTG 2 | 01INR0041 | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 48
258 | SANDHILL ENERGY CENTER CTG 3 | 01INR0041 | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 48
259 | SANDHILL ENERGY CENTER CTG 4 | 01INR0041 | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 48
260 | SANDHILL ENERGY CENTER CTG 6 | 09INR0045 | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 48
261 | SANDHILL ENERGY CENTER CTG 7 | 09INR0045 | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 48
262 | SILAS RAY CTG 10 | 04INR0014 | SILASRAY_SILAS_10 | CAMERON | GAS | COASTAL | 2004 | 46
263 | T H WHARTON CTG 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 57
264 | T H WHARTON CTG 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 57
265 | T H WHARTON CTG 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 57
266 | T H WHARTON CTG 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 57
267 | T H WHARTON CTG 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 57
268 | T H WHARTON CTG 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 57
269 | T H WHARTON CTG G1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13
270 | TEXAS GULF SULPHUR |  | TGF_TGFGT_1 | WHARTON | GAS | SOUTH | 1985 | 89
271 | V H BRAUNIG CTG 5 | 09INR0028 | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48
272 | V H BRAUNIG CTG 6 | 09INR0028 | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48
273 | V H BRAUNIG CTG 7 | 09INR0028 | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48
274 | V H BRAUNIG CTG 8 | 09INR0028 | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 47
275 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FT. BEND | GAS | HOUSTON | 1967 | 13
276 | W A PARISH - PETRA NOVA CTG | 12INR0086 | PNPI_GT2 | FORT BEND | GAS | HOUSTON | 2013 | 88
277 | WINCHESTER POWER PARK CTG 1 | 09INR0027 | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 46
278 | WINCHESTER POWER PARK CTG 2 | 09INR0027 | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 46
279 | WINCHESTER POWER PARK CTG 3 | 09INR0027 | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 46
280 | WINCHESTER POWER PARK CTG 4 | 09INR0027 | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 46
281 | B M DAVIS STG U1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | COASTAL | 1974 | 330
282 | CEDAR BAYOU STG U1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745
283 | CEDAR BAYOU STG U2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749
284 | DANSBY STG U1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 110
285 | DECKER CREEK STG U1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 320
286 | DECKER CREEK STG U2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 428
287 | GRAHAM STG U1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 234
288 | GRAHAM STG U2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390
289 | GREENS BAYOU STG U5 |  | GBY_GBY_5 | HARRIS | GAS | HOUSTON | 1973 | 371
290 | HANDLEY STG U3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395
291 | HANDLEY STG U4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435
292 | HANDLEY STG U5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435
293 | LAKE HUBBARD STG U1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392
294 | LAKE HUBBARD STG U2 |  | LHSES_UNIT2A | DALLAS | GAS | NORTH | 1973 | 523
295 | MOUNTAIN CREEK STG U6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 122
296 | MOUNTAIN CREEK STG U7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 118
297 | MOUNTAIN CREEK STG U8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 568
298 | O W SOMMERS STG U1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420
299 | O W SOMMERS STG U2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 410
300 | PEARSALL STG U1 |  | PEARSALL_PEARS_1 | FRIO | GAS | SOUTH | 1961 | 20
301 | PEARSALL STG U2 |  | PEARSALL_PEARS_2 | FRIO | GAS | SOUTH | 1961 | 24
302 | PEARSALL STG U3 |  | PEARSALL_PEARS_3 | FRIO | GAS | SOUTH | 1961 | 22
303 | POWERLANE PLANT STG U1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 1966 | 20
304 | POWERLANE PLANT STG U2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 26
305 | POWERLANE PLANT STG U3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 41
306 | R W MILLER STG U1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 2000 | 75
307 | R W MILLER STG U2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 2000 | 120
308 | R W MILLER STG U3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 2000 | 208
309 | RAY OLINGER STG U1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78
310 | RAY OLINGER STG U2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107
311 | RAY OLINGER STG U3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146
312 | SIM GIDEON STG U1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130
313 | SIM GIDEON STG U2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 135
314 | SIM GIDEON STG U3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 340
315 | SPENCER STG U4 |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 61
316 | SPENCER STG U5 |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61
317 | STRYKER CREEK STG U1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167
318 | STRYKER CREEK STG U2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502
319 | TRINIDAD STG U6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 1965 | 235
320 | V H BRAUNIG STG U1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 220
321 | V H BRAUNIG STG U2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230
322 | V H BRAUNIG STG U3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412
323 | W A PARISH STG U1 |  | WAP_WAP_G1 | FT. BEND | GAS | HOUSTON | 1958 | 169
324 | W A PARISH STG U2 |  | WAP_WAP_G2 | FT. BEND | GAS | HOUSTON | 1958 | 169
325 | W A PARISH STG U3 |  | WAP_WAP_G3 | FT. BEND | GAS | HOUSTON | 1961 | 258
326 | W A PARISH STG U4 |  | WAP_WAP_G4 | FT. BEND | GAS | HOUSTON | 1968 | 552
327 | NACOGDOCHES POWER | 09INR0007 | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105
328 | LUFKIN BIOMASS | 08INR0033 | LFBIO_UNIT1 | ANGELINA | BIOMASS | NORTH | 2012 | 45
329 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8
330 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6
331 | FORT WORTH METHANE LFG |  | DG_RDLML_1UNIT | TARRANT | BIOMASS | NORTH | 2011 | 1.6
332 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4
333 | MCKINNEY LFG |  | DG_MKNSW_2UNITS | COLLIN | BIOMASS | NORTH | 2011 | 3.2
334 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.24
335 | SKYLINE LFG |  | DG_FERIS_4 UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4
336 | TRINITY OAKS LFG |  | DG_KLBRG_1UNIT | DALLAS | BIOMASS | NORTH | 2011 | 3.2
337 | VIRIDIS ENERGY-ALVIN LFG |  | DG_AV_DG1 | GALVESTON | BIOMASS | HOUSTON | 2002 | 6.7
338 | VIRIDIS ENERGY-HUMBLE LFG |  | DG_HB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 10
339 | VIRIDIS ENERGY-LIBERTY LFG |  | DG_LB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 3.9
340 | VIRIDIS ENERGY-TRINITY BAY LFG |  | DG_TRN_DG1 | CHAMBERS | BIOMASS | HOUSTON | 2002 | 3.9
341 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4
342 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4
343 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2
344 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2
345 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8
346 | NOTREES BATTERY FACILITY | 12INR0076 | NWF_NBS | WINKLER | STORAGE | WEST | 2012 | 0
347 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 68013.64
348
349 | Operational Resources (Hydro)
350 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
351 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
352 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8
353 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9
354 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16
355 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16
356 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17
357 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40
358 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40
359 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12
360 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12
361 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12
362 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29
363 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29
364 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14
365 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21
366 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20
367 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36
368 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36
369 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 29
370 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 24
371 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 24
372 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.35
373 | EAGLE PASS HYDRO |  | DG_EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6
374 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | DG_CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6
375 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 1931 | 4.8
376 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7
377 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6
378 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2
379 | Operational Capacity Total (Hydro) | [6 empty] | 555.05
380 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 52
381
382 | Operational Resources (Solar)
383 | ACACIA SOLAR | 13DGR0001 | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10
384 | FS BARILLA SOLAR-PECOS | 12INR0059 | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2014 | 22
385 | OCI ALAMO 1 SOLAR | 13INR0058 | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2
386 | OCI ALAMO 4 SOLAR-BRACKETVILLE | 14INR0024 | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6
387 | WEBBERVILLE SOLAR | 10INR0082 | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7
388 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6
389 | BLUE WING 2 SOLAR |  | DG_ELEM_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3
390 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4
391 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5
392 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CCS1 | DENTON | SOLAR | NORTH | 2015 | 2
393 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6
394 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5
395 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
396 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
397 | Operational Capacity Total (Solar) | [6 empty] | 192.7
398 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 100
399
400 | Operational Capacity Unavailable due to Extended Outage or Derate |  | OPERATION_UNAVAIL |  | GAS |  |  | -195
401 | Operational Capacity Total (Including Hydro & Solar) |  | OPERATION_TOTAL |  |  |  |  | 68063.34
402
403 | Switchable Resources
404 | TENASKA KIAMICHI STATION 1CT101 | 03INR0012 | KMCHI_1CT101 | FANNIN | GAS | NORTH | 2003 | 178
405 | TENASKA KIAMICHI STATION 1CT201 | 03INR0012 | KMCHI_1CT201 | FANNIN | GAS | NORTH | 2003 | 180
406 | TENASKA KIAMICHI STATION 1ST | 03INR0012 | KMCHI_1ST | FANNIN | GAS | NORTH | 2003 | 307
407 | TENASKA KIAMICHI STATION 2CT101 | 03INR0012 | KMCHI_2CT101 | FANNIN | GAS | NORTH | 2003 | 178
408 | TENASKA KIAMICHI STATION 2CT201 | 03INR0012 | KMCHI_2CT201 | FANNIN | GAS | NORTH | 2003 | 180
409 | TENASKA KIAMICHI STATION 2ST | 03INR0012 | KMCHI_2ST | FANNIN | GAS | NORTH | 2003 | 307
410 | TENASKA FRONTIER STATION CTG 1 | 00PSR4 | FTR_FTR_G1 | GRIMES | GAS | NORTH | 2000 | 180
411 | TENASKA FRONTIER STATION CTG 2 | 00PSR4 | FTR_FTR_G2 | GRIMES | GAS | NORTH | 2000 | 180
412 | TENASKA FRONTIER STATION CTG 3 | 00PSR4 | FTR_FTR_G3 | GRIMES | GAS | NORTH | 2000 | 180
413 | TENASKA FRONTIER STATION STG 4 | 00PSR4 | FTR_FTR_G4 | GRIMES | GAS | NORTH | 2000 | 400
414 | TENASKA GATEWAY STATION CTG 1 | 01INR0019 | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 162
415 | TENASKA GATEWAY STATION CTG 2 | 01INR0019 | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 179
416 | TENASKA GATEWAY STATION CTG 3 | 01INR0019 | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 178
417 | TENASKA GATEWAY STATION STG 4 | 01INR0019 | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 389
418 | FRONTERA GENERATION CTG 1 |  | FRONTERA_FRONTEG1 | HIDALGO | GAS | SOUTH | 1999 | 170
419 | FRONTERA GENERATION CTG 2 |  | FRONTERA_FRONTEG2 | HIDALGO | GAS | SOUTH | 1999 | 170
420 | FRONTERA GENERATION STG |  | FRONTERA_FRONTEG3 | HIDALGO | GAS | SOUTH | 2000 | 184
421 | Switchable Capacity Total | [6 empty] | 3702
422
423 | Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  | GAS |  |  | -470
424
425 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  | COAL |  |  | 0
426
427 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 4433
428
429 | Wind Resources
430 | ANACACHO WIND | 12INR0072 | ANACACHO_ANA | KINNEY | WIND | SOUTH | 2012 | 99.8
431 | BARTON CHAPEL WIND | 06INR0021 | BRTSW_BCW1 | JACK | WIND | NORTH | 2007 | 120
432 | BLUE SUMMIT WIND 5 | 12INR0075 | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | WEST | 2013 | 9
433 | BLUE SUMMIT WIND 6 | 12INR0075 | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | WEST | 2013 | 126.4
434 | BOBCAT BLUFF WIND | 08INR0049 | BCATWIND_WIND_1 | ARCHER | WIND | WEST | 2012 | 150
435 | BUFFALO GAP WIND 1 | 04INR0015 | BUFF_GAP_UNIT1 | TAYLOR | WIND | WEST | 2006 | 120.6
436 | BUFFALO GAP WIND 2_1 | 06INR0037 | BUFF_GAP_UNIT2_1 | TAYLOR | WIND | WEST | 2007 | 115.5
437 | BUFFALO GAP WIND 2_2 | 06INR0037 | BUFF_GAP_UNIT2_2 | TAYLOR | WIND | WEST | 2007 | 117
438 | BUFFALO GAP WIND 3 | 07INR0030 | BUFF_GAP_UNIT3 | TAYLOR | WIND | WEST | 2008 | 170.2
439 | BULL CREEK WIND U1 | 07INR0037 | BULLCRK_WND1 | BORDEN | WIND | WEST | 2009 | 88
440 | BULL CREEK WIND U2 | 07INR0037 | BULLCRK_WND2 | BORDEN | WIND | WEST | 2009 | 90
441 | CALLAHAN WIND | 04INR0013 | CALLAHAN_WND1 | CALLAHAN | WIND | WEST | 2004 | 114
442 | CAMP SPRINGS WIND 1 | 06INR0038 | CSEC_CSECG1 | SCURRY | WIND | WEST | 2007 | 130.5
443 | CAMP SPRINGS WIND 2 | 07INR0040 | CSEC_CSECG2 | SCURRY | WIND | WEST | 2007 | 120
444 | CAPRICORN RIDGE WIND 1 | 07INR0018 | CAPRIDGE_CR1 | STERLING | WIND | WEST | 2007 | 214.5
445 | CAPRICORN RIDGE WIND 2 | 07INR0041 | CAPRIDGE_CR3 | STERLING | WIND | WEST | 2008 | 186
446 | CAPRICORN RIDGE WIND 3 | 07INR0041 | CAPRIDGE_CR2 | STERLING | WIND | WEST | 2007 | 149.5
447 | CAPRICORN RIDGE WIND 4 | 08INR0063 | CAPRIDG4_CR4 | COKE | WIND | WEST | 2008 | 112.5
448 | CEDRO HILL WIND 1 | 09INR0082 | CEDROHIL_CHW1 | WEBB | WIND | SOUTH | 2010 | 75
449 | CEDRO HILL WIND 2 | 09INR0082 | CEDROHIL_CHW2 | WEBB | WIND | SOUTH | 2010 | 75
450 | CHAMPION WIND | 07INR0045d | CHAMPION_UNIT1 | NOLAN | WIND | WEST | 2008 | 126.5
451 | DESERT SKY WIND 1 |  | INDNENR_INDNENR | PECOS | WIND | WEST | 2002 | 84
452 | DESERT SKY WIND 2 |  | INDNENR_INDNENR_2 | PECOS | WIND | WEST | 2002 | 76.5
453 | ELBOW CREEK WIND | 08INR0053 | ELB_ELBCREEK | HOWARD | WIND | WEST | 2008 | 118.7
454 | FOREST CREEK WIND | 05INR0019 | MCDLD_FCW1 | GLASSCOCK | WIND | WEST | 2007 | 124.2
455 | GOAT WIND | 07INR0028 | GOAT_GOATWIND | STERLING | WIND | WEST | 2008 | 80
456 | GOAT WIND 2 | 07INR0028b | GOAT_GOATWIN2 | STERLING | WIND | WEST | 2010 | 69.6
457 | GOLDTHWAITE WIND 1 | 11INR0013 | GWEC_GWEC_G1 | MILLS | WIND | NORTH | 2014 | 148.6
458 | GRANDVIEW WIND 1 (CONWAY) GV1A | 13INR0005a | GRANDVW1_GV1A | CARSON | WIND | PANHANDLE | 2014 | 107.4
459 | GRANDVIEW WIND 1 (CONWAY) GV1B | 13INR0005a | GRANDVW1_GV1B | CARSON | WIND | PANHANDLE | 2014 | 103.8
460 | GREEN MOUNTAIN WIND (BRAZOS) U1 | 03INR0020 | BRAZ_WND_WND1 | SCURRY | WIND | WEST | 2003 | 99
461 | GREEN MOUNTAIN WIND (BRAZOS) U2 | 03INR0020 | BRAZ_WND_WND2 | SCURRY | WIND | WEST | 2003 | 61
462 | HACKBERRY WIND | 04INR0011e | HWF_HWFG1 | SHACKELFORD | WIND | WEST | 2008 | 163.5
463 | HEREFORD WIND G | 13INR0059a | HRFDWIND_WIND_G | DEAF SMITH | WIND | PANHANDLE | 2015 | 99.9
464 | HEREFORD WIND V | 13INR0059a | HRFDWIND_WIND_V | DEAF SMITH | WIND | PANHANDLE | 2015 | 100
465 | HORSE HOLLOW WIND 1 | 05INR0018b | H_HOLLOW_WND1 | TAYLOR | WIND | WEST | 2005 | 206.6
466 | HORSE HOLLOW WIND 2 | 05INR0018a | HHOLLOW2_WIND1 | TAYLOR | WIND | WEST | 2006 | 158
467 | HORSE HOLLOW WIND 3 | 06INR0040 | HHOLLOW3_WND_1 | TAYLOR | WIND | WEST | 2006 | 208
468 | HORSE HOLLOW WIND 4 | 06INR0040 | HHOLLOW4_WND1 | TAYLOR | WIND | WEST | 2006 | 108
469 | INADALE WIND | 07INR0045b | INDL_INADALE1 | NOLAN | WIND | WEST | 2008 | 196.6
470 | INDIAN MESA WIND | 00INR0022 | INDNNWP_INDNNWP | PECOS | WIND | WEST | 2001 | 82.5
471 | JUMBO ROAD WIND 1 | 13INR0059b | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND | PANHANDLE | 2015 | 146.2
472 | JUMBO ROAD WIND 2 | 13INR0059b | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND | PANHANDLE | 2015 | 153.6
473 | KEECHI WIND 138 KV JOPLIN | 14INR0049_2 | KEECHI_U1 | JACK | WIND | NORTH | 2014 | 110
474 | KING MOUNTAIN WIND (NE) | 00INR0025 | KING_NE_KINGNE | UPTON | WIND | WEST | 2001 | 79.3
475 | KING MOUNTAIN WIND (NW) | 00INR0025 | KING_NW_KINGNW | UPTON | WIND | WEST | 2001 | 79.3
476 | KING MOUNTAIN WIND (SE) | 00INR0025 | KING_SE_KINGSE | UPTON | WIND | WEST | 2001 | 40.3
477 | KING MOUNTAIN WIND (SW) | 00INR0025 | KING_SW_KINGSW | UPTON | WIND | WEST | 2001 | 79.3
478 | LANGFORD WIND POWER | 10INR0026 | LGD_LANGFORD | TOM GREEN | WIND | WEST | 2009 | 155
479 | LOGANS GAP WIND I U1 | 13INR0050 | LGW_UNIT1 | COMANCHE | WIND | NORTH | 2015 | 103.8
480 | LOGANS GAP WIND I U2 | 13INR0050 | LGW_UNIT2 | COMANCHE | WIND | NORTH | 2015 | 106.3
481 | LONE STAR WIND 1 (MESQUITE) | 04INR0011d | LNCRK_G83 | SHACKELFORD | WIND | WEST | 2006 | 200
482 | LONE STAR WIND 2 (POST OAK) U1 | 04INR0011a | LNCRK2_G871 | SHACKELFORD | WIND | WEST | 2007 | 100
483 | LONE STAR WIND 2 (POST OAK) U2 | 04INR0011a | LNCRK2_G872 | SHACKELFORD | WIND | WEST | 2007 | 100
484 | LONGHORN WIND NORTH U1 | 14INR0023 | LHORN_N_UNIT1 | FLOYD | WIND | PANHANDLE | 2015 | 100
485 | LONGHORN WIND NORTH U2 | 14INR0023 | LHORN_N_UNIT2 | FLOYD | WIND | PANHANDLE | 2015 | 100
486 | LORAINE WINDPARK I | 09INR0047 | LONEWOLF_G1 | MITCHELL | WIND | WEST | 2009 | 49.5
487 | LORAINE WINDPARK II | 09INR0047 | LONEWOLF_G2 | MITCHELL | WIND | WEST | 2009 | 51
488 | LORAINE WINDPARK III | 09INR0047 | LONEWOLF_G3 | MITCHELL | WIND | WEST | 2011 | 25.5
489 | LORAINE WINDPARK IV | 09INR0047 | LONEWOLF_G4 | MITCHELL | WIND | WEST | 2011 | 24
490 | MESQUITE CREEK WIND 1 | 09INR0051 | MESQCRK_WND1 | DAWSON | WIND | WEST | 2015 | 105.6
491 | MESQUITE CREEK WIND 2 | 09INR0051 | MESQCRK_WND2 | DAWSON | WIND | WEST | 2015 | 105.6
492 | MIAMI WIND G1 | 14INR0012a | MIAM1_G1 | GRAY | WIND | PANHANDLE | 2014 | 144.3
493 | MIAMI WIND G2 | 14INR0012a | MIAM1_G2 | GRAY | WIND | PANHANDLE | 2014 | 144.3
494 | MCADOO WIND | 08INR0028 | MWEC_G1 | DICKENS | WIND | PANHANDLE | 2008 | 150
495 | NOTREES WIND 1 | 07INR0005 | NWF_NWF1 | WINKLER | WIND | WEST | 2009 | 92.6
496 | NOTREES WIND 2 | 07INR0005 | NWF_NWF2 | WINKLER | WIND | WEST | 2009 | 60
497 | OCOTILLO WIND | 04INR0017 | OWF_OWF | HOWARD | WIND | WEST | 2008 | 58.8
498 | PANHANDLE WIND 1 U1 | 14INR0030a_2 | PH1_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 109.2
499 | PANHANDLE WIND 1 U2 | 14INR0030a_2 | PH1_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 109.2
500 | PANHANDLE WIND 2 U1 | 14INR0030b | PH2_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 94.2
501 | PANHANDLE WIND 2 U2 | 14INR0030b | PH2_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 96.6
502 | PANTHER CREEK WIND 1 | 07INR0022 | PC_NORTH_PANTHER1 | HOWARD | WIND | WEST | 2008 | 142.5
503 | PANTHER CREEK WIND 2 | 08INR0037 | PC_SOUTH_PANTHER2 | HOWARD | WIND | WEST | 2008 | 115.5
504 | PANTHER CREEK WIND 3 | 11INR0015 | PC_SOUTH_PANTHER3 | HOWARD | WIND | WEST | 2009 | 199.5
505 | PECOS WIND 1 (WOODWARD) | 01INR0035 | WOODWRD1_WOODWRD1 | PECOS | WIND | WEST | 2001 | 82.5
506 | PECOS WIND 2 (WOODWARD) | 01INR0035 | WOODWRD2_WOODWRD2 | PECOS | WIND | WEST | 2001 | 77.2
507 | PYRON WIND | 07INR0045a | PYR_PYRON1 | SCURRY | WIND | WEST | 2008 | 249
508 | RATTLESNAKE DEN WIND PHASE 1 G1 | 13INR0020a | RSNAKE_G1 | GLASSCOCK | WIND | WEST | 2015 | 104.3
509 | RATTLESNAKE DEN WIND PHASE 1 G2 | 13INR0020a | RSNAKE_G2 | GLASSCOCK | WIND | WEST | 2015 | 103
510 | RED CANYON WIND | 05INR0017 | RDCANYON_RDCNY1 | BORDEN | WIND | WEST | 2006 | 84
511 | ROSCOE WIND | 07INR0045e | TKWSW1_ROSCOE | NOLAN | WIND | WEST | 2008 | 209
512 | ROUTE 66 WIND | 14INR0032a | ROUTE_66_WIND1 | CARSON | WIND | PANHANDLE | 2015 | 150
513 | SAND BLUFF WIND | 05INR0019 | MCDLD_SBW1 | GLASSCOCK | WIND | WEST | 2008 | 90
514 | SENATE WIND | 08INR0011 | SENATEWD_UNIT1 | JACK | WIND | NORTH | 2012 | 150
515 | SHERBINO 1 WIND | 06INR0012a | KEO_KEO_SM1 | PECOS | WIND | WEST | 2008 | 150
516 | SHERBINO 2 WIND | 06INR0012b | KEO_SHRBINO2 | PECOS | WIND | WEST | 2011 | 147.5
517 | SILVER STAR WIND | 03INR0034 | FLTCK_SSI | EASTLAND | WIND | NORTH | 2008 | 60
518 | SNYDER WIND | 04INR0020 | ENAS_ENA1 | SCURRY | WIND | WEST | 2007 | 63
519 | SOUTH TRENT WIND | 07INR0029 | STWF_T1 | NOLAN | WIND | WEST | 2008 | 98.2
520 | SPINNING SPUR WIND TWO | 13INR0048 | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 2014 | 161
521 | SPINNING SPUR 3 [WIND 1] | 14INR0053 | SSPURTWO_SS3WIND1 | OLDHAM | WIND | PANHANDLE | 2015 | 96
522 | SPINNING SPUR 3 [WIND 2] | 14INR0053 | SSPURTWO_SS3WIND2 | OLDHAM | WIND | PANHANDLE | 2015 | 98
523 | STANTON WIND ENERGY | 07INR0010 | SWEC_G1 | MARTIN | WIND | WEST | 2008 | 120
524 | STEPHENS RANCH WIND 1 | 12INR0034a | SRWE1_UNIT1 | BORDEN | WIND | WEST | 2014 | 211.2
525 | STEPHENS RANCH WIND 2 | 12INR0034b | SRWE1_SRWE2 | BORDEN | WIND | WEST | 2015 | 164.7
526 | SWEETWATER WIND 1 | 01INR0036 | SWEETWND_WND1 | NOLAN | WIND | WEST | 2003 | 36.6
527 | SWEETWATER WIND 2A | 01INR0036 | SWEETWN2_WND24 | NOLAN | WIND | WEST | 2006 | 15.9
528 | SWEETWATER WIND 2B | 01INR0036 | SWEETWN2_WND2 | NOLAN | WIND | WEST | 2004 | 97.5
529 | SWEETWATER WIND 3A | 01INR0036 | SWEETWN3_WND3A | NOLAN | WIND | WEST | 2011 | 28.5
530 | SWEETWATER WIND 3B | 01INR0036 | SWEETWN3_WND3B | NOLAN | WIND | WEST | 2011 | 100.5
531 | SWEETWATER WIND 4-5 | 07INR0023 | SWEETWN4_WND5 | NOLAN | WIND | WEST | 2007 | 79.2
532 | SWEETWATER WIND 4-4B | 07INR0023 | SWEETWN4_WND4B | NOLAN | WIND | WEST | 2007 | 103.7
533 | SWEETWATER WIND 4-4A | 07INR0023 | SWEETWN4_WND4A | NOLAN | WIND | WEST | 2007 | 117.8
534 | TEXAS BIG SPRING WIND a |  | SGMTN_SIGNALMT | HOWARD | WIND | WEST | 1999 | 27.7
535 | TEXAS BIG SPRING WIND b |  | SGMTN_SIGNALM2 | HOWARD | WIND | WEST | 1999 | 6.6
536 | TRENT WIND | 01INR0038 | TRENT_TRENT | NOLAN | WIND | WEST | 2001 | 150
537 | TRINITY HILLS WIND 1 | 08INR0062 | TRINITY_TH1_BUS1 | YOUNG | WIND | WEST | 2012 | 117.5
538 | TRINITY HILLS WIND 2 | 08INR0062 | TRINITY_TH1_BUS2 | YOUNG | WIND | WEST | 2012 | 107.5
539 | TURKEY TRACK WIND | 07INR0011 | TTWEC_G1 | NOLAN | WIND | WEST | 2008 | 169.5
540 | WEST TEXAS WIND |  | SW_MESA_SW_MESA | UPTON | WIND | WEST | 1999 | 80.3
541 | WHIRLWIND ENERGY | 07INR0003 | WEC_WECG1 | FLOYD | WIND | PANHANDLE | 2007 | 57
542 | WHITETAIL WIND | 11INR0091 | EXGNWTL_WIND_1 | WEBB | WIND | SOUTH | 2012 | 91
543 | WINDTHORST 2 WIND | 13INR0057 | WNDTHST2_UNIT1 | ARCHER | WIND | WEST | 2014 | 67.6
544 | WKN MOZART WIND | 09INR0061 | MOZART_WIND_1 | KENT | WIND | WEST | 2012 | 30
545 | WOLF RIDGE WIND | 07INR0034 | WHTTAIL_WR1 | COOKE | WIND | NORTH | 2008 | 112.5
546 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND | WEST | 2008 | 2
547 | WOLF FLATS WIND (WIND MGT) |  | DG_TURL_UNIT1 | HALL | WIND | PANHANDLE | 2007 | 1
548 | Operational Wind Capacity Sub-total (Non-Coastal Counties) | [6 empty] | 12705.4
549 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PEAK_PCT_NC | % |  |  |  | 18
550
551 | GULF WIND I | 05INR0015a | TGW_T1 | KENEDY | WIND-C | COASTAL | 2010 | 141.6
552 | GULF WIND II | 05INR0015a | TGW_T2 | KENEDY | WIND-C | COASTAL | 2010 | 141.6
553 | LOS VIENTOS WIND I | 11INR0033 | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1
554 | LOS VIENTOS WIND II | 11INR0033 | LV1_LV1B | WILLACY | WIND-C | COASTAL | 2013 | 201.6
555 | MAGIC VALLEY WIND (REDFISH) 1A | 10INR0060 | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.8
556 | MAGIC VALLEY WIND (REDFISH) 1B | 10INR0060 | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5
557 | PAPALOTE CREEK WIND | 08INR0012a | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.9
558 | PAPALOTE CREEK WIND II | 08INR0012b | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.1
559 | PENASCAL WIND 1 | 06INR0022a | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8
560 | PENASCAL WIND 2 | 06INR0022b | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
561 | PENASCAL WIND 3 | 06INR0022b | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8
562 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9
563 | Operational Wind Capacity Sub-total (Coastal Counties) | [6 empty] | 1680.4
564 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 37
565
566 | Operational Wind Capacity Total (All Counties) |  | WIND_OPERATIONAL |  |  |  |  | 14385.8
567
568 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  | GAS |  |  | 0
569
570 | Non-Synchronous Tie Resources
571 | EAGLE PASS TIE |  | DC_S | MAVERICK |  | SOUTH |  | 30
572 | EAST TIE |  | DC_E | FANNIN |  | NORTH |  | 600
573 | LAREDO VFT TIE |  | DC_L | WEBB |  | SOUTH |  | 100
574 | NORTH TIE |  | DC_N | WILBARGER |  | WEST |  | 220
575 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO |  | SOUTH |  | 150
576 | SHARYLAND RAILROAD TIE 2 |  | DC_R2 | HIDALGO |  | SOUTH |  | 150
577 | Non-Synchronous Ties Total | [6 empty] | 1250
578 | Non-Synchronous Ties Capacity Contribution (Top 20 Hours) |  | DCTIE_CAP_CONT |  | OTHER |  |  | 371.4
579
580 | Planned Resources with Executed SGIA, Air Permit, GHG Permit and Water Rights
581 | TEXAS CLEAN ENERGY PROJECT | 13INR0023 |  | ECTOR | COAL | WEST | 2018 | 0
582 | FGE TEXAS I PROJECT | 16INR0010 |  | MITCHELL | GAS | WEST | 2017 | 0
583 | GSEC ANTELOPE 1-3 IC & ELK 1 CTG (SWITCHABLE) | 13INR0028 |  | HALE | GAS | PANHANDLE | 2016 | 0
584 | LA PALOMA ENERGY CENTER PROJECT | 16INR0004 |  | CAMERON | GAS | COASTAL | 2018 | 0
585 | PHR PEAKERS [BAC_CTG1-6] | 14INR0038 |  | GALVESTON | GAS | HOUSTON | 2016 | 0
586 | SKY GLOBAL POWER ONE | 16INR0057 |  | COLORADO | GAS | SOUTH | 2016 | 0
587 | INDECK WHARTON ENERGY CENTER | 15INR0023 |  | WHARTON | GAS | SOUTH | 2017 | 0
588 | PONDERA KING PROJECT | 10INR0022 |  | HARRIS | GAS | HOUSTON | 2017 | 0
589 | PINECREST ENERGY CENTER PROJECT | 16INR0006 |  | ANGELINA | GAS | NORTH | 2017 | 0
590 | STEC RED GATE IC PLANT | 14INR0040 |  | HIDALGO | GAS | SOUTH | 2016 | 0
591 | GSEC ELK STATION CTG 2 (SWITCHABLE) | 15INR0032 |  | HALE | GAS | PANHANDLE | 2016 | 0
592 | GSEC ELK STATION CTG 3 | 15INR0033 |  | HALE | GAS | PANHANDLE | 2016 | 0
593 | BETHEL CAES | 15INR0013 |  | ANDERSON | STORAGE | NORTH | 2018 | 0
594 | Planned Capacity Total (Coal, Gas & Storage) | [6 empty] | 0
595
596 | Planned Solar Resources with Executed SGIA
597 | FS BARILLA SOLAR 1B [HOVEY_UNIT2] | 12INR0059b |  | PECOS | SOLAR | WEST | 2015 | 7.4
598 | FS BARILLA SOLAR 2 | 12INR0059c |  | PECOS | SOLAR | WEST | 2016 | 0
599 | OCI ALAMO 5 (DOWNIE RANCH) [HELIOS_UNIT1] | 15INR0036 |  | UVALDE | SOLAR | SOUTH | 2015 | 0
600 | RE ROSEROCK SOLAR | 16INR0048 |  | PECOS | SOLAR | WEST | 2016 | 0
601 | OCI ALAMO 6 (WEST TEXAS) | 15INR0070_1 |  | PECOS | SOLAR | WEST | 2016 | 0
602 | OCI ALAMO 6 (WEST TEXAS PHASE II) | 15INR0070_1b |  | PECOS | SOLAR | WEST | 2016 | 0
603 | SE BUCKTHORN WESTEX SOLAR (OAK) | 15INR0045 |  | PECOS | SOLAR | WEST | 2017 | 0
604 | FS EAST PECOS SOLAR | 16INR0073 |  | PECOS | SOLAR | WEST | 2016 | 0
605 | OCI ALAMO 7 (PAINT CREEK) | 16INR0052 |  | HASKELL | SOLAR | WEST | 2016
606 | LC NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2016
607 | PECOS SOLAR POWER I | 15INR0059 |  | PECOS | SOLAR | WEST | 2017
608 | BNB LAMESA SOLAR | 16INR0023 |  | DAWSON | SOLAR | WEST | 2016 | 0
609 | CAPRICORN RIDGE SOLAR | 16INR0019 |  | COKE | SOLAR | WEST | 2016 | 0
610 | UPCO POWER 1 (SP-TX-12) | 16INR0065 |  | UPTON | SOLAR | WEST | 2016 | 0
611 | Planned Capacity Total (Solar) | [6 empty] | 7.4
612
613 | Planned Wind Resources with Executed SGIA
614 | GUNSIGHT MOUNTAIN WIND | 08INR0018 |  | HOWARD | WIND | WEST | 2016 | 0
615 | BAFFIN WIND [BAFFIN_UNIT1-2] | 06INR0022c |  | KENEDY | WIND-C | COASTAL | 2015 | 202
616 | MIDWAY FARMS WIND | 11INR0054 |  | SAN PATRICIO | WIND-C | COASTAL | 2016 | 0
617 | LONGHORN WIND SOUTH | 14INR0023b |  | BRISCOE | WIND | PANHANDLE | 2016 | 0
618 | MARIAH WIND A | 13INR0010a |  | PARMER | WIND | PANHANDLE | 2016 | 0
619 | MARIAH WIND B | 13INR0010b |  | PARMER | WIND | PANHANDLE | 2016 | 0
620 | MIAMI WIND 1B | 14INR0012b |  | GRAY | WIND | PANHANDLE | 2016 | 0
621 | SHANNON WIND [SHANNONW_UNIT_1] | 11INR0079a |  | CLAY | WIND | WEST | 2015 | 200
622 | SENDERO WIND ENERGY [EXGNSND_WIND_1] | 12INR0068 |  | JIM HOGG | WIND | SOUTH | 2015 | 0
623 | RATTLESNAKE DEN WIND 2 | 13INR0020b |  | GLASSCOCK | WIND | WEST | 2017 | 0
624 | PATRIOT WIND (PETRONILLA) | 11INR0062 |  | NUECES | WIND-C | COASTAL | 2016 | 0
625 | COMANCHE RUN WIND | 12INR0029 |  | SWISHER | WIND | PANHANDLE | 2016 | 0
626 | CAMERON COUNTY WIND [CAMWIND_UNIT1] | 11INR0057 |  | CAMERON | WIND-C | COASTAL | 2015 | 165
627 | LOS VIENTOS III WIND [LV3_UNIT_1] | 13INR0052 |  | STARR | WIND | SOUTH | 2015 | 200
628 | PAMPA WIND | 12INR0018 |  | GRAY | WIND | PANHANDLE | 2017 | 0
629 | GREEN PASTURES WIND [GPASTURE_WIND_I & II] | 12INR0070 |  | KNOX | WIND | WEST | 2015 | 300
630 | SOUTH PLAINS WIND I [SPLAIN1_WIND1-2] | 14INR0025a |  | FLOYD | WIND | PANHANDLE | 2015 | 200
631 | SOUTH PLAINS WIND II | 14INR0025b |  | FLOYD | WIND | PANHANDLE | 2016 | 0
632 | SOUTH PLAINS WIND III | 14INR0025c |  | FLOYD | WIND | PANHANDLE | 2016 | 0
633 | BRISCOE WIND [BRISCOE_WIND] | 14INR0072 |  | BRISCOE | WIND | PANHANDLE | 2015 | 150
634 | WAKE WIND | 14INR0047 |  | DICKENS | WIND | PANHANDLE | 2016 | 0
635 | DOUG COLBECK'S CORNER (CONWAY) | 13INR0005b |  | CARSON | WIND | PANHANDLE | 2016 | 0
636 | GRANDVIEW WIND 3 (CONWAY) | 13INR0005c |  | CARSON | WIND | PANHANDLE | 2016 | 0
637 | SCANDIA WIND D | 13INR0010d |  | PARMER | WIND | PANHANDLE | 2017 | 0
638 | SCANDIA WIND E | 13INR0010e |  | PARMER | WIND | PANHANDLE | 2017 | 0
639 | SCANDIA WIND F | 13INR0010f |  | PARMER | WIND | PANHANDLE | 2017 | 0
640 | PULLMAN ROAD WIND | 15INR0079 |  | RANDALL | WIND | PANHANDLE | 2016 | 0
641 | PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND | PANHANDLE | 2016 | 0
642 | SALT FORK WIND | 14INR0062 |  | GRAY | WIND | PANHANDLE | 2016 | 0
643 | LOS VIENTOS IV WIND | 15INR0037 |  | STARR | WIND | SOUTH | 2016 | 0
644 | LOS VIENTOS V WIND [LV5_UNIT_1] | 15INR0021 |  | STARR | WIND | SOUTH | 2015 | 0
645 | PALO DURO WIND | 15INR0050 |  | DEAF SMITH | WIND | PANHANDLE | 2016 | 0
646 | JAVELINA WIND [BORDAS_JAVEL18 & 20] | 13INR0055 |  | ZAPATA | WIND | SOUTH | 2015 | 0
647 | CAPROCK WIND | 10INR0009 |  | CASTRO | WIND | PANHANDLE | 2017 | 0
648 | SAN ROMAN WIND | 14INR0013 |  | CAMERON | WIND-C | COASTAL | 2016 | 0
649 | TORRECILLAS WIND A | 14INR0045a |  | WEBB | WIND | SOUTH | 2016 | 0
650 | TORRECILLAS WIND B | 14INR0045b |  | WEBB | WIND | SOUTH | 2016 | 0
651 | CHANGING WINDS | 13INR0045 |  | CASTRO | WIND | PANHANDLE | 2016 | 0
652 | ELECTRA WIND | 16INR0062 |  | WILBARGER | WIND | WEST | 2016 | 0
653 | HORSE CREEK WIND | 14INR0060 |  | HASKELL | WIND | WEST | 2016 | 0
654 | WILLOW SPRINGS WIND | 14INR0060b |  | HASKELL | WIND | WEST | 2016 | 0
655 | MUENSTER WIND | 15INR0085 |  | COOKE | WIND | NORTH | 2016 | 0
656 | HAPPY WHITEFACE WIND | 15INR0074 |  | DEAF SMITH | WIND | PANHANDLE | 2016 | 0
657 | CHAPMAN RANCH WIND I | 16INR0055 |  | NUECES | WIND-C | COASTAL | 2016 | 0
658 | HIDALGO & STARR WIND | 16INR0024 |  | HIDALGO | WIND | SOUTH | 2016 | 0
659 | BLANCO CANYON WIND (COTTON PLAINS) | 16INR0037 |  | FLOYD | WIND | PANHANDLE | 2016 | 0
660 | BLANCO CANYON WIND (OLD SETTLER) | 16INR0037b |  | FLOYD | WIND | PANHANDLE | 2016
661 | ROCK SPRINGS VAL VERDE WIND | 11INR0082a |  | VAL VERDE | WIND | WEST | 2016
662 | MAGIC VALLEY WIND II (REDFISH 2A) | 14INR0041a |  | WILLACY | WIND-C | COASTAL | 2016
663 | MAGIC VALLEY WIND II (REDFISH 2B) | 14INR0041b |  | WILLACY | WIND-C | COASTAL | 2016
664 | SALT FORK WIND 2 | 16INR0082 |  | CARSON | WIND | PANHANDLE | 2016 | 0
665 | SWISHER WIND | 13INR0038 |  | SWISHER | WIND | PANHANDLE | 2016 | 0
666 | BUCKTHORN WIND 1 | 14INR0057 |  | ERATH | WIND | NORTH | 2016 | 0
667 | BUCKTHORN WIND 2 | 14INR0057b |  | ERATH | WIND | NORTH | 2016 | 0
668 | Planned Capacity Total (Wind) | [6 empty] | 1417
669
670 | Planned Wind Capacity Sub-total (Non-Coastal Counties) |  | WIND_PLANNED_NC |  |  |  |  | 1050
671 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PEAK_PCT_NC | % |  |  |  | 18
672
673 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 367
674 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 37
675
676 | Seasonal Mothballed Resources
677 | MARTIN LAKE U1 (SEASONAL MOTHBALL) |  | MLSES_UNIT1_M | RUSK | COAL | NORTH | 2016 | 815
678 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 820
679 | Total Seasonal Mothballed Capacity | [6 empty] | 1635
680
681 | Mothballed Resources
682 | J T DEELY U1 (MOTHBALLED) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 2018 | 0
683 | J T DEELY U2 (MOTHBALLED) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 2018 | 0
684 | SILAS RAY CTG 5 (RETIRES 3/5/2016) |  | SILASRAY_SILAS_5 | CAMERON | GAS | COASTAL | 1953 | 10
685 | S R BERTRON CTG 2 |  | SRB_SRBGT_2 | HARRIS | GAS | HOUSTON | 1967 | 13
686 | S R BERTRON U1 |  | SRB_SRB_G1 | HARRIS | GAS | HOUSTON | 1958 | 118
687 | S R BERTRON U2 |  | SRB_SRB_G2 | HARRIS | GAS | HOUSTON | 1956 | 174
688 | S R BERTRON U3 |  | SRB_SRB_G3 | HARRIS | GAS | HOUSTON | 1959 | 211
689 | S R BERTRON U4 |  | SRB_SRB_G4 | HARRIS | GAS | HOUSTON | 1960 | 211
690 | Total Mothballed Capacity | [6 empty] | 737

## Background
Release Date: November 2, 2015
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a one-in-ten-years loss-of-load event criteria on a probabilistic basis.
For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner.
In contrast to the Capacity, Demand and Reserves (CDR) report, which addresses the sufficiency of planning reserves on an annual basis as described above, the SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. Consequently, load reduction resources included in the CDR report, such as Emergency Response Service (ERS) and Load Resources that provide operating reserves (LRs), are excluded from the SARA.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur, and thus help fulfill the reporting requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). Several sensitivity analyses are developed by varying the value of certain parameters that affect resource adequacy. The variation in these parameters is based on historic values of these parameters or adjustments by any known or expected changes.