## Slide 1: Transmission Operator Protection System Misoperations 2015 Q2
ERCOT Transmission Protections System Misoperations Data – 138kV and 345kV Combined (Not including Failure to Reclose)
NOTE: Includes only transmission system protection system misoperations from 1/1/2011 thru 6/30/2015 reported by Transmission Operators

## Slide 2: Protection System Misoperations 2015 Q2
 |  | Value
# of Misoperations | Total | 55
 | 345 kV | 7
 | 138 kV | 47
 | < 100 kV | 1
By Category | Failure to Trip | 1
 | Slow Trip | 1
 | Unnecessary Trip during Fault | 36
 | Unnecessary Trip – Non Fault | 17
 | SPS | 0
By Relay System Type | Electromechanical | 11
 | Solid State | 0
 | Microprocessor | 37
 | Other/ N/A | 7
By Equipment Protected | Line | 25
 | Transformer | 4
 | Generator | 2
 | Shunt/Series Capacitor | 0
 | Shunt/Series Reactor | 2
 | Dynamic VAR system | 1
 | Bus | 8
 | Breaker | 13

## Slide 3
Summary of Human Performance Issues noted for 2015 Q2:
138kV line overtrip due to 67 ground inst setting too low. Recent reconductor project caused increase in fault current and existing settings were no longer appropriate.
138kV line overtrip for a remote end bus fault due to incorrect line length setting in relay.
138kV bus overtrip due to miswired output contacts on an SEL line relay. Carrier start contacts accidently miswired to BF start.
138kV breaker trip during trip testing on adjacent circuit breaker due to mislabeled test switch.
138kV GSU trip due to CT wire landed on wrong terminal.
345kV line overtrip due to incorrectly wired SEL relay output contact which prevented carrier blocking signal from being sent.
345kV line overtrip due to incorrect CT polarity on both primary and backup relays.
Multiple 138kV line overtrips due to carrier ground switch closed and coax disconnected from line tuner.
138kV breaker failure to trip due to incorrect zero-sequence voltage applied to relay.
138kV bus overtrip for an external fault due to CTs from new breaker not included in differential logic.
345kV breaker overtrip due to voltage circuits miswired (rolled) in the PT junction box.
Protection System Misoperations 2015 Q2

## Slide 4
Protection System “Human Performance” Trends
“Human” performance misoperations defined as the percentage of misoperation each quarter caused by incorrect settings, incorrect design, logic errors, and as-left personnel errors.

## Slide 5
Misoperations by Entity

## Slide 6
Relay Failures since 2011