## Slide 1: NERC PRC Standards & SPCS Activities Report to ERCOT SPWG
November 12 & 13, 2015
By Sam Francis
Notes: <number>

## Slide 2: SPCS
SPCS is scheduled to meet November 11 & 12, 2015 at MRO Offices in St. Paul MN
  The primary issue to be addressed will be the review of the SPCS paper “UAT Transformer Overcurrent Relay Loadability During a Transmission Depressed Voltage Event”
    The analysis reveals the 150 percent tap requirement in PRC-025-1 for the unit auxiliary transformer high-side overcurrent relay setting is a conservative setting that can be reduced.
    It is highly unlikely that the low side UAT load responsive relays will operate due to a depressed transmission voltage of .85 PU.

## Slide 3: SPCS
  “UAT Transformer Overcurrent Relay Loadability During a Transmission Depressed Voltage Event”
    It is recommended that this guideline be used by the industry to verify that the low side UAT load responsive relays remain secure for a depressed transmission voltage of .85 PU.
    It is recommended that this guideline be used by the industry to verify that the low side UAT load responsive relays remain secure for a depressed transmission voltage of .85 PU.
    It is recommended that the industry highly consider the low side UAT load responsive relays to pick up at a value of no less than 135% of the full load amps of the transformer.

## Slide 4: PRC-005-3 (6)
FERC Order 803
  FERC approved Standard PRC-005-3 (maintenance of reclosing relays at specific locations)
  Directed NERC to develop modifications to PRC-005-3 to include supervisory devices associated with auto-reclosing relay schemes to which the standard applies

## Slide 5: PRC-005-3 (6)
PRC-005-6 draft submitted for comments 06/11/15 - 07/10/15
  Revision of Automatic Reclosing definition to four specific elements
    Reclosing relay
    Supervisory relay(s) – relay(s) that perform voltage and/or sync check functions that enable or disable operation of the reclosing relay
    Voltage sensing devices associated with the supervisory relay(s)
    Control circuitry associated with the reclosing relay or supervisory relay(s)

## Slide 6: PRC-005-3 (6)
A final ballot for PRC-005-6 – Protection System, Automatic Reclosing, and Sudden Pressure Relaying Maintenance concluded 8 p.m. Eastern, Monday, October 26, 2015.
  The standard received sufficient affirmative votes for approval.
    Ballot (Quorum/Approval) 90.00%/96.38%

## Slide 7: PRC-005-3 (6)
The standard will be submitted to the Board of Trustees for adoption and then filed with the appropriate regulatory authorities.

## Slide 8: PRC-005 RSAW Changes
In an effort to answer questions raised at a technical conference and clear up certain issues concerning the proposed RSAW for PRC-005, the PSMTSDT developed a revised RSAW for PRC-005-6 and a New FAQ for the Supplementary Reference and FAQ document.

## Slide 9: PRC-005 RSAW Changes
Proposed additions to RSAW
  Special note to the Auditor
    Entities may vary in the itemization of Components within their PSMP according to their established maintenance practices. Some entities may choose to identify each Component individually; however, other entities may choose approaches such as itemizing the relay panels, local-zones-of-protection, entire stations, or other approaches, whereupon the Entity intends to manage their PSMP based on this itemization. To support this, it is recommended that the Entity be asked to specify how they identify their Components for management of their PSMP, and that subsequent approaches to request of maintenance records respect the Entity’s methodology.

## Slide 10: PRC-005 RSAW Changes
Proposed additions to RSAW
  Change the RSAW to include whenever it talks about Components and their records the brief statement
    “in accordance with the Entity’s PSMP”
  Change the RSAW evidence from dates of the “last two performances” to “most recent performance”

## Slide 11: NEW PRC-005 FAQ
New FAQ Language Pending
  If an Entity is using the time- based methodology, is it required to have a complete Protection System component inventory?
    Utilizing the time- based methodology does not necessarily require a Protection System component inventory. It is noted that an inventory may be beneficial to an Entity and required if future plans are to utilize performance-based methodology on a specific set of components.
    In the time-based methodology, an Entity is required to provide evidence that their PSMP is meeting the expectations of the Implementation Plan, ( i.e. 30, 60, or 100% complete by the required dates). As such, the necessary evidence is dependent on how the PSMP is defined.
    For instance, if an Entity has selected a station-based or panel- based program, then the entity would need to show that they had completed the prescribed maintenance on 30, 60, or 100% of their stations or panels by the dates noted in the Implementation Plan.

## Slide 12: NEW PRC-005 FAQ
  If an Entity is using the time- based methodology, is it required to have a complete Protection System component inventory?
    It is noted that if the Entity’s PSMP is specified at the individual component level (protective relays, dc control circuits, etc.) then an inventory of each component would be required to demonstrate that the Entity had completed a specified % of maintenance of each component.
    It is also noted that an entity may have to provide some information concerning numbers of components of a particular component type in their PSMP if they are found non-compliant with Requirement R3 or R4 in order to establish the violation severity level. However, this will not necessarily require a complete inventory of all components within a component type; but, only sufficient information to establish a VSL level/category.

## Slide 13: Project 2007 – 06 & 06.2 drafting teams
Project 2007-06 originated in 2007 to address FERC Order 693 and SPCTF issues pertaining to PRC-001
  PRC-027-1 was developed by the SPCSDT to address coordination of Protection Systems in isolating faults in the intended sequence during faults
  Requirements 3 and 4 of PRC-001 are to be moved to the new standard PRC-027-1

## Slide 14: Project 2007 – 06 & 06.2 drafting teams
Project 2007-06.2 Phase 2 of System Protection Coordination was established to address the Requirements 1, 2, 5, & 6 of PRC-001 and in Phase 2 of this Project, NERC is proposing the complete retirement of PRC-001-1.1(ii)

## Slide 15: Project 2007 – 06 & 06.2 drafting teams
Project 2007-06.2 Phase 2 drafting team is proposing
  Requirement R1 of PRC-001 will be incorporated into NERC Standard TOP-009-1
  Requirements R2, R5, and R6 of PRC-001 will be retired because those reliability objectives are addressed by other TOP/IRO standards pending regulatory approval

## Slide 16: PRC-027-1
Draft 6 of PRC-027-1
  A final ballot for PRC-027-1 – Coordination of Protection Systems for Performance During Faults concluded 8 p.m. Eastern, Wednesday, October 14, 2015
  The standard received sufficient affirmative votes for approval.
    Ballot (Quorum/Approval) 89.16%/80.94%

## Slide 17: PRC-027-1
The standard will be submitted to the Board of Trustees for adoption.
  Once TOP-009-1 is approved by ballot and adopted by the Board of Trustees, PRC-027-1 will be filed with the appropriate regulatory authorities in conjunction with TOP-009-1 to achieve the complete retirement of PRC-001-1.1(ii).

## Slide 18: Questions