| NOGRR Number | 145 | NOGRR Title | Alignment with NPRR705, Provides Consistency for References to the End Date of the Generation Interconnection Process |
| --- | --- | --- | --- |
| Date of Decision |  | October 29, 2015 |  |
| Action |  | Tabled |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | Upon system implementation of NPRR705, Provides Consistency for References to the End Date of the Generation Interconnection Process. |  |
| Priority and Rank Assigned |  | Not applicable |  |
| Nodal Operating Guide Sections Requiring Revision |  | 2.2.6, Power System Stabilizers |  |
| Related Documents/Revision Requests |  | Nodal Protocol Revision Request (NPRR) 705, Provides Consistency for References to the End Date of the Generation Interconnection Process Planning Guide Revision Request (PGRR) 045, Alignment with NPRR705, Provides Consistency for References to the End Date of the Generation Interconnection Process Resource Registration Glossary Revision Request (RRGRR) 008, Alignment with NPRR705, Provides Consistency for References to the End Date of the Generation Interconnection Process |  |
| Revision Description |  | In the Resource Interconnection Handbook, the term “commercial operations” has a different meaning to Resource Entities and financial institutions involved in construction and financing of Generation Resources than it does in the context of performance testing by ERCOT for new Generation Resources. This Nodal Operating Guide Revision Request (NOGRR) aligns the Nodal Operating Guides with NPRR705 by replacing various terms used to refer to the date on which Generation Resources complete the Resource interconnection process with the proposed defined terms “Commercial Operations Date” and “Resource Commissioning Date” to provide consistency for references to the end of the generation interconnection process. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | Clears up confusion regarding various terms used to describe the end of the generation interconnection process and prevents potential schedule delays in bringing new Resources On-Line. |  |
| OWG Decision |  | On 6/18/15, the Operations Working Group (OWG) was in consensus to table NOGRR145 for one month. On 7/23/15, OWG was in consensus to table NOGRR145. On 8/20/15, OWG was in consensus to recommend approval of NOGRR145 as submitted. On 9/17/15, OWG was in consensus to endorse and forward to ROS the 8/20/15 OWG Report and Impact Analysis for NOGRR145. |  |
| Summary of OWG Discussion |  | On 6/18/15, participants agreed to submit a set of comments for each related Revision Request for a new term than what is proposed in the current Revision Requests and review them next month. On 7/23/15, participants reviewed the proposed language changes for NOGRR145 and discussed the effects this may have if the Planning Working Group (PLWG) makes additional language changes to the associated PGRR045 or NPRR705. Participants concluded that tabling NOGRR145 would allow OWG time to review any new language changes to the associated Revision Requests. On 8/20/15, participants were in consensus that OWG would not propose any additional revisions to the Revision Requests related to NOGRR145. On 9/17/15, there was no discussion. |  |
| ROS Decision |  | On 10/8/15, ROS unanimously voted to recommend approval of NOGRR145 as recommended by OWG in the 9/17/15 OWG Report. All Market Segments were present for the vote. |  |
| Summary of ROS Discussion |  | On 10/8/15, there was no discussion. |  |
| TAC Decision |  | On 10/29/15, TAC unanimously voted to table NOGRR145. All Market Segments were present for the vote. |  |
| Summary of TAC Discussion |  | On 10/29/15, participants noted that NOGRR145 is related to NPRR705 and that a TAC review of NPRR705 is needed before a recommendation can be provided regarding NOGRR145. |  |

| Sponsor |  |
| --- | --- |
| Name | Ted Hailu |
| E-mail Address | thailu@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-3873 |
| Cell Number | (512) 431-8494 |
| Market Segment | Not applicable. |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Lindsay Butterfield |
| E-Mail Address | Lindsay.Butterfield@ercot.com |
| Phone Number | 512-248-6521 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

None

Proposed Guide Language Revision

2.2.6	Power System Stabilizers

(1)	Generation Resources with Power System Stabilizers (PSSs) shall keep their PSSs in-service (“On” or energized and performing as designed by the manufacturer) unless the PSS is installed but not in service as described in paragraph (4)(a)(ii) below.  When available, the PSS shall be active and responsive at all times the generator is synchronized to the ERCOT Transmission Grid and operating at or above its Low Sustained Limit (LSL).  However, if the PSS of a Generation Resource is set to be active and responsive at a point above the LSL for technical reasons, the Generation Resource may request ERCOT to allow an exception to the requirement that the PSS be active anytime the Generation Resource is at or above its LSL.  In order to obtain the exception, the Generation Resource shall notify ERCOT and provide the necessary technical information to ERCOT to justify a higher activation point for the PSS.

(2)	Generation Entities shall notify their QSEs of any change in PSS status (e.g. PSS unavailability due to maintenance or failure and when the PSS returns to normal operation).  QSEs shall notify ERCOT and the TO at the POI of any change in PSS status and shall supply PSS status logs to ERCOT upon request per Protocol Section 6.5.5.1, Changes in Resource Status.

(3)	Synchronous Generation Resources greater than 10 MW installed after January 1, 2008 and on or before December 1, 2010 shall install a PSS and place the PSS in service by June 1, 2011.  Synchronous Generation Resources greater than 10 MW installed after December 1, 2010 shall install a PSS and place the PSS in-service prior to the Resource Commissioning Date of the Generation Resource.  The Generation Resource shall establish PSS settings to dampen modes with oscillations within the range of 0.2 Hz to 2 Hz.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

(4)	Synchronous Generation Resources greater than 10 MW installed before January 1, 2008 are subject to the following requirements:

(a)	All Generation Resources that are in this category shall notify ERCOT and the TSP:

(i)	Whether or not a PSS has been installed; and

(ii)	Whether or not PSS settings have been determined and the PSS has been or will be placed in-service.

(b)	If a PSS was in-service prior to January 1, 2008, the PSS shall remain in-service with the established PSS settings, provided that ERCOT may direct the Generation Resource to modify the settings.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.

(c)	If a PSS is newly installed and/or placed in-service the Generation Resource shall establish PSS settings to dampen modes with oscillations within the range of 0.2 Hz to 2 Hz.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

(5)	If an excitation system on a synchronous Generation Resource greater than 10 MW is modified or replaced after January 1, 2008, the Generation Resource shall install a PSS, establish PSS settings to dampen modes with oscillations within the range of 0.2 Hz to 2 Hz, and place the PSS in-service.  The settings shall be tested and tuned to ensure the excitation system has appropriate damping characteristics.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

(6)	If it is determined that a change in PSS settings or the addition of a PSS to a synchronous Generation Resource would improve overall system performance, ERCOT shall coordinate with the Generation Resource owner to determine appropriate settings.  Within 180 days of determining appropriate settings, the Generation Resource owner shall revise the PSS setting and/or install the PSS.  Any PSS setting established pursuant to this section shall be established to dampen modes with oscillations as directed by ERCOT and place the PSS in-service.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

(7)	At least every five years, Generation Entities shall conduct performance tests on PSS settings or verify PSS performance based on operational data.  If PSS equipment characteristics are modified, the Generation Entity shall conduct a performance test within 30 days of the modification.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

(8)	The results of PSS tests or PSS performance verification shall be supplied to ERCOT and the TSP within 30 days of a request from ERCOT.