## Slide 1
Panhandle Project
ERCOT Independent Review
Jeff Billo, Senior Manager
ERCOT Transmission Planning
TAC, November 19, 2015

## Slide 2: Background
4304 MW of wind generation in Panhandle by end of 2017 (existing plus planned units that meets Planning Guide Section 6.9 requirements as of September 2015)
Previous studies* have identified weak grid and stability constraints limiting Panhandle exports
RPG project proposals
  April 2014: DATC Phoenix Project
  September 2015: Sharyland Panhandle Loop Project
PUCT Open Meeting on September 24, 2015
  A second 345-kV circuit on the Alibates-AJ Swope-Windmill-Ogallala-Tule Canyon transmission line (AAWOTC Line) is under the CREZ Order
*http://www.ercot.com/content/news/presentations/2014/Panhandle%20Renewable%20Energy%20Zone%20Study%20Report.pdf
http://interchange.puc.texas.gov/WebApp/Interchange/application/dbapps/filings/pgSearch_Results.asp?TXT_CNTR_NO=42647&TXT_ITEM_NO=58

## Slide 3: Independent Review Results
Scenario | Transmission Options | Upgrade Cost Assumption (M$) | Annual Production Cost Savings/ Capital Cost | Pass Economic Criteria (3)?
0 | N/A | 0 | N/A | N/A
1 | PH Second Circuit | 80 | 21% (1) | Yes
2 | PH Second Circuit + SC(4) at Alibates and Tule Canyon | 64.25 (SCs only) | 34% (2) | Yes
Compared to Scenario 0
Compared to Scenario 1
Per Protocol Section 3.11.2 (5) the projected annual production cost savings of a project must be greater than or equal to the first year annual revenue requirement of a project which is assumed to be 15% of the capital cost of the project
SC = Synchronous Condenser

## Slide 4: ERCOT Recommendation
ERCOT will seek Board endorsement of the following project:
  Synchronous condensers at Alibates and Tule Canyon
    Each synchronous condenser modeled in this study is based on a generic assumption of a 150 MVA capacity providing 1,050 Ampere (A) of three-phase fault current to the 345 kV system
The cost estimate is $64.25 million
Conclusions
Synchronous Condensers at Alibates and Tule Canyon pass the ERCOT economic planning criteria
The Panhandle second circuit is considered a CREZ project but would also pass the ERCOT economic planning criteria
The transmission upgrades will improve system strength and voltage stability in Panhandle.

## Slide 5: Questions and Answers

## Slide 6: Panhandle Transmission Map
Tule Canyon
Railhead
AJ Swope
Gray
Ogallala
Windmill
Cottonwood
White River
Tesla
Alibates