Dynamics Working Group

Procedure Manual

Revision 10

ROS Approved

(Effective November, 2015)

TABLE OF CONTENTS

Foreword	4

1	Activities of the DWG	5

2	Administrative Procedures	5

2.1	Membership	5

2.2	Duties of Chair and Vice-Chair	5

2.3	Meetings	5

2.4	Reports to ROS	6

3	Dynamics Data	7

3.1	General	7

3.1.1	Software	7

3.1.2	Dynamics Models – General	7

3.1.3	Standard Dynamics Models	7

3.1.4	User-Written Dynamics Models	8

3.1.5	Maintenance of Dynamics Models	8

3.1.6	Dynamics Data for Existing Equipment	9

3.1.7	Dynamics Data for Planned Equipment	9

3.2	Dynamics Data for Equipment Owned by Resource Entities (RE)	9

3.2.1	Dynamics Data Requirements for New Equipment	9

3.2.2	Updates to Existing Dynamics Data	13

3.3	Data for Load Resource	13

3.4	Dynamics Data for Equipment Owned by Transmission-Distribution Service Providers (TDSP)	13

3.4.1	Under Frequency Firm Load Shedding Relay Data (UFLS)	13

3.4.2	Under Voltage Load Shedding Relay Data	14

3.4.3	Protective Relay Data	14

3.4.4	Load Model Data	15

3.4.5	Other Types of Dynamics Data	16

3.4.6	Missing or Problematic Dynamics Data	16

3.4.7	Dynamics Data and Stability Book Storage	16

4	Overview of DWG Activities	17

4.1	Updating Dynamics Data and Flat Starts	17

4.1.1	Schedule for Dynamic Data Updates and Flat Start Cases	17

4.1.2	Dynamics Data Updates	17

4.1.3	Dynamics Data Screening	18

4.1.4	Flat Start Criteria	18

4.2	Post Flat Start Activities	18

4.2.1	Distribution of Flat Start Results and the Dynamics Data Base	18

4.2.2	Stability Book	18

4.2.3	DWG Coordination with the Steady State Working Group	19

4.2.4	DWG Dynamic Contingency Assumptions List	19

4.3	Other DWG Activities	20

4.3.1	Dynamic Disturbance Recording (DDR) Equipment Annual Review	20

4.3.2	Location Requirements:	20

4.3.3	Data Recording Requirements:	20

4.3.4	Triggering Requirements:	21

4.3.51.	Data Reporting Requirements:	21

4.3.6	Maintenance and Testing Requirements:	21

4.3.7	Event Simulation	22

4.3.8	Procedure Manual Revision Guidelines	22

4.4	DWG Study Methodologies and Criteria	25

4.4.1	Transient Voltage Criteria	25

4.4.2	Damping Criteria	25

4.4.3	Voltage Instability Identification in Stability Studies	25

4.4.4	Cascading Identification in Stability Studies	26

4.4.5	Uncontrolled Islanding Identification in Stability Studies	26

4.4.6	Generator Protection Assumptions	27

# Foreword

This Procedure Manual is intended for use by the stakeholder members of the Electric Reliability Council of Texas (ERCOT) for the purpose of creating and maintaining the dynamics database and dynamics simulation cases which are used to evaluate the dynamic performance of the ERCOT system.

The majority of ERCOT members utilize Siemens Power Technologies Inc. (PTI) Power System Simulator (PSS/E) software.  Consequently, the various activities in the procedure manual incorporate PSS/E procedures and nomenclature in describing these activities. Wherever possible, a description of the PSS/E activity is given so users of software other than PSS/E may implement similar actions.

# Activities of the DWG

- DWG builds dynamic data sets and dynamic study cases for the ERCOT system from data supplied by equipment owners. ERCOT coordinates the compilation and publication of dynamics data and dynamics study cases. The dynamics data are published in the form of dynamics study cases (flat start cases) as described within these procedures.

- DWG prepares the annual update of the Stability Book that documents data used in the flat start cases.

- DWG provides a forum for discussing dynamic modeling and system dynamic performance issues and questions.

- Perform other activities as directed by ROS.

# Administrative Procedures

## Membership

DWG membership is open to ERCOT, Transmission Service Providers (TSPs), and Texas Reliability Entity (TRE).

Each ERCOT area, as defined in the dynamic study base cases, shall have at least one designated Dynamics Working Group (DWG) member.  The designated DWG member(s) shall be an employee(s) of an ERCOT Registered TSP. A Designated Agent of a DWG member may represent the DWG member but is not a DWG member itself. All Designated Agents, must follow data sharing rules as outlined in Section 2.5. Designated Agents are permitted on the DWG email exploder list at the discretion of the sponsoring DWG member under the stipulation that a NDA is in place with both the sponsoring DWG member and ERCOT. It is the responsibility of the sponsoring DWG member to inform ERCOT of Designated Agents that no longer represent them and to have them removed from the email exploder list. Participating Designated Agents shall be reviewed annually by DWG.

DWG members and any Designated Agents shall be identified in the DWG roster, and the roster will be updated as needed by DWG.

Each January, the DWG will nominate a Chair and Vice-Chair to be approved by the Reliability and Operating Subcommittee (ROS).

## Duties of Chair and Vice-Chair

The Chair will coordinate the activities of the DWG and represent the DWG at the ROS Meetings and other working group meetings as required.

The Vice-Chair will support the Chair and fulfill the duties of the Chair in the absence of the Chair.

## Meetings

The DWG will meet at least quarterly. DWG meetings are closed meetings. DWG members and Designated Agents of DWG members can attend. If a Designated Agent is not on the DWG roster, the sponsoring DWG member will inform ERCOT and the DWG chair and vice chair of the name of the Agent attending one week prior to the meeting.

The Chair may coordinate additional meetings as needed to facilities the activities of the DWG. The Vice Chair will track attendance and write meeting minutes for in person meetings.

Agendas and meeting schedules will be published at least two weeks prior to the meeting. The minutes of each meeting will be distributed to DWG members.

## Reports to ROS

Each month, the DWG chair will provide a written report to the ROS.

## Dynamic Data Sharing Rules

Dynamic data and dynamic study cases are considered confidential and protected.  They shall be provided to DWG members only.

DWG members can provide dynamics data and dynamic study cases to a consultant for the DWG member’s own studies under the condition that a

Non-Disclosure Agreement is in place between the DWG member and the consultant.

# Dynamics Data

## General

### Software

DWG uses PSS/E version 33 .  During years where a PSS/E version change is being conducted, the previous PSS/E version user defined models shall also be provided until a full transition is completed.

### Dynamics Models – General

ERCOT staff shall inform the ERCOT compliance team if any dynamic data has not been made available or is missing.

Dynamic models shall fulfil the following requirements:

- Each dynamic device requires a model with model parameters that represent the dynamics of the device.

- Dynamic models shall be compatible with the software listed in section 3.1.1. Models should not interfere with the operation of other models.

- All associated dynamic models for a given generating unit shall be provided with the same MBASE in accordance with the machine characteristics where the MBASE is typically the generator MVA rating.

- No model shall restrict the DWG from using any integration time-step less than or equal to a ¼ cycle in simulations.

- Models shall be submitted to both ERCOT and the connecting TSP.

### Standard Dynamics Models

The use of PSS/E Standard dynamics models is preferred when they can accurately represent the dynamic performance of the device being modeled.

### User-Written Dynamics Models

A user written model is any model that is not a standard Siemens PSS/E library model.  When no compatible PSS/E standard dynamics model(s) can be used to represent the dynamics of a device, accurate and appropriate user written models can be used, if accepted by ERCOT and the DWG after being tested for compatibility with the flat start cases.

User-written models for the dynamic equipment and associated data can be in either dynamic model source code or dynamic model object code or dynamic linked library (dll).

- User-written source code, object code, and parameters must be updated for PSS/E version changes per section 3.1.1 or as requested by the DWG and/or ERCOT.  The preferred User-written model format for PSS/E version 33 or later is the DLL format.

- Models requiring allocation of bus numbers shall be compatible with the ERCOT bus numbering system, and shall allow the user to determine the allocation of the bus numbers.

User-written model(s) must be accompanied by the following:

- Technical description of characteristics of the model,

- Block diagram for the model,

- Values and names for all model parameters,

- Text form of the model parameter values (PSSE dyr file format),

- List of all state variables,

- A user’s guide for each model shall be provided and,

- Appropriate procedures and considerations for using the model in dynamic simulations

### Maintenance of Dynamics Models

Maintenance of the models is the responsibility of the device owner. Models shall be maintained in accordance with section 3.2.  Any user-written dynamics models shall also be maintained to fulfill the requirements in section 3.1.4.

### Dynamics Data for Existing Equipment

“As built” data is required for all completed facilities. Unit-specific data shall be reported for generator units installed after 1990. If a permanent new equipment or temporary equipment in place for more than a year is added to the facility then the dynamic model data needs to be re-submitted.  “As Built” data shall be submitted in accordance with section 3.2.

### Dynamics Data for Planned Equipment

The development of future year case data may require an entity to submit the best available information for the planned equipment prior to development of a detailed design. In such cases, estimated or typical manufacturer’s dynamics data, based on units of similar design and characteristics, may be submitted. However, the resource owner shall update the model information upon completion of the detailed design and again upon commissioning the equipment. Dynamics data for planned equipment shall be submitted in accordance with section 3.2.

## Dynamics Data for Equipment Owned by Resource Entities (RE)

### Dynamics Data Requirements for New Equipment

Note: This section addresses the requirements stated in R1 of NERC Standard MOD 032-1 (effective July 1, 2015).

RE’s are responsible for providing models with model parameters resulting in a tuned model that represents the dynamic performance of the device. Final responsibility for the submission and the accuracy of the dynamic data lies on the RE’s. ERCOT and the DWG will provide voluntary assistance if requested by RE’s to complete parameter tuning and prepare PSS/E model records. ERCOT will serve as the single point of contact to facilitate these activities. If the DWG identifies inappropriate or incomplete dynamics data, the appropriate DWG member will act through ERCOT to resolve discrepancies with the data owner. The DWG member of the which the generator is connected is responsible for incorporating the dynamics data received from the RE into the DWG Flat Start cases during annual updates.

RE shall fulfill its interconnection data requirement by completing the corresponding sections of the RARF for their facilities with dynamic models data embedded or attached to their RARF submission.

The following two subsections describe data requirements for two distinct categories of generation facilities:

  - Conventional Generation Facilities Interconnecting More Than 10 MVA of Generation Capacity:

- The model data shall include, at minimum, a generator model, a governor model, an exciter model, and if applicable, a power system stabilizer model and an excitation limiter model.

- Classical model data is not acceptable.

- Estimated or typical model data is not acceptable for units after they are already connected to the ERCOT system.

- In accordance with the SSWG procedure manual, all non self-serve generation connected to the transmission system at 60kV and above with at least 10 MW aggregated at the point of interconnect must be explicitly modeled.  This translates to (1) no lumping of generating units and (2) explicit modeling of each step-up transformer.

- The SSWG manual states that station auxiliary load for generating plants should not be modeled explicitly at the generator bus.  While explicit modeling of station auxiliary load may be necessary for dynamic simulations, DWG dynamics study cases shall not include it.

- All combined cycle steam turbines shall use the CIGRE (International Council on Large Electric Systems) governor model, as developed by Siemens PTI and implemented by ERCOT.

- All combined cycle gas turbine models shall be compatible with the CIGRE steam turbine model.

  - Intermittent Renewable Resources (e.g. Wind and Solar) Facilities:

The RE shall provide the following data as applicable to the generator technology:

- Model, data and description of voltage control method.

- Model, data and description of how they will meet ERCOT reactive requirements.

- A one-line diagram of the proposed facility.

- Data for all transformers. The data should include:

  - MVA rating.

  - High and low side rated voltage.

  - Number of taps, and step size.

  - Impedance, including base values if different from rated values listed above.

- Dynamic modeling data including:

- Wind generator or solar inverter manufacturerand type.

- Rated voltage.

- Rated MVA.

- Reactive capability, leading and lagging.

- Rated MW output.

- Net MW output.

- Transient or subtransient reactance, including base values, if applicable.

- Transient or subtransient time constant, if applicable.

- Total inertia constant, H, of generator, including the shaft and gearbox, if applicable.

- Under frequency and under voltage protection settings.

- Over frequency and over voltage protection settings.

- Number of machines by manufacturer types.

- Reactive resource data such as capacitor banks, STATCOMS, etc. Provide the number of devices, location of the devices, step size, speed of switching, location where voltage is sensed and controlled, control strategy, and voltage limits. For dynamic reactive devices, provide the appropriate model and data.

- Line data from the point of connection to each generator.  
Include:

- Line type (overhead or underground)

- Line length

- Line resistance in ohms/1000 ft

- Line reactance in ohms/1000 ft

- Line susceptance in mhos/1000 ft

- Wind turbine models shall account for rotor mass, aerodynamic energy conversion, and pitch control.

### Updates to Existing Dynamics Data

The requirements of section 3.2.1 apply to all updated models and data.  Any change in generator dynamics data, associated generator data, or wind farm items listed in section 3.2.1 , or other types of equipment listed in this procedure, determined either through field testing or after changing relevant equipment or equipment settings shall be reported to ERCOT and the TSP to which they are connected, by the RE within 30 days.  Model data shall be provided in the same form (such as PSS/E model data sheets) as required in section 3.2.1.   Model parameter tuning updates may also be required to perform dynamic studies. Obsolete data should be deleted

As per section 3.1.4., when updated equipment modifications are provided, data for all other related models shall be updated with the same MBASE.  For example, replacement of an old excitation system with a new excitation system would require an RE to provide updated model data.

## Data for Load Resource

Load Resource models used for system frequency response shall be prepared using a PSSE standard model. Data for the Load Resource model shall be documented in the Stability Book and .dyr files posted to the DWG data site.

## Dynamics Data for Equipment Owned by Transmission-Distribution Service Providers (TDSP)

### Under Frequency Firm Load Shedding Relay Data (UFLS)

UFLS data shall be prepared annually in accordance with ERCOT and NERC standards. TDSPs are responsible for preparing the UFLS relay model records for their respective loads .  The TDSP shall submit the UFLS relay data to ERCOT in the form of a PSS/E dyre file using an appropriate model. The models should contain the necessary information to properly represent the UFLS relay actions in a dynamic study, including:

- Owner and operator of the UFLS program.

- Size and location of customer load, or percent of connected load, to be interrupted.

- Corresponding frequency set points.

- Overall scheme clearing times (includes all time delays, breaker clearing times, etc.).

Also, the TDSP should indicate any other schemes that are part of or impact the UFLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UVLS and Special Protection Systems.

All UFLS data will be documented in the annual Stability Book.

### Under Voltage Load Shedding Relay Data

Note: This section addresses requirements stated in NERC Standards PRC-20 and PRC-21 (soon to be PRC-010).

After installation of any under voltage load shedding (UVLS) relays, the TDSP installing the UVLS relays will submit the corresponding relay model to ERCOT during the annual data update and as needed for DWG studies. The DWG member shall submit the UVLS relay data in the form of a PSSE dyre file using an appropriate model.  The model shall contain the necessary information to properly represent the under voltage relay actions in a dynamic study, including:

- Owner and operator of the UVLS program.

- Size and location of customer load, or percent of connected load, to be interrupted.

- Corresponding voltage set points.

- Overall scheme clearing times (includes all time delays, breaker clearing times, etc.).

Also, the TDSP should indicate any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems.

All UVLS data will be documented in the annual Stability Book.

### Protective Relay Data

The operation of protection, control, and special protection systems can affect the dynamic performance of the ERCOT system during and following contingencies.  Planning, documenting, maintaining, or other activities associated with these systems is outside the scope of the DWG.  However, because they can affect dynamic performance, the DWG should, on an as needed basis, identify and document protection, control, and special protection systems for inclusion to its dynamic data sets.  Identification of these protection systems will normally require the assistance of individuals or groups outside the DWG.  The specific information to be considered for inclusion will depend on the type, purpose, and scope of study.

Protection, control, and special protection systems included in the DWG database should be in the form of a  dynamic model and shall be compatible with the software listed in section 3.1.1.  Protection, control, and special protection systems adequately modeled for dynamic purposes by other working groups only need to be referenced in the DWG study reports.

The DWG member, as part of the annual database update, shall review and update as necessary protection, control, and special protection systems already in the DWG database.  This review should include evaluating the existing data for applicability and accuracy.

Protective relay data included in a DWG flat start case shall be documented in the Stability Book.

### Load Model Data

Note: This section addresses the requirements stated in R1 of NERC Standard MOD 032-1 and R2.4.1 of NERC Standard TPL-001-4.

Another key component of any dynamic study is the load model and its representation as a function of changing frequency or voltage.  The load model can have a significant effect on results of dynamic analysis.  For this reason, it is important to use an appropriate load model during the study.

DWG shall review and update standard load models for each area, composed of a mix of constant impedance (Z), constant current (I), and constant power (P) representations, known as ZIP models.  PSS/E CONL activity is used to incorporate the ZIP models into a PSS/E study.

Additional load detail (large motor MW, small motor MW, etc.) is provided in the Annual Load Data Request (ALDR).  ALDR information can be used with generic motor model parameters for screening purposes.  Within 30 days of a written request from ERCOT, a TSP will provide load models with induction motor parameters in DYR format compatible with the software in 3.1 and documentation about the load model.  .

A standard load-frequency dependency model (LDFRAL) will also be documented in the Stability Book.

Each study performed by the DWG, ERCOT, or by TDSP members submitted to an ERCOT regional planning group should document the load modeling assumptions in the body of the report.

### Other Types of Dynamics Data

Note: This section addresses requirements stated in R1 of NERC Standard MOD 032-1 (effective July 1, 2015).

After a dynamic element planned to be installed on the transmission system owned by a TDSP is modeled in the SSWG base cases such as an SVC, STATCOM, Superconducting Magnetic Energy Storage (SMES), DC ties, and Variable-Frequency Transformer data, the DWG member of the TDSP owning the equipment will provide the corresponding PSS/E model to the designated DWG member during the annual dynamic database update or as needed for DWG studies.

### Missing or Problematic Dynamics Data

The DWG is responsible for reviewing the dynamics data on an annual basis or as requested by ROS and reporting to the ROS any missing data or unresolved issues relating to data submission requirements.  DWG will report select data problems to the respective ERCOT working group per Section 4.2.3.

If there are problems with the data, the DWG will work through ERCOT with the equipment owner to resolve data problems. However, the final responsibility for the submission and the accuracy of the data lies with the equipment owner. All of the data and the revisions requested by ERCOT shall be resolved by the entity owning the equipment within 30 days.  Until valid data becomes available, ERCOT or the DWG member to whose system the equipment is connected shall recommend an interim solution to the missing or problematic data.

### Dynamics Data and Stability Book Storage

ERCOT shall make available to the DWG members in electronic format the dynamics data described in this procedure.  ERCOT shall maintain a repository of dynamics data approved by the DWG and will maintain the submitted revisions. ERCOT staff shall inform the ERCOT compliance team if any data is missing or has not been made available.

# Overview of DWG Activities

## Updating Dynamics Data and Flat Starts

### Schedule for Dynamic Data Updates and Flat Start Cases

Note: This section addresses requirements stated in R2 of NERC Standards TPL-001-4.

Each February, the DWG shall prepare a schedule for updating dynamics data and preparing the DWG flat start cases and providing dynamic contingencies.  The schedule shall be constructed to align with the Steady State Working Group (SSWG) schedule so that a seed case for a flat start can be selected following a finish date of an update.

Typical Schedule:

- Long term case completed before summer and typically finished in March

- Near term case completed before summer and typically finished in June

- HWLL term case completed concurrently with the near term case and typically finished in September.

The DWG shall prepare the following flat start cases based on the following SSWG steady state cases:

- Near Term On-Peak:  Second year (Y+2) summer on-peak case of the latest Dataset B cases

- Near Term Off-Peak Case:  The high wind low load case (Y+3)    off-peak case from the latest Dataset B cases

- Long Term On-Peak Case:  Last year (Y+6) of summer on-peak case of the latest  Dataset B cases

The DWG may choose to flat start additional cases.

After January 1st, 2015, ERCOT shall prepare all the flat start cases.

### Dynamics Data Updates

Each DWG member shall review the dynamic data from the prior year for its portion of the ERCOT System and provide necessary updates according to the schedule established in section 4.1.1. The changes in the data must be identified and submitted with the updated data.

Data for mothballed units shall be retained. Obsolete data should be deleted.

Other revisions of data that should be submitted to the designated DWG member include updates to the load model, Zsource corrections, generation netting, or any other modifications to the network necessary for dynamic studies.

### Dynamics Data Screening

DWG members should review the dynamics data for equipment connected to their system for completeness and applicability.  The data should be appropriate for the model, and the model should be appropriate for the equipment.  Before submitting data for inclusion in updated dynamics base cases, each DWG member should perform dynamics data screening.

### Flat Start Criteria

DWG Flat Start cases shall:

- Initialize with no errors;

- Demonstrate that simulation output channels for frequency, voltage and power do not deviate from an acceptable range for a ten-second run with no disturbance.

- The product of a successful flat start will be a PSS/E simulation-ready base case (the unconverted base case) with its associated dynamic data files including user models (.dyr, .obj, .lib, and .dll files), stability data change documentation, python (.py) files and response files (.idv) files.  The product of a successful flat start also includes the steps taken to build the flat start case such as network model changes (i.e. changing the schedule of the North DC, tuning voltages, etc.).

## Post Flat Start Activities

### Distribution of Flat Start Results and the Dynamics Data Base

Upon completion of each flat start, an electronic copy of all dynamics data and final data files will be distributed electronically in PSS/E format to each of the DWG members and to ERCOT System Planning for archiving.  This dynamic data distribution shall be within the schedule established by the DWG for the given flat start.

### Stability Book

The Stability Book is an annual document used to record dynamics data changes and/or corrections required during the flat start processes.  The flat start coordinator shall prepare the annual stability book.  Recommendations to revise load flow data are also included in the book.  DWG Members are required to communicate these recommendations to other respective working groups, including Steady State Working Group, Operations Working Group, and Network Data Support Working Group, to eliminate recurring problems.

The following information is included in Stability Book:

- Deviation tables or plots of the flat start results are included to verify the successful completion of the flat start process.

- Dynamics data.  This data is in the DOCU ALL PSS/E activity format.

- Load shedding relay data submitted by each of the appropriate DWG members.

- Additional information identified for inclusion by Section 3.4

### DWG Coordination with the Steady State Working Group

To support coordination with the Steady State Working Group, Operations Working Group, and Network Data Support Working Group a list of the changes to the items listed below will be provided to the ERCOT Steady State Working Group Representative member to assure conflicting data is addressed.

ERCOT shall compile the list following finalization of the flat start.

For Flat Starts, data changes for one of categories list below submitted by shall be grouped and labeled by the submitter to support efficient compilation of these changes at the end of the flat start by ERCOT.  The following items should be provided to these working groups for data coordination:

- Unit MVA Base.  This is also known as MBase used by the dynamic model.

- Zsource changes.  Reactive machine impedances required for dynamic initialization of models.

### DWG Dynamic Contingency Assumptions List

The DWG shall construct a dynamic contingency assumptions list detailing contingency assumptions for each TSP for the purpose of screening studies conducted by ERCOT and the DWG members. ERCOT and the DWG members shall annually review and update the dynamic contingency assumption list. Upon completion of the annual review, ERCOT shall collect the contingency assumptions and submit the finalized dynamic contingency assumptions list to the DWG.

The assumptions would include:

- Breaker trip time for normal clearing,

- Breaker trip time for delayed clearing due to stuck breaker

- Breaker trip time for delayed clearing due to relay failure

- Relay characteristic assumptions to assess generic apparent impedance swings that can trip any transmission system elements

- Other assumptions deemed necessary by DWG as specified during the annual review

### DWG Dynamic Contingency Database

- The DWG shall prepare a Dynamic Contingency Database according to a standard spreadsheet format.  The spreadsheet format will be reviewed annually.  The spreadsheet of dynamic contingencies will be distributed to DWG members.

## Other DWG Activities

### Dynamic Disturbance Recording (DDR) Equipment Annual Review

Note: This section addresses NERC Blackout Recommendation 12b.

The purpose for installing dynamic disturbance recording (DDR) equipment is to:

- Collect actual data following a dynamic disturbance.

- Enable the results of dynamic simulations to be evaluated for effectiveness.

### Location Requirements:

ERCOT and the DWG shall prepare a list and perform an annual review of facilities that operate above 100 kV, are part of a dynamic stability (not transient stability) interface, and require the installation of a DDR.  ERCOT and the DWG shall forward any revised DDR facility list to the Reliability and Operating Subcommittee (ROS) for its review and approval.  Upon approval of the DDR facility list, facility owners shall have six months to install and place in service DDRs at each listed facility.

DDRs shall be removed or taken out of service by the same process.

### Data Recording Requirements:

The appropriate quantities, such as the following, must be recorded for equipment operating at 100 kV or above at facilities where DDR equipment is required:

- Bus Voltage

- Line Current

- MW and MVAR flow

- Frequency

### Triggering Requirements:

DDR equipment triggering should occur for one or more of system voltage magnitude, current magnitude, or frequency magnitude disturbances (V, I, or f) without requiring any circuit breaker operations or trip outputs from protective relay systems.

Disturbance recording equipment shall be capable of continuous recording for not less than 5 minutes and shall be retrievable for a period of not less than 72 hours.

Dynamic Disturbance Recorders (DDR’s) should be time synchronized when practical.

The sampling rate for DDR’s should be 240 samples per second.

### 4.3.5 Data Reporting Requirements

At DDR installations where communication equipment exists and it is practical, communication from the device should be automatic to an ERCOT central database.  Where communication equipment does not exist or automatic communication from the device to ERCOT is not practical, facility owners who have installed DDR's may report data for any event they consider significant to ERCOT.  ERCOT may request facility owners who have installed DDR's to report data for any event.  ERCOT’s request should be made within 24 hours after the event to allow the transmission provider adequate time to retrieve the data.  DDR data of significant events shall be reported to ERCOT at least annually for compilation into a database.

The database compiled by ERCOT shall be made available to all ERCOT members for verifying and improving system models, or analyzing system disturbances.  Submitted data will be retained by ERCOT for a minimum of one year.

DDR records shall be provided to ERCOT and NERC upon request. Disturbance records shall be retained and made available for at least one year from the date the record was made.  DDR records shall be shared between entities, upon request, for the analysis of system disturbances.

### 4.3.6 Maintenance and Testing Requirements:

DDR equipment must be properly maintained and tested in accordance with the manufacturer’s recommendations.  Maintenance and test records shall be provided to ERCOT upon request within 30 business days.

### 4.3.7 Event Simulation

Note: This section addresses NERC blackout recommendation 14.

When requested by ROS, the DWG will simulate an actual disturbance event for the purpose of assessing the fidelity of the ERCOT dynamics models and data against actual system performance recordings of the event. In addition, the DWG will annually consider recent significant events to determine their suitability for an event simulation. The DWG will consider their work load and the type of information likely to be obtained in making a decision as to whether to simulate an event.

### 4.3.8 Procedure Manual Revision Guidelines

Note: This section addresses requirements stated in NERC Standards MOD-013-0 (R2).

The DWG is responsible for maintaining and updating this Procedure Manual.  Revisions, additions and/or deletions to this Procedure Manual may be undertaken at such times that the DWG feels it is necessary due to changes in PSS/E dynamic simulation software or to meet new and/or revised requirements of NERC, ERCOT, or any other organization having oversight or regulatory authority.

At least annually, the DWG Chair shall request a thorough review of the current Procedure Manual for any needed revisions.  The notification will request that proposed revisions be submitted to the DWG Chair (or the Chair’s designate) for consolidation and distribution to all DWG members for comment and/or additional revision. The DWG Chair should give consideration to being able procedure complete the review and revision process in time to avoid any delays in collecting dynamic data or completing other DWG work.

The DWG Chair may seek approval of any revision, addition, or deletion to the Procedure Manual by email vote, regular meeting, or called special meeting as deemed necessary or requested by DWG membership.

## Recommended DWG Study Methodologies

Note: This section addresses, in part, requirements R4, R5 and R6 of NERC Standard TPL-001-4 (effective January 1, 2016)

Voltage stability margin, transient voltage criteria, and damping criteria are described in the ERCOT Planning Guide Section 4.

### Voltage Instability Identification in Stability Studies

Voltage Instability is indicated by severely low bus voltage or bus voltage collapse.

Voltage Instability could cause:

- Motor stalling leading to significant amount of customer initiated motor tripping.

- Loss of generator(s) due to low voltage

- Voltage collapse of an area

### Cascading Identification in Stability Studies

Cascading Definition - Cascading is defined as the uncontrolled loss of any system facilities or load, whether because of thermal overload, voltage collapse, or loss of synchronism, except those occurring as a result of fault isolation. Cascading is indicated by one or more of the following conditions:

- Uncontrolled sequential loss of generators

- Uncontrolled sequential loss of load

- Uncontrolled sequential loss of branches.

Cascading could cause conditions like:

- Voltage collapse of an area

- Expanding number of buses with voltage instability

- System islanding, frequency instability due to power-load unbalance

NERC Definition: The uncontrolled successive loss of system elements triggered by an incident at any location. Cascading results in widespread electric service interruption that cannot be restrained from sequentially spreading beyond an area predetermined by studies.

### Uncontrolled Islanding Identification in Stability Studies

Uncontrolled islanding is the separation and loss of synchronism between a portion of the interconnection and the remaining interconnected system.  Islanding originates with uncontrolled loss of branches, ending with the formation of subnetwork islands.

Generators disconnected from the System by fault clearing action or by a Special Protection System are not considered out of synchronism.  Similarly, islands formed from being disconnected from the System by fault clearing action or by a Special Protection System are not considered an uncontrolled island.

Subnetworks islands have the following characteristics:

- The subnetwork islands have both generation and load to support the continuation of the island.

- The subnetworks formed are not connected to each other.

Uncontrolled islanding in a screening study could cause:

- Out-of-step generators

- Off-nominal frequency disturbances

- Eventual collapse of one of the islands due to frequency or voltage instabilities caused by the generation-load unbalance in the subnetwork island.

### Generator Protection Assumptions

Note: This section addresses, in part, requirements R3.3.1.1 and R4.3.1.2 of NERC Standard TPL-001-4 (effective January 1, 2016).

If dynamic models are not provided for Generator protection schemes, generic generator protection may be assumed for screening purposes

- For synchronous generators, a rotor angle swing greater than 180 degrees may be considered an unstable generator.

- Generators may be assumed to be compliant with the minimum requirements of Section 2.9 Voltage Ride-Through Requirements for Generation Resources of the ERCOT Nodal Operating Guide.

- Generators may be assumed to be compliant with the minimum requirements of Section 2.6 Requirements for Under/Over-Frequency Relaying of the ERCOT Nodal Operating Guide.

Additional load detail (large motor MW, small motor MW, etc) is provided in the Annual Load Data Request (ALDR). ALDR information can be used with generic motor model parameters for screening purposes.