## 1) General Information
CenterPoint Energy Distribution Loss Factor for 2016 R2
----> | Changes for 2016 are shown in bold red font
General Information on Distribution Loss Factor:
The Distribution Loss Factor is a percent that ERCOT will use to determine distribution losses for each Distribution Service Provider.
See ERCOT Protocols Section 13: Transmission and Distribution Losses, which was updated on December 1, 2010. See following
protocol link: http://www.ercot.com/mktrules/nprotocols/current
According to this protocol, ERCOT will calculate Distribution Loss Factors for each Settlement Interval of the Operating Day for
settlement purposes. Distribution Loss Factors will be calculated from the data provided by Distribution Service Providers using
the following equation
SILFi = F1 * (SIELi/AAL) + F2 + F3 / (SIELi / AAL)
Where:
i = interval (15 minutes)
SILFi = Settlement Interval Distribution Loss Factor
SIELi = Settlement Interval estimated ERCOT System Load
AAL = Annual Interval Average ERCOT System Load (15 minute basis)
F1, F2, F3 = Coefficients derived from regression analysis of the TDSP loss study results
AAL = Annual Total System MWh / (Number of settlement intervals in the year) Typically = 365 days * 24 hrs * 4 intervals
----> | AAL value for use in 2016 = 9,940 MWH
AAL value for use in 2015 = 9,741 MWH
AAL value for use in 2014 = 9,290 MWH
AAL value for use in 2013 = 9,304 MWH
AAL value for use in 2012 = 9,463 MWH
AAL value for use in 2011 = 9,034 MWH
AAL value for use in 2010 = 8,785 MWH
AAL value for use in 2009 = 9,043 MWH
AAL value for use in 2008 = 8,794 MWH
Customer Coding for CenterPoint Energy:
Distribution customers that take service at secondary voltage are coded "D"
Distribution customers that take service at primary voltage are coded "E"
CenterPoint Energy customers taking service at transmission level voltages have no distribution losses associated with their energy
delivery. Therefore, each transmission ESI-ID account has been coded with a "T", and their losses are determined by ERCOT rules for
transmission customers.
For "D" Secondary Customers
F1 = 0.017560
F2 = 0.000402
F3 = 0.019800
AAL for ERCOT (15 mins) = 9,940
For "E" Primary Customers
F1 = 0.012000
F2 = 0.000015
F3 = 0.000970
AAL for ERCOT (15 mins) = 9,940
Assumptions
1. Assume AAL for CNP corresponds to AAL for ERCOT
2. However, the peak for CNP is proportionately greater than the peak for ERCOT relative to AAL.
Ratio of Peak to AAL
|  | CNP | ERCOT
|  | 2.0462 | 1.7519
Ratio of Peak to AAL for CNP is not proportional to ERCOT
| 2013 for use in 2014 |  | 2014 for use in 2015 |  | 2015 for use in 2016
| 15 mins | 1 hour | 15 mins | 1 hour | 15 mins | 1 hour
CNP Peak | 3687 | 14748 | 3678.75 | 14715 | 3923.5 | 15694
CNP AAL | 1824.25 | 7297 | 1882.25 | 7529 | 1917.5 | 7670
ERCOT Peak | 16915.75 | 67663 | 16712.75 | 66851 | 17414 | 69656
ERCOT AAL | 9290 | 37160 | 9741 | 38964 | 9940 | 39760
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % losses (and DLF) above AAL are
increased an amount that is consistent with this higher loading at peak, so that when ERCOT hits peak, % losses will correspond to CNP peak.
Methodology upon which the calculation of loss factor was made:
Over the years, CenterPoint Energy has developed system loss equations for each part of the system. Equations for distribution
substation transformer losses, distribution primary conductor losses, distribution transformer losses and secondary conductor losses
were utilized to calculate the total losses on the CenterPoint Energy distribution system for various load levels. See Tab 3 - Loss Equations.
|  | Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
The constants (A & B) for each of the equations were updated in 2015 for use in 2016 as follows:
1. Substation Transformer Losses (The A B constants for substation transformers were updated for 2016)
The current substation transformer database was used to determine the total "No-load" losses for all transformers on the system.
This database contains test data for every substation transformer.
The total no-load losses are 20.867 MW.
Also, the database provided the total "Load" losses for the transformers on the system at rated trf load.
This value is 54.789 MW at 17,546 MW load level.
This results in a total of 75.656 MW of substation transformer losses at approximately 17,546 MW at CNP.
The constants in the system loss equations were adjusted to match this result. See Tab 3.
2. Primary Conductor Losses (No change in the A B constants for primary conductor for 2016)
The primary conductor losses for 2007 were considered to be similar to the losses in 2006, but the constant for the system loss
equation was increased 2.5% due to the increased loading on our circuits which is a result of our revised design criteria.
The design criteria allows higher loadings due to an increase in switching operations under contingency conditions from
2 pairs of switching operations to 4 pairs of switching operations.
For 2016, there is no further change in the system loss equations.
3. Distribution Transformer Losses (The A B constants for distribution transformers were updated for 2016)
An inventory of the distribution transformers was downloaded from the GIS system. For every size transformer
the "No-load" losses and "Load" losses were determined by various test reports. This information was entered
for each size of transformer to determine the total "No-load" losses and the total "Load" losses for the distribution transformers.
Additionally, a TLM (Transformer Load Maintenance) Program was used to calculate no-load and load losses.
Since the no-load losses used in the TLM program were based on older/higher values from 1985 and the GIS spreadsheet
used more current test values from 2000-2005, the results of the two programs were averaged together to get
a balanced result for "no-load" losses for a distribution system that has both old and new transformers.
The "load losses" from both methods were very close, so the load losses from GIS were used.
See Tab 3 for the updated A B constants for distribution transformers.
4. Secondary Conductor Losses (No change in the A B constants for secondary conductor for 2016)
The constant in the system loss equation for secondary losses for 2016 is same as used in previous years.
5. AAL for ERCOT
The AAL for ERCOT was updated based on information from ERCOT. The new value for 2016 is 9,940 MWH for 15 minutes.
DLF Coefficients (F1, F2 and F3)
For both primary and secondary customers, the F1, F2 and F3 coefficients were selected to provide a curve fit with the loss equations that were
developed above. F1 impacts the right side of the curve, F2 impacts the middle/entire curve, and F3 impacts the left side of the curve. These
coefficents were adjusted to get a curve fit in the most critical areas. See spreadsheet and graphs in Tab 2 - Loss Analysis.
The F1, F2, and F3 coefficients for D secondary customers and E primary metered customers for 2015 are shown above.
Overall results:
For "E" Primary Customers |  |  | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 for use in 2016
|  | DLF at AAL | 1.254% | 1.311% | 1.291% | 1.241% | 1.272% | 1.299%
|  | DLF at ERCOT Peak | 2.039% | 2.131% | 2.072% | 2.105% | 2.05% | 2.159%
For "D" Secondary Customers |  |  | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 for use in 2016
|  | DLF at AAL | 3.681% | 3.663% | 3.705% | 3.704% | 3.739% | 3.776%
|  | DLF at ERCOT Peak | 4.124% | 4.218% | 4.178% | 4.197% | 4.144% | 4.247%
Questions:
If you have any questions, please call Richard Moffatt at CenterPoint Energy at 713-945-4162 or Ben Kirchhofer at CenterPoint Energy at 713-207-6313
or email at richard.moffatt@centerpointenergy.com or ben.kirchhofer@centerpointenergy.com
CenterPoint Energy Distribution Loss Factor For 2016
Oct 26, 2015

## Loss Comparison (hidden)
Loss Comparison With Different A/B Constants |  |  |  |  | Loss Analysis 02.xls
|  | Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
|  | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 1995 | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 2001 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 2001 Modified | #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| Load |  | Sub Trf Losses |  | Primary Cond Losses |  | Dist Trf Losses |  | Sec Cond Losses |  | Total Losses | Total Losses
| (MW) |  | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%)
1995 | 4000 |  | 22.7412 | 0.5685% | 16.6095 | 0.4152% | 106.3877 | 2.66% | 6.3214 | 0.158% | 152.0598 | 3.801%
2001 | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 7600 |  | 37.0131 | 0.9253% | 60.0587 | 1.501% | 130.2566 | 3.256% | 23.1303 | 0.5783% | 250.4587 | 3.296%
2001 | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 11200 |  | 60.1434 | 1.504% | 130.3012 | 3.258% | 168.4144 | 4.21% | 50.0129 | 1.25% | 408.8719 | 3.651%
2001 | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note: All % calculations are based on the total load which is shown in column 2.

## Loss Analysis 1995 (hidden)
HL&P Distribution Loss Analysis |  |  | 1995 |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | 19.2415 | 2380.7585 | 5.9514 | 2374.8071 | 100.482 | 2274.325 | 2.2011 | 127.8761 | 79.0922 | 48.7838 | 5.328% | 1.041% | 4.287% | 2.845% | 2.484% | 3.296% | 68.2691 | 59.607
2 | 2800 | 19.9524 | 2780.0476 | 8.1151 | 2771.9325 | 101.6834 | 2670.2491 | 3.0341 | 132.7851 | 92.2743 | 40.5108 | 4.742% | 1.214% | 3.528% | 2.879% | 1.863% | 3.296% | 80.6186 | 52.1665
3 | 3200 | 20.7726 | 3179.2274 | 10.6129 | 3168.6145 | 103.0686 | 3065.5459 | 3.999 | 138.453 | 105.4563 | 32.9967 | 4.327% | 1.388% | 2.939% | 2.914% | 1.413% | 3.296% | 93.2456 | 45.2075
4 | 3600 | 21.7022 | 3578.2978 | 13.4444 | 3564.8534 | 104.6369 | 3460.2165 | 5.0949 | 144.8784 | 118.6383 | 26.2401 | 4.024% | 1.561% | 2.463% | 2.949% | 1.076% | 3.296% | 106.1501 | 38.7284
5 | 4000 | 22.7412 | 3977.2588 | 16.6095 | 3960.6493 | 106.3877 | 3854.2617 | 6.3214 | 152.0598 | 131.8204 | 20.2394 | 3.801% | 1.734% | 2.067% | 2.983% | 0.8182% | 3.296% | 119.3321 | 32.7277
6 | 4400 | 23.8895 | 4376.1105 | 20.1079 | 4356.0027 | 108.3204 | 4247.6823 | 7.6778 | 159.9955 | 145.0024 | 14.9931 | 3.636% | 1.908% | 1.728% | 3.018% | 0.6183% | 3.296% | 132.7917 | 27.2038
7 | 4800 | 25.1472 | 4774.8528 | 23.9392 | 4750.9137 | 110.4343 | 4640.4793 | 9.1634 | 168.6841 | 158.1844 | 10.4997 | 3.514% | 2.081% | 1.433% | 3.053% | 0.4616% | 3.296% | 146.5287 | 22.1554
8 | 5200 | 26.5142 | 5173.4858 | 28.1032 | 5145.3826 | 112.729 | 5032.6536 | 10.7777 | 178.1241 | 171.3665 | 6.7576 | 3.425% | 2.255% | 1.171% | 3.087% | 0.3381% | 3.296% | 160.5433 | 17.5808
9 | 5600 | 27.9906 | 5572.0094 | 32.5997 | 5539.4098 | 115.2037 | 5424.2061 | 12.52 | 188.3139 | 184.5485 | 3.7654 | 3.363% | 2.428% | 0.9345% | 3.122% | 0.2407% | 3.296% | 174.8354 | 13.4785
10 | 6000 | 29.5764 | 5970.4236 | 37.4283 | 5932.9954 | 117.8578 | 5815.1376 | 14.3897 | 199.2521 | 197.7305 | 1.5216 | 3.321% | 2.602% | 0.7192% | 3.157% | 0.1641% | 3.296% | 189.405 | 9.8471 | Highlighted Area Represents 96% Range
11 | 6400 | 31.2715 | 6368.7285 | 42.5887 | 6326.1398 | 120.6908 | 6205.449 | 16.3862 | 210.9372 | 210.9126 | 0.024651 | 3.296% | 2.775% | 0.5207% | 3.191% | 0.1045% | 3.296% | 204.2522 | 6.685
12 | 6800 | 33.076 | 6766.924 | 48.0808 | 6718.8432 | 123.702 | 6595.1412 | 18.5089 | 223.3677 | 224.0946 | -0.72694 | 3.285% | 2.949% | 0.3362% | 3.226% | 0.05869% | 3.296% | 219.3768 | 3.9908
13 | 7200 | 34.9898 | 7165.0102 | 53.9042 | 7111.1059 | 126.8908 | 6984.2152 | 20.7571 | 236.542 | 237.2766 | -0.73466 | 3.285% | 3.122% | 0.1632% | 3.261% | 0.02449% | 3.296% | 234.779 | 1.763
14 | 7600 | 37.0131 | 7562.9869 | 60.0587 | 7502.9282 | 130.2566 | 7372.6717 | 23.1303 | 250.4587 | 250.4587 | 0 | 3.296% | 3.296% | 0% | 3.296% | 0% | 3.296% | 250.4587 | 0
15 | 8000 | 39.1456 | 7960.8544 | 66.544 | 7894.3104 | 133.7988 | 7760.5116 | 25.6279 | 265.1163 | 263.6407 | 1.4756 | 3.314% | 3.469% | -0.155% | 3.33% | -0.01625% | 3.296% | 266.4159 | -1.2996
16 | 8400 | 41.3876 | 8358.6124 | 73.3597 | 8285.2527 | 137.5168 | 8147.7359 | 28.2492 | 280.5133 | 276.8228 | 3.6905 | 3.339% | 3.642% | -0.303% | 3.365% | -0.02544% | 3.296% | 282.6506 | -2.1373
17 | 8800 | 43.7389 | 8756.2611 | 80.5057 | 8675.7554 | 141.41 | 8534.3454 | 30.9936 | 296.6482 | 290.0048 | 6.6434 | 3.371% | 3.816% | -0.4449% | 3.4% | -0.02858% | 3.296% | 299.1628 | -2.5146
18 | 9200 | 46.1996 | 9153.8004 | 87.9817 | 9065.8188 | 145.4777 | 8920.341 | 33.8606 | 313.5196 | 303.1868 | 10.3328 | 3.408% | 3.989% | -0.5815% | 3.434% | -0.02645% | 3.296% | 315.9526 | -2.433
19 | 9600 | 48.7696 | 9551.2304 | 95.7873 | 9455.4431 | 149.7195 | 9305.7236 | 36.8496 | 331.126 | 316.3689 | 14.7571 | 3.449% | 4.163% | -0.7135% | 3.469% | -0.01973% | 3.296% | 333.0199 | -1.8939
20 | 10000 | 51.449 | 9948.551 | 103.9224 | 9844.6286 | 154.1346 | 9690.494 | 39.9599 | 349.4659 | 329.5509 | 19.915 | 3.495% | 4.336% | -0.8415% | 3.504% | -0.008988% | 3.296% | 350.3646 | -0.89877
21 | 10400 | 54.2378 | 10345.7622 | 112.3865 | 10233.3757 | 158.7226 | 10074.6531 | 43.1909 | 368.5378 | 342.7329 | 25.8049 | 3.544% | 4.51% | -0.966% | 3.538% | 0.005297% | 3.296% | 367.9869 | 0.55086
22 | 10800 | 57.1359 | 10742.8641 | 121.1796 | 10621.6845 | 163.4827 | 10458.2018 | 46.5421 | 388.3403 | 355.915 | 32.4253 | 3.596% | 4.683% | -1.087% | 3.573% | 0.02272% | 3.296% | 385.8868 | 2.4536
23 | 11200 | 60.1434 | 11139.8566 | 130.3012 | 11009.5554 | 168.4144 | 10841.141 | 50.0129 | 408.8719 | 369.097 | 39.7749 | 3.651% | 4.857% | -1.206% | 3.608% | 0.04293% | 3.296% | 404.0641 | 4.8079
24 | 11600 | 63.2602 | 11536.7398 | 139.7512 | 11396.9886 | 173.5171 | 11223.4715 | 53.6027 | 430.1312 | 382.279 | 47.8522 | 3.708% | 5.03% | -1.322% | 3.642% | 0.06562% | 3.296% | 422.5189 | 7.6123
25 | 12000 | 66.4864 | 11933.5136 | 149.5292 | 11783.9844 | 178.7903 | 11605.1941 | 57.3109 | 452.1168 | 395.4611 | 56.6557 | 3.768% | 5.203% | -1.436% | 3.677% | 0.09055% | 3.296% | 441.2513 | 10.8654
26 | 12400 | 69.822 | 12330.178 | 159.635 | 12170.543 | 184.2332 | 11986.3098 | 61.1369 | 474.827 | 408.6431 | 66.1839 | 3.829% | 5.377% | -1.548% | 3.712% | 0.1175% | 3.296% | 460.2612 | 14.5658
27 | 12800 | 73.267 | 12726.733 | 170.0682 | 12556.6648 | 189.8453 | 12366.8195 | 65.0801 | 498.2606 | 421.8251 | 76.4355 | 3.893% | 5.55% | -1.658% | 3.746% | 0.1462% | 3.296% | 479.5486 | 18.712
| % Losses at Peak = | 0.5724% |  | 1.336% |  | 1.512% |  | 0.5262%
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified

## 2) Loss Analysis
|  | CenterPoint Energy Distribution Loss Factor for 2016 Rev 2.xls | [13 empty] | With Scaling | Using F1, F2 & F3 Coefficients |  |  | With Scaling
ERCOT | ERCOT |  | CNP | CNP |  | PELCAR | Primary | Total | Total |  |  | 2015 | Secondary | 2015 | 2015 | 2015 | 2015 | 2015 | Total | 2015 | Adjustment for % Losses |  | 2008 | 2008
Load (15 min) | Load (1 hr) |  | Load (15 min) | Input To Sub Trfs | Sub Trf Losses | Input to Dist Sys | Conductor Losses | Primary Losses | Primary Loss % | Input to Dist Trfs | Dist Trf Losses | Input To Secondary | Conductor Losses | Total Losses | Total Losses | Total Losses | DLF | DLF | Primary Loss % | Primary Loss % | Sec | Pri | Primary MW Losses | Sec MW Losses
|  |  |  | (MW) | (MW) | (MW) | (MW) |  |  | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | Secondary | Primary
SIEL | [15 empty] | 0% |  |  |  | 0%
|  |  |  | 50 | 20.8674 | 29.1326 | 0.00096701 | 20.8684 | 41.74% | 29.1316 | 145.3904 | -116.2588 | 0.0047909 | 166.2636 | 332.5% | 332.5%
|  |  |  | 135 | 20.8702 | 114.1298 | 0.014841 | 20.8851 | 15.47% | 114.1149 | 145.3957 | -31.2808 | 0.00034683 | 166.2811 | 123.2% | 123.2%
|  |  |  | 500 | 20.9115 | 479.0885 | 0.26152 | 21.173 | 4.235% | 478.827 | 145.4899 | 333.3371 | 0.039385 | 166.7023 | 33.34% | 33.34%
1295.9583 | 5183.8331 |  | 250 | 1000 | 21.045 | 978.955 | 1.0919 | 22.1369 | 2.214% | 977.8631 | 145.8065 | 832.0566 | 0.2454 | 168.1888 | 16.82% | 16.82%
3110.2999 | 12441.1995 | 1 | 600 | 2400 | 21.8921 | 2378.1079 | 6.4437 | 28.3358 | 1.181% | 2371.6642 | 147.8402 | 2223.824 | 1.7529 | 177.929 | 7.414% | 7.414% | 6.917% | 0.687% | 1.181% | 1.181% |  |  | 28.3358 | 177.929
3628.6832 | 14514.7327 | 2 | 700 | 2800 | 22.2623 | 2777.7377 | 8.7913 | 31.0536 | 1.109% | 2768.9464 | 148.7299 | 2620.2165 | 2.4336 | 182.217 | 6.508% | 6.508% | 6.105% | 0.7053% | 1.109% | 1.109% |  |  | 31.0536 | 182.217
4147.0665 | 16588.266 | 3 | 800 | 3200 | 22.6894 | 3177.3106 | 11.5025 | 34.1919 | 1.068% | 3165.8081 | 149.7559 | 3016.0523 | 3.2244 | 187.1721 | 5.849% | 5.849% | 5.519% | 0.7346% | 1.068% | 1.068% |  |  | 34.1919 | 187.1721
4665.4498 | 18661.7992 | 4 | 900 | 3600 | 23.1734 | 3576.8266 | 14.577 | 37.7504 | 1.049% | 3562.2496 | 150.9178 | 3411.3318 | 4.1249 | 192.7931 | 5.355% | 5.355% | 5.083% | 0.7714% | 1.049% | 1.049% |  |  | 37.7504 | 192.7931
5183.8331 | 20735.3325 | 5 | 1000 | 4000 | 23.7145 | 3976.2855 | 18.0147 | 41.7292 | 1.043% | 3958.2708 | 152.2152 | 3806.0557 | 5.1347 | 199.0791 | 4.977% | 4.977% | 4.753% | 0.8133% | 1.043% | 1.043% |  |  | 41.7292 | 199.0791
5702.2164 | 22808.8657 | 6 | 1100 | 4400 | 24.3124 | 4375.6876 | 21.8155 | 46.1279 | 1.048% | 4353.8721 | 153.6476 | 4200.2245 | 6.2533 | 206.0288 | 4.682% | 4.682% | 4.499% | 0.859% | 1.048% | 1.048% |  |  | 46.1279 | 206.0288
6220.5997 | 24882.399 | 7 | 1200 | 4800 | 24.9673 | 4775.0327 | 25.9792 | 50.9465 | 1.061% | 4749.0535 | 155.2146 | 4593.8389 | 7.4803 | 213.6414 | 4.451% | 4.451% | 4.303% | 0.9075% | 1.061% | 1.061% |  |  | 50.9465 | 213.6414
6738.9831 | 26955.9322 | 8 | 1300 | 5200 | 25.6792 | 5174.3208 | 30.5056 | 56.1848 | 1.08% | 5143.8152 | 156.9158 | 4986.8994 | 8.8151 | 221.9157 | 4.268% | 4.268% | 4.151% | 0.9581% | 1.08% | 1.08% |  |  | 56.1848 | 221.9157
7257.3664 | 29029.4654 | 9 | 1400 | 5600 | 26.448 | 5573.552 | 35.3946 | 61.8426 | 1.104% | 5538.1574 | 158.7508 | 5379.4066 | 10.2574 | 230.8507 | 4.122% | 4.122% | 4.034% | 1.01% | 1.104% | 1.104% |  |  | 61.8426 | 230.8507
7775.7497 | 31102.9987 | 10 | 1500 | 6000 | 27.2738 | 5972.7262 | 40.646 | 67.9198 | 1.132% | 5932.0802 | 160.7191 | 5771.3612 | 11.8066 | 240.4454 | 4.007% | 4.007% | 3.945% | 1.064% | 1.132% | 1.132% |  |  | 67.9198 | 240.4454
8294.133 | 33176.5319 | 11 | 1600 | 6400 | 28.1565 | 6371.8435 | 46.2597 | 74.4162 | 1.163% | 6325.5838 | 162.8202 | 6162.7636 | 13.4623 | 250.6987 | 3.917% | 3.917% | 3.878% | 1.119% | 1.163% | 1.163% |  |  | 74.4162 | 250.6987
8812.5163 | 35250.0652 | 12 | 1700 | 6800 | 29.0961 | 6770.9039 | 52.2355 | 81.3316 | 1.196% | 6718.6684 | 165.0538 | 6553.6145 | 15.224 | 261.6095 | 3.847% | 3.847% | 3.83% | 1.175% | 1.196% | 1.196% |  |  | 81.3316 | 261.6095
9330.8996 | 37323.5984 | 13 | 1800 | 7200 | 30.0928 | 7169.9072 | 58.5733 | 88.666 | 1.231% | 7111.334 | 167.4195 | 6943.9145 | 17.0913 | 273.1768 | 3.794% | 3.794% | 3.798% | 1.231% | 1.231% | 1.231% | 0 | 0 | 88.666 | 273.1768
9849.2829 | 39397.1317 | 14 | 1900 | 7600 | 31.1463 | 7568.8537 | 65.2729 | 96.4192 | 1.269% | 7503.5808 | 169.9167 | 7333.6641 | 19.0638 | 285.3997 | 3.755% | 3.771% | 3.778% | 1.288% | 1.269% | 1.284% | 1 | 1 | 97.5845 | 286.5853
10367.6662 | 41470.6649 | 15 | 2000 | 8000 | 32.2568 | 7967.7432 | 72.3341 | 104.5909 | 1.307% | 7895.4091 | 172.5451 | 7722.864 | 21.1409 | 298.2769 | 3.728% | 3.76% | 3.77% | 1.346% | 1.307% | 1.338% | 2 | 2 | 107.0443 | 300.7729
10886.0495 | 43544.1982 | 16 | 2100 | 8400 | 33.4243 | 8366.5757 | 79.7568 | 113.1811 | 1.347% | 8286.8189 | 175.3042 | 8111.5147 | 23.3223 | 311.8076 | 3.712% | 3.759% | 3.771% | 1.404% | 1.347% | 1.393% | 3 | 3 | 117.0451 | 315.7388
11404.4329 | 45617.7314 | 17 | 2200 | 8800 | 34.6487 | 8765.3513 | 87.5409 | 122.1896 | 1.389% | 8677.8104 | 178.1937 | 8499.6167 | 25.6074 | 325.9907 | 3.704% | 3.767% | 3.781% | 1.463% | 1.389% | 1.45% | 4 | 4 | 127.5869 | 331.4819
11922.8162 | 47691.2647 | 18 | 2300 | 9200 | 35.93 | 9164.07 | 95.6862 | 131.6162 | 1.431% | 9068.3838 | 181.213 | 8887.1708 | 27.9959 | 340.8251 | 3.705% | 3.783% | 3.797% | 1.522% | 1.431% | 1.507% | 5 | 5 | 138.6696 | 348.0011
12441.1995 | 49764.7979 | 19 | 2400 | 9600 | 37.2683 | 9562.7317 | 104.1925 | 141.4608 | 1.474% | 9458.5392 | 184.3618 | 9274.1774 | 30.4872 | 356.3098 | 3.712% | 3.805% | 3.82% | 1.581% | 1.474% | 1.566% | 6 | 6 | 150.2928 | 365.2954
12959.5828 | 51838.3312 | 20 | 2500 | 10000 | 38.6636 | 9961.3364 | 113.0596 | 151.7232 | 1.517% | 9848.2768 | 187.6396 | 9660.6372 | 33.081 | 372.4438 | 3.724% | 3.834% | 3.848% | 1.64% | 1.517% | 1.625% | 7 | 7 | 162.4566 | 383.3638
13477.9661 | 53911.8644 | 21 | 2600 | 10400 | 40.1158 | 10359.8842 | 122.2875 | 162.4033 | 1.562% | 10237.5967 | 191.046 | 10046.5506 | 35.7768 | 389.2261 | 3.743% | 3.867% | 3.881% | 1.7% | 1.562% | 1.684% | 8 | 8 | 175.1607 | 402.2053
13996.3494 | 55985.3977 | 22 | 2700 | 10800 | 41.625 | 10758.375 | 131.876 | 173.501 | 1.606% | 10626.499 | 194.5806 | 10431.9184 | 38.5741 | 406.6557 | 3.765% | 3.906% | 3.919% | 1.76% | 1.606% | 1.744% | 9 | 9 | 188.405 | 421.8189
14514.7327 | 58058.9309 | 23 | 2800 | 11200 | 43.1911 | 11156.8089 | 141.8249 | 185.0159 | 1.652% | 11014.9841 | 198.243 | 10816.7411 | 41.4725 | 424.7314 | 3.792% | 3.948% | 3.96% | 1.82% | 1.652% | 1.805% | 10 | 10 | 202.1893 | 442.2034
15033.116 | 60132.4641 | 24 | 2900 | 11600 | 44.8141 | 11555.1859 | 152.134 | 196.9481 | 1.698% | 11403.0519 | 202.0327 | 11201.0192 | 44.4716 | 443.4524 | 3.823% | 3.994% | 4.005% | 1.881% | 1.698% | 1.866% | 11 | 11 | 216.5134 | 463.358
15551.4993 | 62205.9974 | 25 | 3000 | 12000 | 46.4941 | 11953.5059 | 162.8032 | 209.2973 | 1.744% | 11790.7027 | 205.9494 | 11584.7533 | 47.5708 | 462.8175 | 3.857% | 4.044% | 4.053% | 1.941% | 1.744% | 1.928% | 12 | 12 | 231.3773 | 485.2815
16069.8827 | 64279.5306 | 26 | 3100 | 12400 | 48.2311 | 12351.7689 | 173.8324 | 222.0635 | 1.791% | 12177.9365 | 209.9925 | 11967.944 | 50.7699 | 482.8259 | 3.894% | 4.097% | 4.104% | 2.002% | 1.791% | 1.99% | 13 | 13 | 246.7808 | 507.9731
16588.266 | 66353.0639 | 27 | 3200 | 12800 | 50.025 | 12749.975 | 185.2214 | 235.2463 | 1.838% | 12564.7537 | 214.1617 | 12350.592 | 54.0683 | 503.4764 | 3.933% | 4.152% | 4.157% | 2.062% | 1.838% | 2.053% | 14 | 14 | 262.7237 | 531.4316
17106.6493 | 68426.5971 | 28 | 3300 | 13200 | 51.8758 | 13148.1242 | 196.97 | 248.8458 | 1.885% | 12951.1542 | 218.4566 | 12732.6976 | 57.4656 | 524.768 | 3.976% | 4.21% | 4.213% | 2.123% | 1.885% | 2.115% | 15 | 15 | 279.2058 | 555.656
17625.0326 | 70500.1304 | 29 | 3400 | 13600 | 53.7836 | 13546.2164 | 209.078 | 262.8616 | 1.933% | 13337.1384 | 222.8767 | 13114.2616 | 60.9614 | 546.6998 | 4.02% | 4.269% | 4.27% | 2.184% | 1.933% | 2.178% | 16 | 16 | 296.227 | 580.6454
18143.4159 | 72573.6636 | 30 | 3500 | 14000 | 55.7483 | 13944.2517 | 221.5454 | 277.2938 | 1.981% | 13722.7062 | 227.4217 | 13495.2845 | 64.5552 | 569.2707 | 4.066% | 4.331% | 4.33% | 2.245% | 1.981% | 2.241% | 17 | 17 | 313.7871 | 606.3987
18661.7992 | 74647.1969 | 31 | 3600 | 14400 | 57.77 | 14342.23 | 234.372 | 292.1421 | 2.029% | 14107.8579 | 232.091 | 13875.7669 | 68.2466 | 592.4797 | 4.114% | 4.395% | 4.392% | 2.306% | 2.029% | 2.305% | 18 | 18 | 331.8861 | 632.9149
19180.1825 | 76720.7301 | 32 | 3700 | 14800 | 59.8487 | 14740.1513 | 247.5576 | 307.4063 | 2.077% | 14492.5937 | 236.8843 | 14255.7094 | 72.0352 | 616.3259 | 4.164% | 4.461% | 4.455% | 2.367% | 2.077% | 2.368% | 19 | 19 | 350.5236 | 660.1931
19698.5658 | 78794.2634 | 33 | 3800 | 15200 | 61.9843 | 15138.0157 | 261.1021 | 323.0863 | 2.126% | 14876.9137 | 241.8012 | 14635.1124 | 75.9206 | 640.8081 | 4.216% | 4.528% | 4.519% | 2.429% | 2.126% | 2.432% | 20 | 20 | 369.6997 | 688.2321
20216.9492 | 80867.7966 | 34 | 3900 | 15600 | 64.1768 | 15535.8232 | 275.0052 | 339.182 | 2.174% | 15260.818 | 246.8413 | 15013.9767 | 79.9022 | 665.9255 | 4.269% | 4.596% | 4.585% | 2.49% | 2.174% | 2.496% | 21 | 21 | 389.414 | 717.0311
20735.3325 | 82941.3299 | 35 | 4000 | 16000 | 66.4263 | 15933.5737 | 289.2669 | 355.6932 | 2.223% | 15644.3068 | 252.0041 | 15392.3027 | 83.9797 | 691.6771 | 4.323% | 4.666% | 4.652% | 2.551% | 2.223% | 2.56% | 22 | 22 | 409.6666 | 746.5891
21642.5033 | 86570.013 |  | 4175 | 16700 | 70.4999 | 16629.5001 | 315.0872 | 385.5872 | 2.309% | 16314.4128 | 261.3331 | 16053.0797 | 91.3448 | 738.2651 | 4.421% | 4.78% | 4.773% | 2.659% | 2.309% | 2.662% | 23 | 23
9940 | 39760 |  | 1917.5 | 7670 |  | 7670
15 min | ERCOT |  | 15 min | CNP |  | 7639 | AAL for CNP (7,639 MW) is measured at the Dist Fdr Bkr (PELCAR - Column G) so this value is increased 31 MW (Cell F24 ) for the high side of the sub trfs | [9 empty] | Secondary | Primary | CenterPoint Energy
9940 | 39760 | AAL | 1917.5 | 7670 | 31.3365 | 7638.6635 | 66.4825 | 97.819 | 1.275% | 7572.181 | 170.3672 | 7401.8138 | 19.4197 | 287.606 | 3.75% |  | 3.776% | 1.298% | At ERCOT AAL
17414 | 69656 | Peak | 3923.5 | 15694 | 64.7003 | 15629.2997 | 278.3245 | 343.0248 | 2.186% | 15350.9752 | 248.0435 | 15102.9316 | 80.8518 | 671.9202 | 4.281% |  | 4.247% | 2.159% | At ERCOT Peak
15694
[6 empty] | 15629 | Peak for CNP (15,629 MW) is measured at the Dist Fdr Bkr (PELCAR - Column G) so this value is increased 65 MW (Cell F44) for the high side of the sub trfs
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % Losses above AAL are scaled proportionately ---> | [14 empty] | Scaling for % Losses |  |  | 2016
(When ERCOT is at peak, CNP is 5 intervals below peak, so % losses at ERCOT peak are scaled up to match % losses at CNP peak.) | [14 empty] | Secondary | Primary |  | For Secondary Distribution Customers "D"
|  |  |  | Substation Transformers |  | Primary Conductor |  |  |  | Distribution Transformers |  | Secondary Conductor |  |  | 0.234% | 0.23% |  | Secondary Constants
|  |  |  | B Constant | A Constant | B Constant | A Constant |  |  | B Constant | A Constant | B Constant | A Constant
|  |  | 2015 Values ----> | 20.867 | 1.7797e-07 | 0 | 1.1394e-06 |  |  | 145.39 | 4.3561e-07 | 0 | 3.5446e-07 | <--- 2015 Values
|  |  | 2014 Values ----> | 19.863 | 1.893e-07 | 0 | 1.1394e-06 |  |  | 142.346 | 4.4856e-07 | 0 | 3.5446e-07 | <--- 2014 Values
|  |  | 2013 Values ----> | 19.473 | 1.9548e-07 | 0 | 1.1394e-06 |  |  | 137.751 | 4.7391e-07 | 0 | 3.5446e-07 | <--- 2013 Values
|  |  | 2012 Values ----> | 21.1118 | 1.8286e-07 | 0 | 1.1394e-06 |  |  | 133.986 | 5.0407e-07 | 0 | 3.5446e-07 | <--- 2012 Values
|  |  | 2009 Values ----> | 20.312 | 1.9194e-07 | 0 | 1.1394e-06 |  |  | 130.794 | 5.041e-07 | 0 | 3.5446e-07 | <--- 2009 Values
|  |  | 2008 Values ----> | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2008 Values |  |  | F1 = | 0.01756 | right
|  |  | 2007 Values ----> | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2007 Values |  |  | F2 = | 0.000402 | middle
[17 empty] | F3 = | 0.0198 | left
|  |  |  | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | <--- 1995 |  | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | <--- 1995
|  |  |  | 19.73 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2001 |  | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2001 |  |  |  | For Primary Distribution Customers "E"
|  |  |  | 20.2955 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2004/2006 |  | 133.2966 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2004/2006 |  |  |  | Primary Constants
|  |  |  | 2.866% increase in Sub Trf nameplate MVA from 2001 to 2004 | [5 empty] | 15.9% 1ncrease in distribution trf nameplate KVA from 2001 to 2004
|  |  | 2007 Start Values ----> | 18.586 | 2.13e-07 | 0 | 1.1116e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <---2007 Start Value |  |  | F1 = | 0.012 | right
|  |  |  | New values as per updated |  | Add 2.5 % to 2006 values due |  |  |  | New values as per updated | [6 empty] | F2 = | 1.5e-05 | middle
|  |  | 2007 Adjustments ----> | substation trf review. |  | to increased loading on circuits |  |  |  | distribution trf review. | [6 empty] | F3 = | 0.00097 | left
|  |  |  | Decrease from 2006 values. |  | as per revised Design Criteria |  |  |  | Decrease from 2006 values. |  | No change to 2006 values.
[11 empty] | AAL for ERCOT (15 mins) = 9,940 |  |  | DLF = F1 * (SIEL/AAL) + F2 + F3 / (SIEL/AAL)
(See graphs below and to the right)
2016
Secondary Constants
F1 = | 0.01756 | right
F2 = | 0.000402 | middle
F3 = | 0.0198 | left

## 3) Loss Equations
System Loss Equations For CenterPoint Energy for 2016 DLF
| Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
Substation Transformers
| 75.656 = | A * (17,546*17,546) + 20.867 |  |  |  |  | 75.656
| A = | 1.7797e-07 |  |  |  |  | 20.867
| B = | 20.867 | Total No-Load Losses For Substation Transformers = 20.867 MW |  |  |  | 54.789
Total Load Losses = 54.789 MW at 17,546 MW load level
[6 empty] | 2015 for use in 2016 | 17546
[5 empty] | No Load Losses | 20.867 | 17546
[5 empty] | Load Losses | 54.789 | 307862116
[5 empty] | Total | 75.656
1.7797e-07
Primary Conductor
| A = | 1.1394e-06
| B = | 0
Distribution Transformers
| 248.084 = | A * (15,354*15,354) + 145.390
| A = | 4.3561e-07 | Total Load Losses = 102.694 MW at 15,354 MW input to Dist Trfs
| B = | 145.39 | Total No-Load Losses For Distribution Transformers = 145.390 MW |  |  |  |  | 248.084
|  |  |  | 2015 | Corresponds to CNP load at Dist Bkrs of 15,629.00 MW (coincident peak) |  |  | 145.39
|  | No Load Losses |  | 145.39 | Corresponds to CNP load at high side of sub trfs of 15,964 MW |  |  | 102.694
|  | Load Losses |  | 102.694 | Corresponds to CNP load input to distribution service trfs of 15,354.00
|  | Total |  | 248.084 |  |  |  | 15354
15354
|  |  |  | Information from: DLF - 2015 Dist Trf Summary for DLF Calculation Rev 10 21 2015.xlsx |  |  |  | 235745316
Secondary Conductor | [7 empty] | 4.3561e-07
| A = | 3.5446e-07
| B = | 0

## Loss Analysis 2001 Mod (hidden)
HL&P Distribution Loss Analysis |  |  | 2001 Modified |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | 2800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | 3200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | 3600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | 4000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | 4400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | 4800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | 5200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | 5600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
10 | 6000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11 | 6400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | 6800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | 7200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
14 | 7600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | 8000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | 8400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
17 | 8800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | 9200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | 9600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
20 | 10000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
21 | 10400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
22 | 10800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
23 | 11200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
24 | 11600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 12000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
26 | 12400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
27 | 12800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| % Losses at Peak = | #REF! |  | #REF! |  | #REF! |  | #REF!
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified