ERCOT Nodal Operating Guides

Section 2:  System Operations and Control Requirements

January 1, 2016

2	System Operations and Control Requirements	2-1

2.1	Operational Duties	2-1

2.2	System Monitoring and Control	2-3

2.2.1	Overview	2-3

2.2.2	Security Criteria	2-4

2.2.3	Response to Transient Voltage Disturbance	2-5

2.2.4	Load Frequency Control	2-5

2.2.5	Automatic Voltage Regulators	2-6

2.2.6	Power System Stabilizers	2-6

2.2.7	Turbine Speed Governors	2-8

2.2.8	Performance/Disturbance/Compliance Analysis	2-9

2.2.9	Time Error and Time Synchronization	2-10

2.2.10	Generation Resource Response Time Requirements	2-10

2.3	Ancillary Services	2-12

2.3.1	Responsive Reserve	2-14

2.3.2	Non-Spinning Reserve Service	2-16

2.4	Outage Coordination	2-17

2.5	Reliability Unit Commitment	2-17

2.5.1	Criteria for Removing Contingencies from the Reliability Unit Commitment Analyses	2-17

2.6	Requirements for Under-Frequency and Over-Frequency Relaying	2-18

2.6.1	Automatic Firm Load Shedding	2-18

2.6.2	Generators	2-19

2.7	System Voltage Profile	2-20

2.7.1	Introduction	2-20

2.7.2	Maintaining Voltage Profile	2-20

2.7.3	Special Consideration for Nuclear Power Plants	2-22

2.7.4	Reactive Considerations for Generation Resources	2-22

2.8	Operation of Direct Current Ties	2-24

2.8.1	Inadvertent Energy Management	2-24

2.9	Voltage Ride-Through Requirements for Generation Resources	2-24

2.9.1	Additional Voltage Ride-Through Requirements for Intermittent Renewable Resources	2-26

# System Operations and Control Requirements

2.1	Operational Duties

The duties of ERCOT are described in relevant sections of the Protocols and North American Electric Reliability Corporation (NERC) Reliability Standards.  These Operating Guides assume that all actions taken will be on components of, or related to, the ERCOT System unless otherwise specified.  The primary operational duties of ERCOT are to ensure the reliability of the ERCOT System.  In doing this ERCOT shall:

(1)	Perform operational planning:

(a)	Perform the Reliability Unit Commitment (RUC) processes in order to commit additional resources as needed to maintain reliability;

(b)	Perform operational ERCOT Transmission Grid reliability studies, including those related to generation and load interconnection responsibilities;

(c)	Review all Outages of Generation Resources and major transmission lines or components to identify and correct possible failure to meet credible N-1 criteria. This shall include possible failure to meet N-1 criteria not resolved through the Day-Ahead process;

(d)	Perform load flows and security analyses of Outages submitted by Qualified Scheduling Entities (QSEs) or Transmission Service Providers (TSPs) as a basis for approval or rejection as described in Protocol Section 3.1, Outage Coordination;

(e)	Withdraw approval of a scheduled Outage if unable to meet credible N-1 criteria after all other reasonable options are exercised as described in Protocol Section 3.1;

(f)	Serve as the point of contact for initiation of generation interconnection to the ERCOT Transmission Grid;

(g)	Forecast Load and Resources for the next seven days for reliability planning; and

(h)	Ensure that sufficient Resources in the proper location and required Ancillary Services have been committed for all expected Load on a Day-Ahead and Real-Time basis.

(2)	Operate energy and Ancillary Service markets:

(a)	Administer a Congestion Revenue Rights (CRR) market;

(b)	Administer a Day-Ahead Market (DAM) including both energy and Ancillary Service;

(c)	Administer the RUC processes;

(d)	If necessary, administer a Supplemental Ancillary Service Market (SASM); and

(e)	Administer a Real-Time energy market using Security-Constrained Economic Dispatch (SCED).

(3)	Supervise the ERCOT System to meet NERC Reliability Standards:

(a)	Monitor and evaluate ERCOT System conditions on a continuous basis;

(b)	Coordinate with Transmission Operators (TOs), ERCOT System events to maintain or restore reliability;

(c)	Dispatch generation via the SCED process and deployment of Ancillary Services to control frequency and congestion;

(d)	Provide access to the ERCOT System on a nondiscriminatory basis;

(e)	Approve schedules of interchange transactions across the Direct Current Ties (DC Ties); and

(f)	Direct emergency operations.

(4)	Collect and Disseminate Information:

(a)	Collect, process, and disseminate market, operational and settlement information;

(b)	Provide relevant operational information to Market Participants over the Market Information System (MIS);

(c)	Collect and maintain operational data required by the Public Utility Commission of Texas (PUCT), NERC and Protocols;

(d)	Receive reports from TOs and QSEs and forward them to the Department of Energy (DOE), NERC, and/or other Governmental Authority as required;

(e)	Submit reports to DOE, NERC, and/or other Governmental Authority as required; and

(f)	Record and report accumulated time error.

2.2	System Monitoring and Control

2.2.1	Overview

(1)	ERCOT will maintain continuous surveillance of the status of operating conditions within ERCOT and act as a central information collection and dissemination point for Market Participants.

(2)	ERCOT is designated to receive information required to continually monitor the operating conditions of the ERCOT System and to order individual Qualified Scheduling Entities (QSEs) and/or Transmission Operators (TOs) to make changes to ensure ongoing security and reliability of ERCOT.

(3)	ERCOT shall maintain, monitor, and/or direct the following in accordance with the Protocols.  This includes but is not limited to:

(a)	Resources - Monitor, deploy, commit and gather data for settlement of Resources in order to maintain reliability and accurately settle energy capacity and Ancillary Service markets as described in the following Protocol Sections:

(i)	Protocol Section 3, Management Activities for the ERCOT System;

(ii)	Protocol Section 4, Day-Ahead Operations;

(iii)	Protocol Section 5, Transmission Security Analysis and Reliability Unit Commitment; and

(iv)	Protocol Section 6, Adjustment Period and Real-Time Operations.

(b)	ERCOT Transmission Grid:

(i)	Monitor line loading and power transfers;

(ii)	Coordinate Planned Outages;

(iii)	Monitor and detect Forced Outages;

(iv)	Perform contingency analyses and direct re-dispatch to maintain reliable operations;

(v)	Monitor and coordinate maintenance and construction schedules;

(vi)	Monitor and control voltage levels; and

(vii)	Monitor Reactive Power flows.

(c)	System Operation:

(i)	Monitor power flows with non-ERCOT systems;

(ii)	Maintain and monitor Ancillary Services plans and delivery;

(iii)	Maintain and document compliance with transmission security criteria;

(iv)	Monitor performance of providers of Ancillary Services;

(v)	Manage inadvertent energy account balances with non-ERCOT systems;

(vi)	Direct Time Error correction;

(vii)	Issue and direct Operating Condition Notices (OCNs), Advisories, Watches, and Emergency Notices; and

(viii)	Direct emergency and short supply operations.

(d)	Information Management:

(i)	Monitor and coordinate information for daily planning, hourly reporting and minute-by-minute operation;

(ii)	Validate the accuracy of the Real-Time data; and

(iii)	Operate the Market Information System (MIS), Energy Management System (EMS) and Market Management System (MMS) to disseminate Real-Time, hourly accounting, and operations plan data between ERCOT and each QSE and TO.

2.2.2	Security Criteria

(1)	Technical limits established for the operation of transmission equipment shall be applied consistently in planning and engineering studies, Congestion Revenue Rights (CRRs), Day-Ahead studies, Real-Time security analyses, and operator actions.

(2)	ERCOT shall operate the system such that pre-contingency flows are within applicable Transmission Facility Ratings.

(3)	ERCOT shall operate the system such that, unless an Emergency Condition has been declared by ERCOT, the occurrence of a Credible Single Contingency will not cause any of the following conditions:

(a)	Uncontrolled breakup of the ERCOT Transmission Grid;

(b)	Loading of Transmission Facilities above defined Emergency Ratings that cannot be eliminated in time to prevent damage or failure following the loss through execution of a Constraint Management Plan (CMP);

(c)	Transmission voltage levels outside system design limits that cannot be corrected through execution of a CMP before voltage instability or collapse occurs; or

(d)	Customer Outages, except for Load that is included in a CMP, high set interruptible and radially served Loads.

2.2.3	Response to Transient Voltage Disturbance

Generation Resources should be designed in accordance with Section 6.2, System Protective Relaying, in order to properly respond to transient voltage disturbances.

2.2.4	Load Frequency Control

(1)	ERCOT shall operate the Load Frequency Control (LFC) system to maintain the scheduled frequency at 60 Hz (correcting periodically for time error) and to minimize the use of energy from Resources providing Regulation Service.

(2)	The ERCOT LFC system shall deploy Regulation Service and Responsive Reserve (RRS) energy as necessary in accordance with Protocol Section 6.5.7.6, Load Frequency Control, to meet North American Electric Reliability Corporation (NERC) Reliability Standards.  ERCOT shall purchase Regulation Service to provide satisfactory frequency control performance for the ERCOT Region.  ERCOT shall determine the satisfactory amount of Regulation Service, required by statistical analysis of possible Resource Outages and Load forecast error, to expect operation of 95% of hours without deploying RRS.

(3)	QSEs shall use Automatic Generation Control (AGC) to direct the output of generation facilities providing Regulation and RRS.

2.2.4.1	Maintenance and Verification

Each provider of Regulation and/or Responsive Reserve Services will properly maintain AGC equipment.  Performance of AGC will be verified by the results of performance metrics for Ancillary Service providers described in the Protocols.  ERCOT will initiate a regulation survey to evaluate the performance of all AGC equipment in the ERCOT Region.

2.2.4.2	Regulation Provider Loss of AGC

If a QSE providing Regulation Services or Responsive Reserve Services loses its AGC for any reason, it will notify ERCOT as soon as practicable of the reason for and estimated duration of the loss.  ERCOT will assess whether additional action should be taken to maintain system frequency.  Possible ERCOT actions include opening a Supplemental Ancillary Service Market (SASM) per Protocol Section 6.4.8.2, Supplemental Ancillary Service Market, for the period of anticipated loss.

2.2.4.3	ERCOT Loss of AGC

(1)	ERCOT has back-up facilities in place for loss of control systems.  In the event that these backup facilities also fail to perform, ERCOT shall direct a QSE providing regulation to implement Constant Frequency Control (CFC) for the duration of the control loss.  ERCOT will direct the QSE providing CFC to enter the appropriate bias into their control system.  If a QSE on CFC develops a problem with regulating room, ERCOT will order additional regulation energy from another QSE to create regulation room.

(2)	ERCOT shall conduct unannounced testing to verify a QSE’s capability to operate in CFC mode.  Only QSEs with at least 350 MW of spinning reserve room will be tested.  QSEs shall be tested at least once every three years.  At a time determined solely by ERCOT, ERCOT will direct the QSE to operate under CFC mode. Once instructed by ERCOT, the QSE will have five minutes to switch to CFC mode.  The duration of this test shall be no more than 15 minutes.  ERCOT shall maintain the list of QSEs that have successfully demonstrated their capability to operate in CFC mode.

2.2.5	Automatic Voltage Regulators

(1)	Generation Entities shall notify their QSEs of any change in Automatic Voltage Regulator (AVR) status (e.g. AVR unavailability due to maintenance or failure and when the AVR returns to normal operation).  QSEs shall notify ERCOT and the TO at the Point of Interconnection (POI) of any change in AVR status and shall supply AVR status logs to ERCOT upon request per Protocol Section 6.5.5.1, Changes in Resource Status.

(2)	Generation Entities shall conduct performance tests on AVRs or verify AVR performance through comparison with operational data a minimum of every five years as prescribed in item (5) of Protocol Section 8.1.1.2.1.4, Voltage Support Service (VSS) Qualification, or if equipment characteristics are knowingly modified, within 30 days of the modification.  The test reports should include the minimum and maximum excitation limiters, volts/hertz settings, gain and time constants, type of voltage regulator control function, date tested, and voltage regulator control setting.

(3)	Generation Resources shall verify excitation systems model data upon initial installation, within 30 days of performance modifications, and a minimum of five years thereafter.

(4)	Generation Resource AVR modeling information required in the ERCOT Planning Criteria shall be determined from actual Generation Resource testing described in these Operating Guides.  Within 30 days of ERCOT’s request, the results of the latest test performed shall be supplied to ERCOT and the Transmission Service Provider (TSP).

2.2.6	Power System Stabilizers

(1)	Generation Resources with Power System Stabilizers (PSSs) shall keep their PSSs in-service (“On” or energized and performing as designed by the manufacturer) unless the PSS is installed but not in service as described in paragraph (4)(a)(ii) below.  When available, the PSS shall be active and responsive at all times the generator is synchronized to the ERCOT Transmission Grid and operating at or above its Low Sustained Limit (LSL).  However, if the PSS of a Generation Resource is set to be active and responsive at a point above the LSL for technical reasons, the Generation Resource may request ERCOT to allow an exception to the requirement that the PSS be active anytime the Generation Resource is at or above its LSL.  In order to obtain the exception, the Generation Resource shall notify ERCOT and provide the necessary technical information to ERCOT to justify a higher activation point for the PSS.

(2)	Generation Entities shall notify their QSEs of any change in PSS status (e.g. PSS unavailability due to maintenance or failure and when the PSS returns to normal operation).  QSEs shall notify ERCOT and the TO at the POI of any change in PSS status and shall supply PSS status logs to ERCOT upon request per Protocol Section 6.5.5.1, Changes in Resource Status.

(3)	Synchronous Generation Resources greater than 10 MW installed after January 1, 2008 and on or before December 1, 2010 shall install a PSS and place the PSS in service by June 1, 2011.  Synchronous Generation Resources greater than 10 MW installed after December 1, 2010 shall install a PSS and place the PSS in-service prior to the Resource Commissioning Date of the Generation Resource.  The Generation Resource shall establish PSS settings to dampen modes with oscillations within the range of 0.2 Hz to 2 Hz.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

(4)	Synchronous Generation Resources greater than 10 MW installed before January 1, 2008 are subject to the following requirements:

(a)	All Generation Resources that are in this category shall notify ERCOT and the TSP:

(i)	Whether or not a PSS has been installed; and

(ii)	Whether or not PSS settings have been determined and the PSS has been or will be placed in-service.

(b)	If a PSS was in-service prior to January 1, 2008, the PSS shall remain in-service with the established PSS settings, provided that ERCOT may direct the Generation Resource to modify the settings.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.

(c)	If a PSS is newly installed and/or placed in-service the Generation Resource shall establish PSS settings to dampen modes with oscillations within the range of 0.2 Hz to 2 Hz.  The PSS settings shall be tested and tuned to ensure the PSS has appropriate damping characteristics.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

(5)	If an excitation system on a synchronous Generation Resource greater than 10 MW is modified or replaced after January 1, 2008, the Generation Resource shall install a PSS, establish PSS settings to dampen modes with oscillations within the range of 0.2 Hz to 2 Hz, and place the PSS in-service.  The settings shall be tested and tuned to ensure the excitation system has appropriate damping characteristics.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

(6)	If it is determined that a change in PSS settings or the addition of a PSS to a synchronous Generation Resource would improve overall system performance, ERCOT shall coordinate with the Generation Resource owner to determine appropriate settings.  Within 180 days of determining appropriate settings, the Generation Resource owner shall revise the PSS setting and/or install the PSS.  Any PSS setting established pursuant to this section shall be established to dampen modes with oscillations as directed by ERCOT and place the PSS in-service.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

(7)	At least every five years, Generation Entities shall conduct performance tests on PSS settings or verify PSS performance based on operational data.  If PSS equipment characteristics are modified, the Generation Entity shall conduct a performance test within 30 days of the modification.  Final PSS settings shall be provided to ERCOT and the TSP within 30 days of the PSS in-service date.

(8)	The results of PSS tests or PSS performance verification shall be supplied to ERCOT and the TSP within 30 days of a request from ERCOT.

2.2.7	Turbine Speed Governors

(1)	A Governor shall be in-service whenever the Generation Resource is providing energy to the ERCOT Transmission Grid.

(2)	Resource Entities shall conduct Governor performance tests for each Generation Resource or Wind-powered Generation Resource (WGR) at least every two years using one of the test methods or historical methods specified in Section 8, Attachment C, Turbine Governor Speed Tests.  The Resource Entity shall then provide test results to ERCOT.

(3)	Every effort should be made to maintain Primary Frequency Response.  Maintenance tests on Governors shall demonstrate calibration for operation consistent with a generator droop characteristic of no greater than 5% but no less than 2% and Governor Dead-Band no greater than +/- 0.036 Hz.

(4)	There are elements that can contribute to poor Primary Frequency Response.  These include:

(a)	Governor Dead-Band in excess of +/- 0.036 Hz (measured from 60 Hz);

(b)	Valve position limits;

(c)	Blocked Governor operation;

(d)	Control mode;

(e)	Adjustable rates or limits;

(f)	Boiler/turbine coordinated control or set point control action; and

(g)	Automated “reset” or similar control action of the turbine’s MW set point.

(5)	Every attempt should be made to minimize the effects of the elements listed in item (4) above on the Governor operation for the duration of all frequency deviations.  Each Resource Entity should monitor its Generation Resources to verify these elements do not contribute to a Governor droop characteristic of no greater than 5% but no less than 2%.

(6)	If ERCOT determines that ERCOT System reliability would be enhanced, for a defined period of time, ERCOT may direct WGRs under the control of a Special Protection System (SPS) to limit power increases due to frequency if there is risk of an SPS operation due to a low frequency event.

2.2.8	Performance/Disturbance/Compliance Analysis

(1)	Performance/Disturbance/Compliance analysis shall be performed by ERCOT for the purpose of ensuring conformance with the Protocols.  All Generation Resources and Controllable Load Resources, except nuclear-powered Resources or WGRs with a permanent exemption approved by ERCOT, must respond to frequency disturbances with a Governor droop of 5% or less.  When assessing conformance with the Protocols, ERCOT shall exclude from the performance analysis the following instances of a Generation Resource or Controllable Load Resource:

(a)	Operating within the larger of five MW or 2% of the High Sustained Limit (HSL) for low frequency disturbances;

(b)	Operating within the larger of five MW or 2% of the LSL for high frequency disturbances;

(c)	Carrying spinning capability only comprised of non-frequency responsive power augmentation equipment, for low frequency disturbances; or

(d)	Having a technical or physical limitation filed with the ERCOT client representative and approved by ERCOT.

(2)	ERCOT will, on an as needed basis, utilize the Performance, Disturbance, Compliance Working Group (PDCWG) as a technical resource in providing input for types of technical or physical limitations that may be approved by ERCOT.

(3)	ERCOT shall make a regular report on selected system disturbances, documenting the response of individual Generation Resources and Controllable Load Resources.  In addition, Resource Entities, QSEs, and individual members of the PDCWG are encouraged to work within their respective companies to enhance the performance of individual Generation Resource’s or Controllable Load Resource’s control systems through application of the results of the PDCWG studies.

2.2.9	Time Error and Time Synchronization

2.2.9.1	Time Error

Sustained frequency deviations from scheduled frequency result in Time Error.  Time Error will be monitored and controlled in ERCOT as follows:

(a)	Time Error Monitoring - ERCOT will monitor accumulated Time Error and initiate time corrections.  The instantaneous Time Error is available to all QSEs on the MIS Public Area.

(b)	Time Error Correction - ERCOT may conduct Time Error correction at any time.  However, ERCOT must promptly initiate Time Error correction if the Time Error exceeds +/- 30 seconds, unless operational circumstances require otherwise.  ERCOT will initiate and terminate Time Error correction via hotline call to all QSEs.  The call initiating Time Error correction will include the frequency offset (- 0.02 Hz for fast and + 0.02 Hz for slow) and the start time.  The Time Error correction may end when:

(i)	The Time Error is within +/- 0.5 seconds of the target reference;

(ii)	System events mandate termination;

(iii)	The period of correction reaches five hours; or

(iv)	After any hour without at least a 0.5 second error reduction.

2.2.9.2	Time Synchronization

To promote accurate data reporting during an Energy Emergency Alert (EEA) and other system events, and to ensure transaction schedules are simultaneous, all QSEs and TOs, and ERCOT will maintain their control system time within ±3 seconds of the National Bureau of Standards (NBS) time signal.  The NBS time signal shall set the time standard for ERCOT.  ERCOT, QSEs and TOs are required to employ clocks, voice and data recording systems that synchronize automatically with the NBS on at least a weekly basis.

2.2.10	Generation Resource Response Time Requirements

(1) 	All Generation Resources providing VSS as described in Protocol Section 3.15, Voltage Support, shall maintain the necessary procedures and processes plus communications, telemetry, remote control, automation, and staffing in order to normally comply with the response times listed below when a VSS Dispatch Instruction as described in Protocol Section 6.5.7.7, Voltage Support Service, is given to the Generation Resource or the QSE representing a Generation Resource.  Compliance is based upon normal operating conditions where VSS Dispatch Instructions respect all equipment operating limits and other restrictions that are periodically placed on equipment.  The response time to a Dispatch Instruction shall commence with the successful receipt by the appropriate Entity.

(2)	In a Force Majeure Event, compliance with VSS Dispatch Instructions shall not be required.  TSPs and QSEs shall follow Dispatch Instructions for VSS except under those exemptions described in paragraphs (1) and (2) of Protocol Section 6.5.7.9, Compliance with Dispatch Instructions.

(3)	The required VSS response times for Generation Resources are:

(a)	For automatically switchable static VAR capable devices, when voltage or reactive measurements at the point of interconnection are outside of the limits as specified in paragraph (d) of Protocol Section 3.15.2, TSP and DSP Responsibilities Related to Voltage Support; then the response (within the operating Reactive Power capability of the Generation Resource) must be sufficient to initiate response in no more than one minute and return the measurement within the required range in no more than five minutes.

(b)	Response to a VSS Dispatch Instructions from ERCOT or authorized VSS Dispatch Instructions from a TSP, within the Reactive Power capability of the Generation Resource shall be completed in no more than five minutes of the receipt of a Dispatch Instruction.

(4) 	Shutting down and disconnecting Generation Resources from the ERCOT Transmission Grid:

(a)	On-Line Generation Resources must be able to commence their shutdown sequence within five minutes of receipt of a Dispatch Instruction from ERCOT.  Nuclear-fueled Generation Resources shall comply with the procedural requirements of the Nuclear Regulatory Commission (NRC) when receiving Dispatch Instructions from ERCOT to disconnect the Generation Resource from the ERCOT Transmission Grid.

(b)	If the ERCOT Transmission Grid condition requires breaker or switch operations needed to disconnect a non-MW producing generator  from the system shall be completed as soon as practical, but no longer than 15 minutes of the receipt of a Dispatch Instruction from ERCOT.  Once disconnected from the ERCOT Transmission Grid, a Generation Resource shall complete as soon as practical, but no longer than 15 minutes, the required switching to return the system to a normal configuration except for nuclear-fueled Generation Resources which shall comply with the procedural requirements of the NRC when receiving Dispatch Instructions from ERCOT to disconnect the Generation Resource from the ERCOT Transmission Grid.

2.3	Ancillary Services

The types of Ancillary Services required by ERCOT are described below:

| ANCILLARY SERVICE TYPE | DESCRIPTION | ERCOT AUTHORITY ACTION |
| --- | --- | --- |
| Regulation Down Service (Reg-Down) and Regulation Up Service (Reg-Up) (for Generation Resources) Reference: Protocol Section 2, Definitions and Acronyms | Resource capacity provided by a Qualified Scheduling Entity (QSE) from a specific Generation Resource to control frequency within the system which is controlled second by second, normally by an Automatic Generation Control (AGC) system. | - a. Reg-Down energy is a deployment to increase or decrease generation at a level below the Generation Resource’s Base Point in response to a change in system frequency. - b. Reg-Up energy is a deployment to increase or decrease generation at a level above the Generation Resource’s Base Point in response to a change in system frequency. |
| Reg-Down and Reg-Up (for Load Resource) Reference: Protocol Section 2, Definitions and Acronyms | Load Resource capacity provided by a QSE from a specific Load Resource to control frequency within the system. | - a. Reg-Down is a deployment to increase or decrease Load as deployed within its Ancillary Service Schedule for Reg-Down below the Load Resource’s Maximum Power Consumption (MPC) limit in response to a change in system frequency. - b. Reg-Up is a deployment to increase or decrease Load as deployed within its Ancillary Service Schedule for Reg-Up above the Load Resource’s Low Power Consumption (LPC) limit in response to a change in system frequency. |
| Responsive Reserve (RRS) Service Reference: Protocol Section 2, Definitions and Acronyms | Operating reserves on Generation Resources and Load Resources maintained by ERCOT to help control the frequency of the system. RRS on Generation Resources and Controllable Load Resources that are qualified to provide Regulation Service can also be used as a backup Regulation Service and energy during an Energy Emergency Alert (EEA) event. | RRS may only be deployed as follows: - a. Through automatic governor action or under-frequency relay in response to frequency deviations; - b. By electronic signal from ERCOT in response to the need; and - c. As ordered by an ERCOT Operator during EEA or other emergencies. |
| Non-Spinning Reserve (Non-Spin) Service Reference: Protocol Section 2, Definitions and Acronyms | - a. Off-Line Generation Resource capacity, or reserved capacity from On-Line Generation Resources, capable of being ramped to a specified output level within 30 minutes, and operating at a specified output for at least one hour - b. Controllable Load Resources that are capable of ramping to an ERCOT-instructed consumption level within 30 minutes consuming at the ERCOT-instructed level for at least one hour. | Deployed in response to loss-of-Resource contingencies, Load forecasting error, or other contingency events on the system. See Protocol Section 6.5.7.6.2.3, Non-Spinning Reserve Service Deployment. |
| Voltage Support Service (VSS) Reference: Protocol Section 3.15, Voltage Support | Reactive capability of a Generation Resource that is required to maintain transmission and distribution voltages on the ERCOT Transmission Grid within acceptable limits. All Generation Resources with a gross rating greater than 20 MVA shall provide VSS. | Direct the scheduling of VSS by providing Voltage Profiles at the point of interconnection. The Generation Resource is obligated to maintain the published voltage profile within its Corrected Unit Reactive Limit (CURL). |
| Black Start Service (BSS) Reference: Protocol Section 3.14.2, Black Start | The provision of Generation Resources under a Black Start Agreement, which are capable of self-starting without support from within ERCOT in the event of a Partial Blackout or Blackout. | Provide emergency Dispatch Instructions to begin restoration to a secure operating state after a Partial Blackout or Blackout. |
| Reliability Must-Run (RMR) Service Reference: Protocol Section 3.14.1, Reliability Must Run | The provision of Generation Resource capacity and energy under an RMR Agreement. | Enter into contractual agreements to retain units required for reliable operations. Direct the operation of those units that otherwise would not operate and that are necessary to provide reliable operations. |

2.3.1	Responsive Reserve

2.3.1.1	Obligation

ERCOT operating reserve requirements are more restrictive than North American Electric Reliability Corporation (NERC) Reliability Standards.  The RRS obligation is a minimum of 2300 MW.  The amount of RRS procured may be adjusted as described in ERCOT Methodologies for Determining Ancillary Service Requirements or if ERCOT determines a reliability need for additional Ancillary Service Resources.

2.3.1.2	Additional Operational Details for Responsive Reserve Providers

(1)	ERCOT shall specify the minimum amount of RRS provided by Generation Resources.  QSE’s Generation Resources providing RRS must be On-Line and capable of ramping to the awarded output level within ten minutes of the notice to deploy energy, must be immediately responsive to system frequency, and must be able to maintain the scheduled level for the period of service commitment.

(2)	RRS provided by a QSE shall meet the requirements as defined in item (3) of Protocol Section 3.18, Resource Limits in Providing Ancillary Service.

(3)	ERCOT shall issue a Verbal Dispatch Instruction (VDI) to QSEs of hydro Generation Resources operating in synchronous condenser fast-response mode who provide MWs to the ERCOT System in response to a frequency event occurring at or below the frequency set point specified in paragraph (3)(b) of Protocol Section 3.18 when the energy is provided without an RRS deployment.  The VDI shall be in the quantity of MWs (energy) supplied by the hydro Generation Resource responding in synchronous condenser fast-response mode and shall relieve the QSE of its obligation for the equivalent RRS obligation quantity.  If ERCOT issues an RRS deployment to the QSE responding with hydro Generation Resources operating in synchronous condenser fast-response mode, ERCOT shall count the responding hydro Generation Resource(s) MWs (energy) as part of its response to the RRS deployment.

(4)	Unless ERCOT issues a recall instruction for the RRS deployed via Inter-Control Center Communications Protocol (ICCP), the hydro Generation Resource(s) QSE may contact ERCOT to determine if it is allowed to recall and reset the individual unit(s) to the synchronous condenser fast-response mode.

(5)	ERCOT, at its sole discretion, may request that the hydro Generation Resource(s) remain On-Line and generating after an initial deployment.  The request to remain On-Line and generating after an initial deployment may not exceed 30 minutes per deployment for each frequency deviation or event nor shall such request exceed two hours per a consecutive 12-hour period in aggregate unless ERCOT has declared an EEA.

(6)	Load Resources providing RRS must be either a Controllable Load Resource qualified for Security-Constrained Economic Dispatch (SCED) and capable of providing Primary Frequency Response or a Load Resource controlled by high-set under-frequency relays for automatic interruption.  For eligibility to participate as a RRS provider, reference Protocol Section 8.1.1.2.1.2, Responsive Reserve Service Qualification.  Load Resources controlled by high-set under-frequency relays shall also complete the following requirements:

(a)	The under-frequency relay must have a delay of no more than 20 cycles (or 0.33 seconds for relays that do not count cycles).  Total time from the time frequency first decays to a value low enough to initiate action of the under frequency relay(s) to the time Load is interrupted should be no more than 30 cycles, including all relay and breaker operating times;

(b)	The initiation setting of the under-frequency relay shall not be any lower than 59.7 Hz; and

(c)	The Load Resource must be able to remain interrupted during actual event until replaced by other net dependable capability.  In no case may interrupted Load be restored to service without the approval of an ERCOT operator.

(7)	To become and remain fully qualified as a provider of RRS, the Load Resource shall complete the requirements above and the following:

(a)	Pass simulated or actual testing according to ERCOT procedures; and

(b)	Perform verification testing as described in Section 8, Attachment G, Load Resource Tests.

(8)	A Direct Current Tie (DC Tie) may be used as RRS up to 30 MW subject to the following constraints:

(a)	The tie shall respond with increased deliveries to ERCOT or decreased deliveries from ERCOT at a frequency of 59.9 Hz;

(b)	The response rate will not be less than 30 MW per minute;

(c)	The response delay will not exceed four seconds;

(d)	The response will be retained until frequency has recovered to a level at or above 60.00 Hz or as directed by ERCOT;

(e)	A QSE claiming DC Tie RRS must demonstrate the existence of contracts agreeing to provide the required response with the DC Tie operator; and

(f)	A QSE claiming DC Tie RRS must have an agreement with the balancing authority on the opposite side of the DC Tie involved approving the amount and conditions.

(9)	Hydro Unit(s) – Modes of RRS that will be counted:

(a)	Synchronous condenser fast response mode - described in item (3) of Protocol Section 3.18;

(b)	Generation MW mode - For any hydro Generation Resource with a 5% droop setting operating as a generator, the amount of RRS provided may never be more than 24% of the High Sustained Limit (HSL);

(c)	Synchronous Condenser Mode in “Manual” Dispatch Mode - Units will supply MWs based on operator action within the ten-minute Protocol requirement for supplying RRS.  Once deployed these units are frequency responsive; and

(d)	A Real-Time signal of the MW capacity of hydro units being operated in any of the synchronous condenser modes is telemetered to ERCOT.

2.3.2	Non-Spinning Reserve Service

2.3.2.1	Additional Operational Details for Non-Spinning Reserve Service Providers

(1)	Non-Spin Service Generation Resource providers must be capable of being synchronized and ramped to a specified output level within 30 minutes of notification of deployment and run at a specified output level for at least one hour, as specified in item (1)(a) of Protocol Section 3.17.3, Non-Spinning Reserve Service.

(2)	Non-Spin Controllable Load Resource providers must be capable of ramping to an ERCOT-instructed consumption level within 30 minutes and consuming at the ERCOT-instructed level for at least one hour, as specified in item (1)(b) of Protocol Section 3.17.3.

(3)	To become provisionally qualified as a provider of Non-Spin, a Controllable Load Resource shall complete the following requirements:

(a)	Register as a Controllable Load Resource with ERCOT;

(b)	Complete asset registration of the Controllable Load Resource;

(c)	Provide ERCOT the appropriate Non-Spinning Load affidavit;

(d)	Test to verify appropriate voice communications are in place for VDIs by ERCOT;

(e)	Provide telemetry through the QSE to ERCOT in accordance with all applicable requirements set forth in paragraph (5) of Protocol Section 6.5.5.2, Operational Data Requirements; and

(f)	Be able to consume at an ERCOT-instructed level during an ERCOT deployment for a minimum of one hour up to a maximum of the hours of service responsibility.

(4)	To become and remain fully qualified as a provider of Non-Spin, the Controllable Load Resource shall complete all the requirements for provisional qualification identified above and the following:

(a)	Respond successfully to an actual ERCOT deployment or pass simulated or actual testing according to ERCOT’s Procedure; and

(b)	Perform verification testing as described in Section 8, Attachment G, Load Resource Tests.

2.4	Outage Coordination

For Outage coordination details, reference Protocol Section 3.1, Outage Coordination and the ERCOT Market Information System (MIS) Secure Area.

2.5	Reliability Unit Commitment

2.5.1	Criteria for Removing Contingencies from the Reliability Unit Commitment Analyses

ERCOT shall remove contingencies from the Reliability Unit Commitment (RUC) analysis when:

(a)	The contingency is known to produce post-contingency results that are incorrect; or

(b)	The contingency is known to produce a non-convergent contingency result which may cause the RUC process to fail.

2.6	Requirements for Under-Frequency and Over-Frequency Relaying

2.6.1	Automatic Firm Load Shedding

(1)	At least 25% of the ERCOT System Load that is not equipped with high-set under-frequency relays shall be equipped at all times with provisions for automatic under-frequency load shedding.  The under-frequency relays shall be set to provide Load relief as follows:

| Frequency Threshold | Load Relief |
| --- | --- |
| 59.3 Hz | 5% of the ERCOT System Load (Total 5%) |
| 58.9 Hz | An additional 10% of the ERCOT System Load (Total 15%) |
| 58.5 Hz | An additional 10% of the ERCOT System Load (Total 25%) |

(2)	With the assistance of applicable Transmission Service Providers (TSPs), ERCOT will, prior to the peak each year, survey each Distribution Service Provider’s (DSP’s) compliance with the automatic Load shedding steps above, and report its findings to the Technical Advisory Committee (TAC).  For minimum compliance, DSPs are obligated to meet the prescribed percent values at all times.  It is not permitted to use rounding to meet the minimum.  ERCOT will direct a review of the automatic firm Load shedding program whenever warranted by conditions.  At a minimum, this review will follow the Reliability and Operations Subcommittee (ROS) directed dynamic simulations of automatic firm Load shedding conducted at five-year intervals beginning in the Summer of 2001.

(3)	Additional under-frequency relays may be installed on Transmission Facilities with the approval of ERCOT provided the relays are set at 58.0 cycles or below, are not directional, and have at least 2.0 seconds time delay.  A DSP may by mutual agreement arrange to have all or part of its automatic Load shedding requirement performed by another entity.  ERCOT will be notified and provided with the details of any such arrangement prior to implementation.

(4)	DSPs shall ensure, to the extent possible, and under the direction of ERCOT, that Loads equipped with under-frequency relays are dispersed geographically throughout the ERCOT Region to minimize the impact of Load shedding within a given geographical area.  Customers equipped with under-frequency relays shall be dispersed without regard to which Load Serving Entity (LSE) serves the customer.  DSPs shall ensure that the under-frequency relays connected to each Load will operate with a fixed time delay of no more than 30 cycles.  Total time from the time when frequency first reaches one of the values specified above to the time Load is interrupted should be no more than 40 cycles, including all relay and breaker operating times.  If the frequency drops below 58.5 Hz, ERCOT shall determine additional steps to continue operation.

(5)	If a loss of Load occurs due to the operation of under-frequency relays, a Transmission Operator (TO) designated by a DSP to shed Load may rotate the physical Load interrupted to minimize the duration of interruption experienced by individual Customers or to restore the availability of under-frequency Load-shedding capability.  In no event shall the initial total amount of Load without service be decreased by a TO without the approval of ERCOT.  TOs, in coordination with DSPs, shall make every reasonable attempt to restore Load, either by automatic or manual means, to preserve system integrity.  Restoration of any Load shed by Under-Frequency Load Shedding (UFLS) systems shall be coordinated with ERCOT.

(6)	Whenever possible, TOs and DSPs shall not manually drop Load connected to under-frequency relays during the implementation of Level 3 of an Energy Emergency Alert (EEA).

2.6.2	Generators

(1)	If under-frequency relays are installed and activated to trip the unit, these relays shall be set such that the automatic removal of individual Generation Resources from the ERCOT System meets the following requirements:

| Frequency Range | Delay to Trip |
| --- | --- |
| Above 59.4 Hz | No automatic tripping (Continuous operation) |
| Above 58.4 Hz up to And including 59.4 Hz | Not less than 9 minutes |
| Above 58.0 Hz up to And including 58.4 Hz | Not less than 30 seconds |
| Above 57.5 Hz up to And including 58.0 Hz | Not less than 2 seconds |
| 57.5 Hz or below | No time delay required |

(2)	If over-frequency relays are installed and activated to trip the unit, they shall be set such that the automatic removal of individual Generation Resources from the ERCOT System meets the following requirements:

This Operating Guide is not intended to conflict with the plant operator’s responsibility to protect Generation Resources from potentially damaging operating conditions.

| Frequency Range | Delay to Trip |
| --- | --- |
| Below 60.6 Hz down to and including 60 Hz | No automatic tripping (Continuous operation) |
| Below 61.6 Hz down to and including 60.6 Hz | Not less than 9 minutes |
| Below 61.8 Hz down to and including 61.6 Hz | Not less than 30 seconds |
| 61.8 Hz or above | No time delay required |

(3)	The Resource Entity that owns Generation Resources that are unable to comply shall provide to ERCOT an explanation of the limitations including, but not limited to, study results or manufacturer’s advice.

2.7	System Voltage Profile

2.7.1	Introduction

(1)	The system Voltage Profile is a predetermined distribution of desired voltage set points across the ERCOT Region.

(2)	ERCOT shall coordinate and conduct studies with the Transmission Service Providers (TSPs) to determine the normally desired Voltage Profile for all Generation Resource busses in the ERCOT Region as specified in item (1) of Protocol Section 3.15, Voltage Support, as published on the Market Information System (MIS) Secure Area.

(3)	ERCOT shall establish and update Voltage Profiles at points of interconnection of Generation Resources to maintain system voltages within established limits.

2.7.2	Maintaining Voltage Profile

ERCOT has the responsibility for monitoring and controlling the Voltage Profile and should use the following:

(a)	Operations Engineering

(i)	All voltage limits must be based on sound engineering studies that use the appropriate Network Operations Model.  TSP study results should be made available to ERCOT; and

(ii)	Transfer limits shall reflect voltage and/or reactive restrictions.

(b)	Coordination

(i)	Entities must coordinate high voltage limits in order to guarantee that the maximum continuous over-voltage of equipment is not exceeded.  Transmission Operators (TOs) shall notify ERCOT of normal operating voltage limits and post-contingency voltage limits for each bus;

(ii)	Low voltage limits must be coordinated in order to prevent one Entity from being a burden to another;

(iii)	Voltage limits shall not be violated during all normal and Credible Single Contingency conditions; and

(iv)	The operation of all Reactive Power devices under the control of a TO or a Qualified Scheduling Entity (QSE) will be coordinated under the direction of ERCOT to maintain transmission voltage levels within normal limits and post-contingency voltages within post contingency limits.  Static reactive devices will be managed to ensure that adequate dynamic reactive reserves are maintained at all times.

(c)	Notification

(i)	Generation Resources with voltage problems shall notify the TO to whom they are directly connected.  TOs shall notify other affected TOs and ERCOT; and

(ii)	ERCOT will monitor events and may direct actions to solve the problem.

(d)	Response

(i)	When the voltage levels deviate from established limits, ERCOT or the TO shall take immediate steps to relieve the condition using all available reactive resources.

(e)	Monitoring

(i)	TOs shall provide telemetry to ERCOT on all major transmission bus voltages.

(f)	Controls

(i)	ERCOT must be aware of the location of and availability of reactive capability;

(ii)	ERCOT shall maintain displays to monitor Voltage Profiles and reactive flows; and

(iii)	Controls to maintain Voltage Profiles may include but are not limited to capacitor switching, reactor switching, auto-transformer tap changing, generator reactive dispatch, transmission line switching, and Load shedding.

(g)	Documentation

(i)	Each TO must maintain a voltage/reactive plan for normal and Emergency Conditions and will provide this plan to adjacent TOs as well as ERCOT upon request.

(h)	Emergency or Abnormal Conditions

(i)	Transmission systems shall be designed so that effective reactive reserves shall be available without de-energizing other Facilities or shedding Load under normal conditions;

(ii)	Major transmission lines shall be kept in service during light Load as much as possible.  Lines should only be removed after all applicable reactive controls are implemented and studies show that reliability will not be degraded; and

(iii)	Voltage reduction should not be done on the transmission system unless coordinated with adjacent TOs.

2.7.3	Special Consideration for Nuclear Power Plants

In all planning studies and Real-Time operations, ERCOT and TOs shall maintain the switchyard voltage at each nuclear power plant at a value that does not violate its licensing basis with the Nuclear Regulatory Commission (NRC).  ERCOT shall notify the QSE representing a nuclear power plant of the result of any studies where the voltage at the plant switchyard cannot be adequately maintained.  ERCOT and the TO shall monitor the voltage in Real-Time.  ERCOT shall provide notice to the QSE representing the nuclear power plant of any voltage inadequacy at the plant switchyard that cannot be corrected within 30 minutes.  High and low limits on switchyard voltage at each nuclear power plant necessary to meet these requirements shall be specified in ERCOT Procedures.

2.7.4	Reactive Considerations for Generation Resources

2.7.4.1	 Maintaining System Voltage

(1)	ERCOT will maintain a performance log of QSEs acknowledgements of Voltage Support Service (VSS) Dispatch Instructions concerning scheduled voltage or scheduled Reactive output requests.  A QSE's response that is completed in no more than five minutes from the time of issuance of such requests shall be deemed satisfactory.

(2)	ERCOT shall monitor the Automatic Voltage Regulator (AVR), as required in Protocol Section 6.5.5.1, Changes in Resource Status, to assure that it is on and operating automatically at least 98% of the time in which the QSE is providing the Reactive Power supply from Generation Resources required to provide VSS.  The percentage is calculated as:  Time (AVR is on while providing Service) / (Total Time Providing Services) (100%).

(3)	Except under Force Majeure conditions or ERCOT-permitted operation of the Generation Resource, failure of a Generation Resource required to provide VSS to provide either leading or lagging reactive up to the required capability of the unit upon request from a TO or ERCOT may, at the discretion of ERCOT, be reported to the Texas Reliability Entity (Texas RE).

(4)	Except under Force Majeure conditions or ERCOT-permitted operation of the Generation Resource, if a Generation Resource required to provide VSS fails to maintain transmission system voltage at the point of interconnection with the TSP within 2% of the voltage profile while operating at less than the maximum reactive capability of the Generation Resource, ERCOT may, at its discretion, report this to the Texas RE.

(5)	The Texas RE will investigate claims of alleged non-compliance and Force Majeure conditions, and address confirmed non-compliance situations.  The Texas RE will advise the Generation Resource, its QSE, ERCOT, and the TSP planning and operating staffs of the results of such investigations.

2.7.4.2	 Parameters for Standard Reactor and Capacitor Switching Plan

TOs shall provide switching plans for automatically controlled reactors, capacitors, and other reactive controlled sources to ERCOT.  For manually switched reactive devices, the TO shall provide its guidelines for the operation of these devices.  These plans and guidelines shall be posted on the MIS Secure Area and must be provided in accordance with the Network Operations Model Change Request (NOMCR) or other ERCOT prescribed process. The parameters to be provided in the standard reactor and capacitor switching plan as required by Protocol Section 3.10.7.1.5, Reactors, Capacitors, and other Reactive Controlled Sources are as follows:

Device Attributes

(a)	Transmission Element name per Protocol Section 3.10.7.1, Modeling of Transmission Elements and Parameters;

(b)	Substation name; and

(c)	Schedules of device:

(i)	Time-based;

(ii)	Voltage-based;

(iii)	Load-based;

(iv)	Contingency-based;

(v)	Normal Operation;

(vi)	Emergency Operation;

(vii)	Seasonal; and

(viii)	Others as required by technology.

2.7.4.3		Unit Dispatch Beyond the Corrected Unit Reactive Limit or Unit Reactive Limit

Each Generation Resource shall respond to ERCOT instructed voltage control, including exceeding its Corrected Unit Reactive Limit (CURL) or Unit Reactive Limit (URL).  For multi-generator busses, ERCOT shall not instruct any single Generation Resource to operate beyond its CURL or URL until all Generation Resources On-Line and interconnected at the same transmission bus, have been instructed to their respective CURLs or URLs.

2.8	Operation of Direct Current Ties

(1)	ERCOT will confirm interconnected non-ERCOT balancing authority schedule profiles with the Direct Current Tie (DC Tie) operator, who will control the tie to the schedules agreed to by both the designated security coordinator for the interconnected non-ERCOT balancing authority and ERCOT.

(2)	Any changes in the DC Tie schedules due to a de-rating of the DC Tie or transmission/generation capabilities in the non-ERCOT balancing authority will be communicated to ERCOT by the DC Tie Operator or designated security coordinator for the interconnected non-ERCOT balancing authority.

(3)	ERCOT will coordinate operation of the DC Tie(s) with the DC Tie operator such that the Inadvertent Energy Account as defined in Protocol Section 6.5.4, Inadvertent Energy Account, is maintained as close to zero as practicable.

2.8.1	Inadvertent Energy Management

The only inadvertent energy will be between ERCOT and the Southwest Power Pool (SPP) and/or Comision Federal de Electricidad (CFE).  ERCOT shall track any differences between the net of scheduled energy across each DC Tie and the actual metered value at that DC Tie in an Inadvertent Energy Account between ERCOT and each interconnected non-ERCOT balancing authority as per Protocol Section 6.5.4, Inadvertent Energy Account.  All inadvertent energy is placed in an inadvertent payback account to be paid back in kind.

2.9	Voltage Ride-Through Requirements for Generation Resources

(1)	The facility’s generation machine characteristics and plant design shall incorporate the firm Load shedding philosophy and criteria defined in this Section.  Inherent in this philosophy is the idea that all generators remain On-Line until all steps of firm Load shedding have been executed.

(2)	Generation Resources must be designed and generation voltage relays must be set to remain connected to the transmission system during the following operating conditions:

(a)	Generator terminal voltages are within 5% of the rated design voltage and volts per hertz are less than 105% of generator rated design voltage and frequency;

(b)	Generator terminal voltage deviations exceed 5% but are within 10% of the rated design voltage and persist for less than ten seconds;

(c)	Generator volts per hertz conditions are less than 116% of generator rated design voltage and frequency and last for less than 1.5 seconds;

(d)	A transmission system fault (three-phase, single-phase or phase-to-phase), but not a generator bus fault, is cleared by the protection scheme coordinated between the Generation Entity and the Transmission Service Provider (TSP) on any line connected to the generator’s transmission interconnect bus, provided such lines are not connected to induction generators described in paragraph (9) of Protocol Section 3.15, Voltage Support; and

(e)	In the case of a generator bus fault or a primary transmission system relay failure, the generator protective relaying may clear the generator independent of the operation of any transmission protective relaying.

(3)	Generating Resources required to provide Voltage Support Service (VSS) shall have and maintain the following capability:

(a)	Over-excitation limiters shall be provided and coordinated with the thermal capability of the generator field winding and protective relays in order to permit short-term reactive capability that allows at least 80% of the unit design standard (ANSI C50.13-1989), as follows:

Time (seconds)		10	30	60	120

Field Voltage %		208	146	125	112

After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.

(b)	Under-excitation limiters shall be provided and coordinated with loss-of-field protection to eliminate unnecessary generating unit disconnection as a result of operator error or equipment malfunction.

(4)	Generation Resources shall have protective relaying necessary to protect its equipment from abnormal conditions as well as to be consistent with protective relaying criteria described in Section 6.2.6.3.4, Generator Protection and Relay Requirements.

(5)	The Voltage Ride-Through (VRT) requirements do not apply to faults that occur between the generator terminals and the transmission voltage side of the Generator Step-Up (GSU) transformer, or when clearing the fault effectively disconnects the Generation Resources from the ERCOT System.

2.9.1	Additional Voltage Ride-Through Requirements for Intermittent Renewable Resources

(1)	All Intermittent Renewable Resources (IRRs) shall also comply with the requirements of this Section, except as follows:

(a)	An IRR that  interconnects to  the ERCOT System pursuant to a Standard Generation Interconnection Agreement (SGIA) (i) executed on or before January 16, 2014 and (ii) under which the IRR provided all required financial security to the TSP on or before January 16, 2014, is not required to meet any high VRT requirement greater than 1.1 per unit voltage unless the interconnected IRR includes one or more turbines that differ from the turbine model(s) described in the SGIA (including any attachment thereto), as that agreement existed on January 16, 2014.  Notwithstanding the foregoing, if the Resource Entity that owns or operates an IRR that was interconnected pursuant to an SGIA executed before January 16, 2014, under which the IRR provided all required financial security to the TSP on or before January 16, 2014, demonstrates to ERCOT’s satisfaction that the high VRT capability of the IRR is not lower than the capability of the turbine model(s) described in the SGIA (including any attachment thereto), as that agreement existed on January 16, 2014 that IRR is not required to meet the high VRT requirement in this Section.

(b)	An IRR that interconnects to the ERCOT System pursuant to an SGIA executed prior to November 1, 2008 is not required to meet VRT requirements presented in this Section.  However, any WGR that is installed on or after November 1, 2008 and that initially synchronizes with the ERCOT System, pursuant to a Standard Generation Interconnection Agreement (SGIA) (i) executed on or before January 16, 2014, and (ii) under which the IRR provided all required financial security to the TSP on or before January 16, 2014 (except for an IRR installed pursuant to an SGIA executed before November 1, 2008) shall be VRT-capable in accordance with the low VRT requirements in this Section and high-voltage requirements in this Section up to 1.1 per unit voltage unless the interconnected IRR includes one or more turbines that differ from the turbine model(s) described in the SGIA (including any attachment thereto), as that agreement existed on January 16, 2014 in which case the IRR shall also be required to comply with the high VRT requirements of this section, subject to the exemption described in paragraph (a), above.

(c)	An IRR that is not technically capable of complying with a 1.2 per unit voltage high VRT requirement and that is not subject to either of the exemptions described in paragraphs (a) or (b), above, is not required to meet any high Voltage Ride-Through (VRT) requirement greater than 1.1 per unit voltage until January 16, 2016

(d)	Notwithstanding any of the foregoing provisions, an IRR’s VRT capability shall not be reduced over time.

(2)	Each IRR shall provide technical documentation of VRT capability to ERCOT upon request.

(3)	Each IRR is required to set generator voltage relays to remain in service for at least 0.15 seconds during all transmission faults and to allow the system to recover as illustrated in Figure 1, Default Voltage Ride-Through Boundaries for IRRs, below.  Recovery time to 90% of per unit voltage should be within 1.75 seconds.  Faults on individual phases with delayed clearing (zone 2) may result in phase voltages outside this boundary but if the phase voltages remain inside this boundary, then generator voltage relays are required to be set to remain connected and recover as illustrated in Figure 1.

(4)	Each IRR shall remain interconnected during three-phase faults on the ERCOT System for a voltage level as low as zero volts with a duration of 0.15 seconds as measured at the Point of Interconnection (POI) unless a shorter clearing time requirement for a three-phase fault specific to the generating plant POI is determined by and documented by the TSP in conjunction with the SGIA.  The clearing time requirement shall not exceed nine cycles.

(5)	Each IRR shall set generator voltage relays to remain interconnected to the ERCOT System during the following high-voltage conditions, as illustrated in Figure 1: any per-unit voltage equal to or greater than 1.175 but less than 1.2 for up to 0.2 seconds, any per-unit voltage equal to or greater than 1.15 but less than 1.175 per unit voltage for up to 0.5 seconds, and any per-unit voltage equal to or greater than 1.1 but less than 1.15 for up to 1.0 seconds.  The indicated voltages are measured at the POI.

(6)	An IRR may be tripped Off-Line after the fault clearing period if this action is part of an approved Special Protection Systems (SPSs).

(7)	VRT requirements may be met by the performance of the generators; by installing additional reactive equipment behind the POI; or by a combination of generator performance and additional equipment behind the POI.  VRT requirements may be met by equipment outside the POI if documented in the SGIA.

(8)	If an IRR fails to comply with the clearing time or recovery VRT requirement, then the IRR and the interconnecting TSP shall be required to investigate and report to ERCOT on the cause of the IRR trip, identifying a reasonable mitigation plan and timeline.

Figure 1:  Default Voltage Ride-Through Boundaries for IRRs.