## Slide 1: NERC Standards Update
Colleen Frosch
ROS Meeting
January 7, 2016

## Slide 2: NERC Standards that go into effect in 2016
  January 1, 2016
  FAC-001-2
  FAC-002-2
  IRO-009-2
  NUC-001-3
  PRC-005-6
  April 1, 2016
  CIP v5
July 1, 2016
  BAL-001-2
  COM-002-4
  MOD-025-2*
  MOD-031-1
  PER-005-2
  PRC-002-2*
  PRC-004-4(i)
  PRC-019-2*
  PRC-024-2*
  * phased implementation

## Slide 3: Impacting Standards
Outline of discussion summarizing changes and impacts:
PRC-002-2 – Disturbance Monitoring and Reporting Requirements
Definition of Remedial Action Scheme
Definition of Operational Planning Analysis/Real-Time Assessment
COM-002-4 – Operating Personnel Communications Protocols

## Slide 4: PRC-002-2
PRC-002-2 Starting Point
What is it?
  To have adequate data available to facilitate analysis of the BES Disturbances
Who does it impact?
  TO, GO and Responsible Entity which is the PC or RC
  Retires PRC-018-1 (following full implementation of PRC-002-2)
When is it?
  Effective 7/1/2016 – phased implementation plan
  Market Rules changes?
  Possible changes to Section 6 of the Operating Guides

## Slide 5: PRC-002-2 R5 - NERC Language
R5 Each Responsible Entity shall:
R5.1 Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following:
  5.1.1 Generating resource (s) with:
    5.1.1.1 Gross individual nameplate rating greater than or equal to 500 MVA.
    5.1.1.1 Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA.
  5.1.2 Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL).
  5.1.3 Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter.
  5.1.4 One of more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL).
  5.1.5 Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program.

## Slide 6: PRC-002-2 R5
5.2 Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1 of at least:
  5.2.1 One BES Element; and
  5.2.2 One BES Element per 3,000 MW of the Responsible Entity’s historical simultaneous peak System Demand.
5.3 Notify all owners of identified BES Elements, within 90-calendar days of completion of Part 5.1, that their respective BES Elements require DDR data when requested.
5.4 Re-evaluate all BES Elements at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3 to implement the re-evaluated list of BES Elements as per the Implementation Plan.

## Slide 7: Implementation Plan for PRC-002-2 R5
  PRC-002-2 Next Steps
  Possible changes to Section 6 of the Operating Guides
ERCOT Planning to review initial identified BES Elements list with ERCOT Operations by 3/15/2016.
ERCOT plans to notify all owners of identified BES Elements by 5/1/2016.
Owners shall be at least 50% compliant within 4 years of the effective date of PRC-002-2 and 100% compliant within 6 years.
When ERCOT re-evaluates the list, the owner has 3 years following the notification to be 100% compliant.

## Slide 8: Remedial Action Scheme Definition
Remedial Action Scheme changes Starting Point
What is it?
  Changes the definition of an SPS/RAS
Who does it impact?
  Impacts many standards and SPS/RAS owners
When is it?
  Effective 4/1/2017
  Market Rules changes?
  Will need Protocol, Operating and Planning Guide changes
  MIS changes required (renaming)

## Slide 9: Remedial Action Scheme Definition- NERC Language
A scheme designed to detect predetermined System conditions and automatically take corrective actions that may include, but are not limited to, adjusting or tripping generation (MW and Mvar), tripping load, or reconfiguring a System(s). RAS accomplish objectives such as:
Meet requirements identified in the NERC Reliability Standards;
Maintain Bulk Electric System (BES) stability;
Maintain acceptable BES voltages;
Maintain acceptable BES power flows;
Limit the impact of Cascading or extreme events.

## Slide 10: Remedial Action Scheme Definition- NERC Language
The following do not individually constitute a RAS:
a. Protection Systems installed for the purpose of detecting Faults on BES Elements and isolating the faulted Elements
b. Schemes for automatic underfrequency load shedding (UFLS) and automatic undervoltage load shedding (UVLS) comprised of only distributed relays
c. Out-of-step tripping and power swing blocking
d. Automatic reclosing schemes
e. Schemes applied on an Element for non-Fault conditions, such as, but not limited to, generator loss-of-field, transformer top-oil temperature, overvoltage, or overload to protect the Element against damage by removing it from service
f. Controllers that switch or regulate one or more of the following: series or shunt reactive devices, flexible alternating current transmission system (FACTS) devices, phase-shifting transformers, variable-frequency transformers, or tap-changing transformers; and, that are located at and monitor quantities solely at the same station as the Element being switched or regulated
g. FACTS controllers that remotely switch static shunt reactive devices located at other stations to regulate the output of a single FACTS device
h. Schemes or controllers that remotely switch shunt reactors and shunt capacitors for voltage regulation that would otherwise be manually switched
i. Schemes that automatically de-energize a line for a non-Fault operation when one end of the line is open
j. Schemes that provide anti-islanding protection (e.g., protect load from effects of being isolated with generation that may not be capable of maintaining acceptable frequency and voltage)
k. Automatic sequences that proceed when manually initiated solely by a System Operator
l. Modulation of HVdc or FACTS via supplementary controls, such as angle damping or frequency damping applied to damp local or inter-area oscillations
m. Sub-synchronous resonance (SSR) protection schemes that directly detect sub-synchronous quantities (e.g., currents or torsional oscillations)
n. Generator controls such as, but not limited to, automatic generation control (AGC), generation excitation [e.g. automatic voltage regulation (AVR) and power system stabilizers (PSS)], fast valving, and speed governing

## Slide 11: Implementation Plan
RAS Next Steps:
ERCOT Planning and Operations to review all SPSs to determine if still an SPS/RAS under the new RAS definition by 2/1/16.
Review list with Texas RE by 3/1/16
If no longer a SPS/RAS, what is it?
ERCOT to draft NPRR/NOGRR/PGRR

## Slide 12: Operational Planning Analysis/Real-time Assessment Definition
Assessment changes Starting Point
What is it?
  New definition for Operational Planning Analysis and Real-time Assessment
Who does it impact?
  ERCOT and TOs
When is it?
  Effective 1/1/2017
  Market Rules changes?
  May need Protocol and/or Operating Guide changes
CFR changes?
  Possible, will need to review language

## Slide 13: Operational Planning Analysis/Real-time Assessment Definition - NERC Language
An analysis of the expected system conditions for the next day’s operation. (That analysis may be performed either a day ahead or as much as 12 months ahead.) Expected system conditions include things such as load forecast(s), generation output levels, Interchange, and known system constraints (transmission facility outages, generator outages, equipment limitations, etc.).
An evaluation of projected system conditions to assess anticipated (pre-Contingency) and potential (post-Contingency) conditions for next-day operations. The evaluation shall reflect applicable inputs including, but not limited to, load forecasts; generation output levels; Interchange; known Protection System and Special Protection System status or degradation; Transmission outages; generator outages; Facility Ratings; and identified phase angle and equipment limitations. (Operational Planning Analysis may be provided through internal systems or through third-party services.)
An examination of existing and expected system conditions, conducted by collecting and reviewing immediately available data
An evaluation of system conditions using Real-time data to assess existing (pre-Contingency) and potential (post-Contingency) operating conditions. The assessment shall reflect applicable inputs including, but not limited to: load, generation output levels, known Protection System and Special Protection System status or degradation, Transmission outages, generator outages, Interchange, Facility Ratings, and identified phase angle and equipment limitations. (Real-time Assessment may be provided through internal systems or through third-party services.)

## Slide 14: Implementation Plan
Assessment changes Next Steps
ERCOT will need to know phase angle limitations
  Most likely conduct a survey to obtain this information
  Reach out to a couple TOs to ensure the correct questions are being asked to get what is needed in the survey
  Conduct Survey
Decisions will need to be made about what will be the actions of ERCOT with phase angle exceedances
  Re-dispatch/commit generation?
  Take actions based on next-day study or wait until real-time?
Still considering if NPRR, NOGRR, CFR changes needed

## Slide 15: COM-002-2
COM-002-2 Starting Point:
What is it?
  To improve communications for the issuance of Operating Instructions with predefined communications protocols to reduce the possibility of miscommunication that could lead to action or inaction harmful to the reliability of the Bulk Electric System (BES).
Who does it impact?
  BA, DP, RC, TOP, GOP
When is it?
  Effective 7/1/2016
  Market Rules changes?
  NPRR748
  NOGRR151
CFR changes are needed

## Slide 16: COM-002-2 - NERC Language
R1 Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall develop documented communications protocols for its operating personnel that issue and receive Operating Instructions. The protocols shall, at a minimum:
See R1.1 – R1.6 of minimum requirements needed in communications protocols
R2 Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall conduct initial training for each of its operating personnel responsible for the Real-time operation of the interconnected Bulk Electric System on the documented communications protocols developed in Requirement R1 prior to that individual operator issuing an Operating Instruction.
R3 Each Distribution Provider and Generator Operator shall conduct initial training for each of its operating personnel who can receive an oral two-party, person-to-person Operating Instruction prior to that individual operator receiving an oral two-party, person-to-person Operating Instruction to either:
Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or
Request that the issuer reissue the Operating Instruction.
R4 Each Balancing Authority, Reliability Coordinator, and Transmission Operator shall at least once every twelve (12) calendar months:
  4.1 Assess adherence to the documented communications protocols in Requirement R1 by its operating personnel that issue and receive Operating Instructions, provide feedback to those operating personnel and take corrective action, as deemed appropriate by the entity, to address deviations from the documented protocols.
  4.2 Assess the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions and modify its documented communication protocols, as necessary.

## Slide 17: COM-002-2 - NERC Language
R5 Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either:
Confirm the receiver’s response if the repeated information is correct (in accordance with Requirement R6).
Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver, or
Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver.
R6 Each Balancing Authority, Distribution Provider, Generator Operator, and Transmission Operator that receives an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either:
Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or
Request that the issuer reissue the Operating Instruction.
R7 Each Balancing Authority, Reliability Coordinator, and Transmission Operator that issues a written or oral single-party to multiple-party burst Operating Instruction during an Emergency shall confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction.

## Slide 18: Implementation Plan
COM-002-2 Next Steps:
ERCOT will work with market on changes to:
  Protocols: NPRR748
  Operating Guides: NOGRR151
  CFR changes
ERCOT will post its communications protocols same place as the Operator Procedures.