| NPRR Number | 747 | NPRR Title | Revision of Voltage Control Requirements |
| --- | --- | --- | --- |
| Date |  | January 13, 2016 |  |
| Submitter’s Information |  |  |  |
| Name |  | John Palen |  |
| E-mail Address |  | John.Palen@nrg.com |  |
| Company |  | NRG Texas LLC |  |
| Phone Number |  | 713-537-3706 |  |
| Cell Number |  | 713-545-3415 |  |
| Market Segment |  | Independent Generator |  |

Comments

NRG Texas LLC (NRG) appreciates the opportunity to opine on the topic of Voltage Support and respectfully submits these comments on top of the 12/8/15 Oncor comments.  Per ERCOT Market Rules, the comment fields were deleted, but they can always be referenced in the 12/8/15 Oncor comments.

Reactive Power is a calculated mathematical quantity, and from a Generation Resource, it is the intangible byproduct created by the following three primary factors:

1.	The magnitude and characteristics of the Generator Step-Up (GSU) impedance

2.	Transmission System voltage magnitude

3.	Terminal voltage of the Generation Resource

During the design of a facility, the GSU impedance is selected according to multiple factors with Volt-Amperes reactive (VAr) production being only one of many.  However, it is a fixed quantity upon construction of the Generation Resource.  After installation, the generator operator can only control one of three factors listed above.  During operation, the generator operator controls the Generation Resource to create and deliver power, while adjusting generator terminal voltage within specified limits.  VAr production (as mentioned, a mathematical computation) is a byproduct of the process.  It is not an independent, tangible product in and of itself.  A Generation Resource does not create VArs.  VArs are created from the interaction of the Generation Resource and the transmission system across the GSU.  It is outside the bounds of reality to expect otherwise and require rigid adherence to specified values of VAr production for variable conditions outside the control of the owner and operator of the Generation Resource.

Additionally, the use of GSU fixed taps offers a means to optimize the delivery of VAr.  However, the selection of taps to fulfill an arbitrary selection of unit operating power factor is not always the best or most favorable position to operate a unit.

To account for the operating reality described above, these comments propose changes to the reactive capability requirement of maintaining a 0.95 power factor capability at the current Voltage Profile to maintaining the lagging reactive capability at nominal system voltage, and leading reactive capability at 1.05 of nominal system voltage, exactly when that capability would be needed.

Current language requires that Generation Resources maintain a reactive capability which references the transmission system Voltage Profile, instead of a fixed value.  Voltage Profiles are the desired voltages across the transmission system, and are developed to maintain voltage stability within the interconnect.  Due to the dynamic nature of the grid, a Voltage Profile at a given point may change significantly over a period of time, as Generation Resources are either added or retired from the system, and as grid topology changes in response to system needs.  By referencing the reactive requirement to a moving target, generators need to unnecessarily plan for this capability across the entire range of possible Voltage Profile values from 95% to 105% of nominal system voltage (327.8 kV to 362.3 kV in a 345 kV circuit as an example), which is beyond normal generation capabilities without the addition of static reactive devices.  Requiring Generation Resources to simultaneously maintain fixed leading and lagging power factor capability for system voltage extremes (95%-105% of nominal), is unnecessary and inefficient. It may actually pose a challenge to grid stability in the event of an inadvertent deployment of this reactive capability at the wrong time.

The proposed comments in Section 3.15, Voltage Support, paragraph (3) and (4) do not change a generator’s reactive capability, inherent to the generator’s design. The comments also do not remove or reduce a Generation Resource’s obligation to respond to changes of a Voltage Profile. They merely provide consistency in reactive capability evaluation and allow for a uniform reporting method in the resource registration process.

In addition, NRG agrees with the Calpine comments submitted on December 4, 2015.  All communications, including the deployment of Voltage Support Service (VSS), should be directed to the Qualified Scheduling Entity (QSE), not the Resource Entity.  While there does not currently appear to be Protocol language precluding a Transmission Service Provider (TSP) from contacting a Resource Entity directly, NRG believes the clear intent of the protocols is for the QSE to serve as the direct line of communication for Resource Entities and Load Serving Entities (LSEs).  Section 2 of the Protocols defines a QSE as:

“A Market Participant that is qualified by ERCOT in accordance with Section 16, Registration and Qualification of Market Participants, for communication with ERCOT for Resource Entities and LSEs and for settling payments and charges with ERCOT” (emphasis added).

If ERCOT must abide by this provision, i.e., to communicate with Resource Entities and LSEs through the QSE, then for consistency TSPs should do the same.  One of the main motivations for setting up QSEs in the first place was ostensibly to simplify and streamline the communication process due to the plethora of registered Resource Entities and LSEs in ERCOT.

In addition to the Section 2 definition, Section 16.2.1(1)(k), Criteria for Qualification as a Qualified Scheduling Entity, states that to become and remain a QSE, an entity must among other things:

“Maintain a 24-hour, seven-day-per-week scheduling center with qualified personnel for the purposes of communicating with ERCOT for scheduling and deploying the QSE’s Ancillary Services in Real-Time….” (emphasis added)

The QSE Ancillary Service being addressed in this Nodal Protocol Revision Request (NPRR) is VSS.  The language is clear, the scheduling and deployment of Ancillary Services in Real-Time is to be performed by communicating the instructions through the QSE, not directly to a Resource Entity.  Indeed, Resource Entity personnel are accustomed to receiving instructions from ERCOT via their QSEs.  Modifying that familiar communication process by having TSPs bypassing the QSEs could lead to confusion, as Resource Entities will now have multiple masters when asked to adjust the output or settings of their generation units.  Ancillary Service deployment instructions have been communicated from ERCOT to QSEs since the market opened.  There is no reason to change this day-to-day operating process by making an exception for VSS.

For the reasons stated above, NRG recommends the QSE remain the point of contact for any and all Ancillary Service deployment instructions.

Revised Proposed Protocol Language

## 2.1	DEFINITIONS

- Voltage Profile

The set of normally desired Voltage Set Points for those Generation Resources specified in paragraph (2) of Section 3.15, Voltage Support, in the ERCOT System for each Season.

- Voltage Set Point

The voltage that a Generation Resource is required to maintain at its Point of Interconnection and that is initially communicated via the Voltage Profile but may be modified by a Real-Time directive from ERCOT, the interconnecting TSP, or that TSP’s agentthrough the Generation Resource’s QSE.

Automatic Voltage Regulator (AVR)

A device on a Generation Resource or a control system at the Facility of a Generation Resource used to automatically control the voltage to an established Voltage Set Point.

3.15	Voltage Support

(1)	ERCOT, in coordination with the Transmission Service Providers (TSPs), shall establish and update, as necessary, the ERCOT System Voltage Profile and shall post it on the Market Information System (MIS) Secure Area.  ERCOT, the interconnecting TSP, or that TSP’s agent, may modify the Voltage Set Point described in the Voltage Profile based on current system conditions.  During the generation of the Voltage profile, special attention shall be paid to those buses whereVoltage Set Points were changed in real time since the last Voltage Profile generation.

(2)	All Generation Resources (including self-serve generating units) that have a gross generating unit rating greater than 20 MVA or those units connected at the same Point of Interconnection (POI) that have gross generating unit ratings aggregating to greater than 20 MVA, that supply power to the ERCOT Transmission Grid, shall provide Voltage Support Service (VSS).

(3)	Each Generation Resource required to provide VSS shall comply with the following Reactive Power Requirements:

(a)	An over-excited (lagging or producing) power factor capability of 0.95 or less determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid and at 1.0 of nominal system voltage , both measured at the POI;

(b)	An under-excited (leading or absorbing) power factor capability of 0.95 or less, determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid and 1.05 of nominal system voltage, both measured at the POI;

(c)	Reactive Power capability shall be available at all MW output levels and may be met through a combination of the Generation Resource’s Unit Reactive Limit (URL), which is the generating unit’s dynamic leading and lagging operating capability, and/or dynamic VAr capable devices.  This Reactive Power profile is depicted graphically as a rectangle.  For Intermittent Renewable Resources (IRRs), the Reactive Power requirements shall be available at all MW output levels at or above 10% of the IRR’s nameplate capacity.  When an IRR is operating below 10% of its nameplate capacity and is unable to support voltage at the POI, ERCOT may require an IRR to disconnect from the ERCOT System for purposes of maintaining reliability; and

(d)	As part of the technical Resource requirements to begin commercial operations, all Generation Resources must conduct an engineering study, or demonstrate through performance testing, compliance with the Reactive Power capability requirements of this Section.  Any study or testing results must be accepted by ERCOT prior to commercial operations.

(4)	Wind-powered Generation Resources (WGRs) that commenced operation on or after February 17, 2004, and have a signed Standard Generation Interconnection Agreement (SGIA) on or before December 1, 2009 (“Existing Non-Exempt WGRs”), must be capable of producing a defined quantity of Reactive Power to maintain a Voltage Set Point established by ERCOT in accordance with the Reactive Power requirements established in paragraph (3) above, except in the circumstances described in paragraph (a) below.

(a)	Existing Non-Exempt WGRs whose current design does not allow them to meet the Reactive Power requirements established in paragraph (3) above must conduct an engineering study using the Summer/Fall 2010 on-peak/off-peak Voltage Profiles, or conduct performance testing to determine their actual Reactive Power capability.  Any study or testing results must be accepted by ERCOT.  The Reactive Power requirements applicable to these Existing Non-Exempt WGRs will be the greater of: the leading and lagging Reactive Power capabilities established by the Existing Non-Exempt WGR’s engineering study or testing results; or Reactive Power proportional to the real power output of the Existing Non-Exempt WGR (this Reactive Power profile is depicted graphically as a triangle) sufficient to provide an over-excited (lagging) power factor capability of 0.95 or less at 1.0 of nominal system voltage, and an under-excited (leading) power factor capability of 0.95 or less, at 1.05 of nominal system voltage, both determined at the POI.

(i)	Existing Non-Exempt WGRs shall submit the engineering study results or testing results to ERCOT no later than five Business Days after its completion.

(ii)	Existing Non-Exempt WGRs shall update any and all Resource Registration data regarding their Reactive Power capability documented by the engineering study results or testing results.

(iii)	If the Existing Non-Exempt WGR’s engineering study results or testing results indicate that the WGR is not able to provide Reactive Power capability that meets the triangle profile described in paragraph (4)(a) above, then the Existing Non-Exempt WGR will take steps necessary to meet that Reactive Power requirement depicted graphically as a triangle by a date mutually agreed upon by the Existing Non-Exempt WGR and ERCOT.  The Existing Non-Exempt WGR may meet the Reactive Power requirement through a combination of the WGR’s URL and/or automatically switchable static VAr capable devices and/or dynamic VAr capable devices.  No later than five Business Days after completion of the steps to meet that Reactive Power requirement, the Existing Non-Exempt WGR will update any and all Resource Registration data regarding its Reactive Power and provide written notice to ERCOT that it has completed the steps necessary to meet its Reactive Power requirement.

(iv)	For purposes of measuring future compliance with Reactive Power requirements for Existing Non-Exempt WGRs, results from performance testing or the Summer/Fall 2010 on-peak/off-peak Voltage Profiles utilized in the Existing Non-Exempt WGR’s engineering study shall be the basis for measuring compliance, even if the Voltage Profiles provided to the Existing Non-Exempt WGR are revised for other purposes.

(b)	Existing Non-Exempt WGRs whose current design allows them to meet the Reactive Power requirements established in paragraph (3) above (depicted graphically as a rectangle) shall continue to comply with that requirement.  ERCOT, with cause, may request that these Existing Non-Exempt WGRs provide further evidence, including an engineering study, or performance testing, to confirm accuracy of Resource Registration data supporting their Reactive Power capability.

(5)	Qualified Renewable Generation Resources (as described in Section 14, State of Texas Renewable Energy Credit Trading Program) in operation before February 17, 2004, required to provide VSS and all other Generation Resources required to provide VSS that were in operation prior to September 1, 1999, whose current design does not allow them to meet the Reactive Power requirements established in paragraph (3) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the ERCOT Operating Guides.

(6)	New generating units connected before May 17, 2005, whose owners demonstrate to ERCOT’s satisfaction that design and/or equipment procurement decisions were made prior to February 17, 2004, based upon previous standards, whose design does not allow them to meet the Reactive Power requirements established in paragraph (3) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the Operating Guides.

(7)	For purposes of meeting the Reactive Power requirements in paragraphs (3) through (6) above, multiple generation units including wind turbines shall, at a Generation Entity’s option, be treated as a single Generation Resource or WGR if the units are connected to the same transmission bus.

[NPRR588: Replace paragraph (7) above with the following upon system implementation:] (7) For purposes of meeting the Reactive Power requirements in paragraphs (3) through (6) above, multiple generation units including IRRs shall, at a Generation Entity’s option, be treated as a single Generation Resource if the units are connected to the same transmission bus.

(8)	Generation Entities may submit to ERCOT specific proposals to meet the Reactive Power requirements established in paragraph (3) above by employing a combination of the URL and added VAr capability, provided that the added VAr capability shall be automatically switchable static and/or dynamic VAr devices.  A Generation Resource and TSP may enter into an agreement in which the proposed static VAr devices can be switchable using Supervisory Control and Data Acquisition (SCADA).  ERCOT may, at its sole discretion, either approve or deny a specific proposal, provided that in either case, ERCOT shall provide the submitter an explanation of its decision.

(9)	A Generation Resource and TSP may enter into an agreement in which the Generation Resource compensates the TSP to provide VSS to meet the Reactive Power requirements of paragraph (3) above in part or in whole.  The TSP shall certify to ERCOT that the agreement complies with the Reactive Power requirements of paragraph (3).

(10)	Unless specifically approved by ERCOT, no unit equipment replacement or modification at a Generation Resource shall reduce the capability of the unit below the Reactive Power requirements that applied prior to the replacement or modification.

(11)	Generation Resources shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damage is imminent.

(12)	All WGRs must provide a Real-Time SCADA point that communicates to ERCOT the number of wind turbines that are available for real power and/or Reactive Power injection into the ERCOT Transmission Grid.  WGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following:

(a)	The number of wind turbines that are not able to communicate and whose status is unknown; and

(b)	The number of wind turbines out of service and not available for operation.

[NPRR588: Insert paragraph (13) below upon system implementation and renumber accordingly:] (13) All PhotoVoltaic Generation Resources (PVGRs) must provide a Real-Time SCADA point that communicates to ERCOT the capacity of PhotoVoltaic (PV) equipment that is available for real power and/or Reactive Power injection into the ERCOT Transmission Grid. PVGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following: (a) The capacity of PV equipment that is not able to communicate and whose status is unknown; and (b) The capacity of PV equipment that is out of service and not available for operation.

(13)	For the purpose of complying with the Reactive Power requirements under this Section 3.15, Reactive Power losses that occur on privately-owned transmission lines behind the POI may be compensated by automatically switchable static VAr capable devices.

- 3.15.3	Generation Resource Requirements Related to Voltage Support

(1)	Generation Resources required to provide VSS shall have and maintain Reactive Power capability at least equal to the Reactive Power capability requirements specified in these Protocols and the ERCOT Operating Guides.

(2)	Generation Resources providing VSS shall be compliant with the ERCOT Operating Guides for response to transient voltage disturbance.

(3)	Generation Resources providing VSS must meet technical requirements specified in Section 8.1.1.1, Ancillary Service Qualification and Testing, and the performance standards specified in Section 8.1.1, QSE Ancillary Service Performance Standards.

(4)	Each Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the automatic voltage control mode unless specifically directed to operate in manual mode by ERCOT, or when the unit is going On-Line or Off-Line, or the QSE determines a need to operate in manual mode in the event of an Emergency Condition at the generating plant.

(5)	Each Generation Resource providing VSS shall maintain the Voltage Set Point established by ERCOT, the interconnecting TSP, or the TSP’s agent, subject to the Generation Resource’s operating characteristic limits, voltage limits, and within tolerances identified in paragraph (4) of Operating Guide Section 2.7.3.5, Resource Entity Responsibilities and Generation Resource Requirements.

(6)	The reactive capability required must be maintained at all times that the Generation Resource is On-Line.

(7)	Each QSE shall send to ERCOT, via telemetry, the AVR and Power System Stabilizer (PSS) status for each of its Generation Resources providing VSS.  For AVRs, an “On” status will indicate the AVR is on and set to regulate the Resource’s terminal voltage in the voltage control mode, and an “Off” status will indicate the AVR is off or in a manual mode.  Each QSE shall monitor the status of its Generation Resources’ regulators and stabilizers, and shall report status changes to ERCOT.

(8)	Each Resource Entity shall provide information related to the tuning parameters, local or inter-area, of any PSS installed at a Generation Resource.

6.5.7.7	Voltage Support Service

(1)	ERCOT shall coordinate with TSPs the creation and maintenance of Voltage Profiles as described in Section 3.15, Voltage Support.

(2)	ERCOT, the interconnecting TSP, or the TSP’s agent may instruct any QSEs having a Generation Resource required to provide Voltage Support Service (VSS) to make adjustments for voltage support within the Generation Resource’s Unit Reactive Limit (URL) provided to ERCOT.    Unless ERCOT has issued a Resource-specific Dispatch Instruction, a Generation Resource providing VSS may not be requested to reduce MW output so as to provide additional MVAr.

(3)	ERCOT and TSPs shall develop procedures for the the operation of transmission-controlled reactive Resourcesin order to minimize the dependence on generation-supplied reactive Resources.  For Generation Resources required to provide VSS, GSU transformer tap settings must be managed to maximize the use of the ERCOT System for all Market Participants while maintaining adequate reliability.

(4)	Each TSP, under ERCOT’s direction, is responsible for monitoring and ensuring that all Generation Resources required to provide VSS, have their dynamic reactive capability deployed in approximate proportion to their respective capability requirements.

(5)	Each Generation Resource required to provide VSS shall follow its Voltage Set Point as directed by ERCOT, the interconnecting TSP, or the TSP’s agent through the Generation Resource’s QSE, within the operating Reactive Power capability of the Generation Resource.