## Slide 1
Review of August 13, 2015
Resmi Surendran
TAC 10/29/2015

## Slide 2: Case Study: August 13th
Chart: MW
| 42229.5835532407 | 42229.586956018502 | 42229.590416666702 | 42229.593900462998 | 42229.597384259301 | 42229.600868055597 | 42229.604351851798 | 42229.607824074097 | 42229.611273148097 | 42229.614722222199 | 42229.618229166699 | 42229.621689814798 | 42229.625185185199 | 42229.628611111097 | 42229.632106481498 | 42229.635578703703 | 42229.6390509259 | 42229.642523148097 | 42229.645983796298 | 42229.649456018502 | 42229.652939814798 | 42229.656435185199 | 42229.659884259301 | 42229.6633449074 | 42229.666863425897 | 42229.670289351903 | 42229.6737615741 | 42229.677233796298 | 42229.680729166699 | 42229.684178240699 | 42229.687685185199 | 42229.691134259301 | 42229.694629629601 | 42229.698067129597 | 42229.701562499999 | 42229.7050115741 | 42229.708530092597 | 42229.711956018502 | 42229.715416666702 | 42229.718900462998 | 42229.722384259301 | 42229.7258449074 | 42229.729328703703 | 42229.732824074097 | 42229.736273148097 | 42229.739733796298 | 42229.743194444403 | 42229.746689814798
RTOLCAP - RRS | 2900.1154 | 2765.7613 | 2582.0186 | 2213.8086 | 1788.8424 | 1918.5828 | 2045.8444 | 1946.9633 | 1878.6061 | 1810.6278 | 1813.3988 | 1723.6427 | 1599.5646 | 1346.6075 | 1478.2095 | 1347.7572 | 1489.5623 | 1699.094 | 1947.7379 | 1892.5466 | 1649.1017 | 1597.4701 | 1568.6072 | 1487.196 | 1531.6108 | 1599.2131 | 1413.2509 | 1469.0649 | 1489.3811 | 1525.3657 | 1489.4736 | 1647.0029 | 1612.3988 | 1560.3567 | 1723.2382 | 1605.3577 | 1597.093 | 2087.5743 | 2210.5768 | 2093.5458 | 1961.1749 | 2269.4894 | 2655.8179 | 2631.2244 | 2850.1359 | 3116.4998 | 3127.5371 | 3185.8895
RTNCLRRRS | 1159.9392 | 1127.3998 | 1130.2303 | 1127.1478 | 1127.446 | 1126.5294 | 1126.4709 | 1126.4702 | 1127.3513 | 1126.6826 | 1126.2031 | 1126.7109 | 1126.3942 | 1126.9816 | 1125.8008 | 1126.2946 | 1129.115 | 1127.1055 | 1127.9598 | 1131.5266 | 1130.2985 | 1129.9056 | 1130.7078 | 1132.3452 | 1132.0178 | 1131.8638 | 1132.8265 | 1131.01 | 1130.1125 | 1131.0164 | 1131.8877 | 1131.2229 | 1132.9049 | 1130.8298 | 1131.973 | 1131.5605 | 1129.3901 | 1129.7826 | 1128.7914 | 1127.7994 | 1130.7045 | 1129.4027 | 1129.3096 | 1126.9841 | 1126.6381 | 1124.4324 | 1126.6938 | 1126.7618
GENRRS | 1154.9 | 1154.9 | 1154.9 | 1170.9 | 1154.9 | 1154.9 | 1154.9 | 1154.9 | 1154.9 | 1154.9 | 1154.9 | 1154.9 | 1055 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155 | 1155
RTOFFCAP | 600.2371 | 600.2371 | 600.2371 | 600.2371 | 600.2371 | 600.2371 | 590.337 | 589.347 | 590.337 | 501.237 | 500.247 | 500.247 | 501.237 | 501.237 | 150.777 | 354.42 | 121.77 | 51.48 | 0 | 0 | 0 | 0 | 0 | 0 | 69.3 | 68.31 | 68.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 Min ERS | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 535.94 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46 | 502.46
10 Min ERS | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 371.564 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498 | 356.498
WS ERS | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74 | 21.74
TDSP Load MP | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183
PRC | 3523.4172 | 3404.9819 | 3342.1206 | 3118.1482 | 2845.1631 | 2845.0911 | 2878.5654 | 2859.8093 | 2816.8005 | 2836.8259 | 2770.2549 | 2739.4309 | 2598.9482 | 2386.5974 | 2471.1936 | 2491.717 | 2473.5454 | 2515.8674 | 2590.7134 | 2659.9795 | 2603.49 | 2509.2502 | 2472.7422 | 2374.1243 | 2447.8721 | 2480.7732 | 2494.9087 | 2437.3733 | 2440.4666 | 2459.6448 | 2417.0417 | 2470.0149 | 2443.8311 | 2412.4028 | 2457.6226 | 2431.9146 | 2396.2361 | 2637.8574 | 2676.8823 | 2706.4802 | 2732.9165 | 2834.8494 | 2937.9863 | 3021.605 | 3089.9219 | 3225.0586 | 3250.2441 | 3375.5596
PRC at 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500 | 2500
Notes: In this graph RTOLCAP = (RTOLCAP – RRS)+ RTNCLRRRS+ GEN RRS
Of the 2300 MWs of RRS, Load Resources were obligated to provide 1150MW. ERCOT had 929 MWs of ERS obligated from 1 to 4 pm and 881 MWs obligated from 4 to 8 pm. When ERCOT is in an emergency condition, we can request the TDSPs to deploy the loads contracted under their Load Management Programs which is about 183 MWs. There were no deployments of RRS or ERS during the scarcity condition notices during the week of Aug 10th.

## Slide 3: PRC Vs ORDC
EEA1 is called based on PRC <2300 to enable the use of Resource that are only available in emergency in a series of steps to avoid load shedding. PRC only considers frequency responsive capacity (max 20%HSL)
ORDC is based on LOLP of reserves falling below 2000. ORDC reserve (RTOLCAP) includes capacity that is considered in PRC up to 100% HSL and it also includes QSGR, capacity from WGRs which are curtailed and NFRC. i.e. ORDC reserves include all the remaining reserves in the system.
PRC drops much faster than ORDC because PRC only considers a fraction of the available online capacity.
Since EEA is based on PRC, ORDC reserves could be high and price adder could be low when we are near EEA unless ORDC converges to PRC
As we approach scarcity PRC will be around 2500 and ORDC will gradually approach PRC as prices increase causing QSGRs to come online, resources to put their duct firing online and SCED to move resources to the top making the remaining capacity within 20%HSL. However, since minimum RRS level is 2300MW there could be situations where PRC stays just above 2300MW for a long time and could drop below 2300 when we still have lot of quick starts physically offline but available to SCED.

## Slide 4: Non-Spin of QSGR
Chart: MW
QSGR_NSRS_R (MW = 0 and NSRS_R > 0) | 935 | 929 | 929 | 929 | 929 | 929 | 929 | 929 | 929 | 929 | 929 | 929 | 929 | 924 | 924 | 785 | 854 | 924 | 924 | 924 | 924 | 924 | 924 | 924 | 854 | 784 | 784 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 923
PRC | 3523.4172 | 3404.9819 | 3342.1206 | 3118.1482 | 2845.1631 | 2845.0911 | 2878.5654 | 2859.8093 | 2816.8005 | 2836.8259 | 2770.2549 | 2739.4309 | 2598.9482 | 2386.5974 | 2471.1936 | 2491.717 | 2473.5454 | 2515.8674 | 2590.7134 | 2659.9795 | 2603.49 | 2509.2502 | 2472.7422 | 2374.1243 | 2447.8721 | 2480.7732 | 2494.9087 | 2437.3733 | 2440.4666 | 2459.6448 | 2417.0417 | 2470.0149 | 2443.8311 | 2412.4028 | 2457.6226 | 2431.9146 | 2396.2361 | 2637.8574 | 2676.8823 | 2706.4802 | 2732.9165 | 2834.8494 | 2937.9863 | 3021.605 | 3089.9219 | 3225.0586 | 3250.2441 | 3375.5596
RTOLCAP | 5214.9546 | 5048.061 | 4867.1489 | 4511.8564 | 4071.1885 | 4200.0122 | 4327.2153 | 4228.3335 | 4160.8574 | 4092.2104 | 4094.502 | 4005.2537 | 3780.9587 | 3628.5891 | 3759.0103 | 3629.0518 | 3773.6772 | 3981.1995 | 4230.6978 | 4179.0732 | 3934.4001 | 3882.3757 | 3854.3149 | 3774.5413 | 3818.6287 | 3886.0769 | 3701.0774 | 3755.075 | 3774.4937 | 3811.3821 | 3776.3613 | 3933.2258 | 3900.3037 | 3846.1865 | 4010.2112 | 3891.9182 | 3881.4832 | 4372.3569 | 4494.3682 | 4376.3452 | 4246.8794 | 4553.8921 | 4940.1274 | 4913.2085 | 5131.7739 | 5395.9321 | 5409.231 | 5467.6514
Notes: Maximum 393.2MW Non-Spin was deployed from 8/13/2015 15:06 to 8/13/2015 18:05 due to low available capacity

## Slide 5: LOLP Vs Emergency Alerts (Corrected Data)
Chart: MW
| 42229.583553240744 | 42229.586956018517 | 42229.590416666666 | 42229.593900462962 | 42229.597384259258 | 42229.600868055553 | 42229.604351851849 | 42229.607824074075 | 42229.611273148148 | 42229.614722222221 | 42229.61822916667 | 42229.621689814812 | 42229.625185185185 | 42229.628611111111 | 42229.632106481484 | 42229.635578703703 | 42229.639050925929 | 42229.642523148148 | 42229.645983796298 | 42229.649456018517 | 42229.652939814812 | 42229.656435185185 | 42229.659884259258 | 42229.663344907407 | 42229.666863425926 | 42229.670289351852 | 42229.673761574071 | 42229.677233796298 | 42229.68072916667 | 42229.684178240743 | 42229.687685185185 | 42229.691134259258 | 42229.69462962963 | 42229.698067129626 | 42229.701562499999 | 42229.705011574071 | 42229.70853009259 | 42229.711956018517 | 42229.715416666666 | 42229.718900462962 | 42229.722384259258 | 42229.725844907407 | 42229.729328703703 | 42229.732824074075 | 42229.736273148148 | 42229.739733796298 | 42229.743194444447 | 42229.746689814812
PRC | 3523.4172 | 3404.9819 | 3342.1206 | 3118.1482 | 2845.1631 | 2845.0911 | 2878.5654 | 2859.8093 | 2816.8005 | 2836.8259 | 2770.2549 | 2739.4309 | 2598.9482 | 2386.5974 | 2471.1936 | 2491.717 | 2473.5454 | 2515.8674 | 2590.7134 | 2659.9795 | 2603.49 | 2509.2502 | 2472.7422 | 2374.1243 | 2447.8721 | 2480.7732 | 2494.9087 | 2437.3733 | 2440.4666 | 2459.6448 | 2417.0417 | 2470.0149 | 2443.8311 | 2412.4028 | 2457.6226 | 2431.9146 | 2396.2361 | 2637.8574 | 2676.8823 | 2706.4802 | 2732.9165 | 2834.8494 | 2937.9863 | 3021.605 | 3089.9219 | 3225.0586 | 3250.2441 | 3375.5596
RTOLCAP | 5214.9546 | 5048.061 | 4867.1489 | 4511.8564 | 4071.1885 | 4200.0122 | 4327.2153 | 4228.3335 | 4160.8574 | 4092.2104 | 4094.502 | 4005.2537 | 3780.9587 | 3628.5891 | 3759.0103 | 3629.0518 | 3773.6772 | 3981.1995 | 4230.6978 | 4179.0732 | 3934.4001 | 3882.3757 | 3854.3149 | 3774.5413 | 3818.6287 | 3886.0769 | 3701.0774 | 3755.075 | 3774.4937 | 3811.3821 | 3776.3613 | 3933.2258 | 3900.3037 | 3846.1865 | 4010.2112 | 3891.9182 | 3881.4832 | 4372.3569 | 4494.3682 | 4376.3452 | 4246.8794 | 4553.8921 | 4940.1274 | 4913.2085 | 5131.7739 | 5395.9321 | 5409.231 | 5467.6514
LOLP | 0.00074895 | 0.0012 | 0.0019765 | 0.0050788 | 0.01504 | 0.011196 | 0.0082467 | 0.010538 | 0.012387 | 0.016359 | 0.01648 | 0.019999 | 0.032167 | 0.044833 | 0.06049 | 0.051789 | 0.051406 | 0.038546 | 0.025892 | 0.028354 | 0.044308 | 0.048903 | 0.050872 | 0.050683 | 0.059522 | 0.044705 | 0.062095 | 0.058434 | 0.060693 | 0.056602 | 0.058362 | 0.045218 | 0.047412 | 0.052173 | 0.038925 | 0.04809 | 0.049015 | 0.01967 | 0.01527 | 0.019344 | 0.024906 | 0.013529 | 0.0059192 | 0.0062761 | 0.0038209 | 0.0020266 | 0.0019608 | 0.001695
Notes: LOLP reflects the N-0 loss of load probability

## Slide 6
Appendix
August 10, 2015 – August 13, 2015
Hour Ending 15-17

## Slide 7: All Reserves
Notes: In this graph RTOLCAP = (RTOLCAP – RRS)+ RTNCLRRRS+ GEN RRS
Of the 2300 MWs of RRS, Load Resources were obligated to provide 1150MW. ERCOT had 929 MWs of ERS obligated from 1 to 4 pm and 881 MWs obligated from 4 to 8 pm. When ERCOT is in an emergency condition, we can request the TDSPs to deploy the loads contracted under their Load Management Programs which is about 183 MWs. There were no deployments of RRS or ERS during the scarcity condition notices during the week of Aug 10th.

## Slide 8: Reserves and Prices

## Slide 9: Reserves and Outages

## Slide 10: System Capacity
Notes: System capacity and load were very similar between 8/12 and 8/13. However PRC was lower on 8/13 primarily due to lower wind over peak, and probably more units dispatched above 80% of HSL

## Slide 11: Aggregate HDL Offer Curves
Notes: On 8/13 ~1000MW of quick-starts were priced at $1500-$1650 Vs $75 on 8/12 over peak.

## Slide 12: DAM vs. RTM Price Convergence

## Slide 13: MCPC vs. ORDC Price Adder Convergence

## Slide 14
Appendix
August 6, 2015 – August 13, 2015
All Hours

## Slide 15: Reserves

## Slide 16: Reserves and Outages

## Slide 17: All Reserves and Prices

## Slide 18: System Capacity