## Slide 1
2014 & 2015 Unannounced Unit Testing Summary
ERCOT
ROS
February 4th, 2016

## Slide 2: 2014 & 2015 Unannounced Unit Testing Summary
Chart: Capacity Testing Results for 01/01/2014 to 12/31/2015
| HSL Reached and Sustained | HSL Reached but Not Sustained | HSL Not Reached | HSL Not Reached and Not Sustained
CapTestSeries | 166 | 29 | 4 | 54
% of Unit Tests (253 tests)

## Slide 3: 2014 & 2015 Unannounced Unit Testing Summary
Unannounced Resource Capacity Testing Summary |  |  |  |  |  |  | 
From 01/01/2014 to 12/31/2015 |  |  |  |  |  |  | 
Resources Tested: | 253 |  |  |  |  |  | 
Distinct Resources Tested: | 92 |  |  |  |  |  | 
Distinct QSE's Tested: | 62 |  |  |  |  |  | 
Capacity of Resources Tested: | 107890 |  |  |  |  |  | 
Resources Passed: |  | 166 | Resources Failed: |  | 87 |  | 
Cap. of Resources Passed: |  | 70711 |  | Cap. Of Resources Failed: | 37179 |  | 
HSL Reached and Sustained: |  | 166 |  |  |  |  | 
HSL Not Reached: |  |  |  |  | 4 |  | 
HSL Not Reached and Not Sustained: |  |  |  |  | 54 |  | 
HSL Reached but Not Sustained: |  |  |  |  | 29 |  | 
Total MW Capacity Excess of Passed Resources: |  |  |  | 785.3 |  |  | 
Total MW Capacity Shortfall of Failed Resources: |  |  |  | -456.74 |  |  | 
Net MW Capacity Excess of All Resources: |  |  |  | 328.56 |  |  | 
0.4%

## Slide 4: 2014 & 2015 Unannounced Unit Testing Summary
Unannounced Resource Capacity Testing Summary |  |  |  |  |  |  | 
From 01/01/2014 to 12/31/2015 |  |  |  |  |  |  | 
Resources Tested: | 253 |  |  |  |  |  | 
Distinct Resources Tested: | 92 |  |  |  |  |  | 
Distinct QSE's Tested: | 62 |  |  |  |  |  | 
Capacity of Resources Tested: | 107890 |  |  |  |  |  | 
Resources Passed: |  | 166 | Resources Failed: |  | 87 |  | 
Cap. of Resources Passed: |  | 70711 |  | Cap. Of Resources Failed: | 37179 |  | 
HSL Reached and Sustained: |  | 166 |  |  |  |  | 
HSL Not Reached: |  |  |  |  | 4 |  | 
HSL Not Reached and Not Sustained: |  |  |  |  | 54 |  | 
HSL Reached but Not Sustained: |  |  |  |  | 29 |  | 
Total MW Capacity Excess of Passed Resources: |  |  |  | 785.3 |  |  | 
Total MW Capacity Shortfall of Failed Resources: |  |  |  | -456.74 |  |  | 
Net MW Capacity Excess of All Resources: |  |  |  | 328.56 |  |  | 
Net Tested MW Actually Higher than Telemetered HSLs

## Slide 5: 2014 & 2015 Unannounced Unit Testing Summary
Chart: Capacity Testing Results by Ambient Temperature for 1/01/2014 to 12/31/2015
| T <= 85 | 85 < T <= 95 | 95 < T
Pass | 80 | 77 | 9
Fail | 32 | 47 | 8
Capacity Shortfall (T > 95) | 
Excess | 44
Shortfall | -36.54
Net | 7.46
Notes: T>95(6,882 MW), 85<T<=95 (49,821 MW), T<=85 (51,187 MW)

## Slide 6: Summer 2014 & 2015 Unannounced Unit Testing Summary
Chart: Capacity Testing Results for 01/01/2014 to 12/31/2015
Chart: Capacity Testing Results for Summer 2014 & Summer 2015
| HSL Reached and Sustained | HSL Reached but Not Sustained | HSL Not Reached | HSL Not Reached and Not Sustained
CapTestSeries | 114 | 22 | 4 | 39
% of Unit Tests (179 tests)

## Slide 7: Summer 2014 & 2015 Unannounced Unit Testing Summary
Unannounced Resource Capacity Testing Summary |  |  |  |  |  |  | 
Summer 2014 & Summer 2015 (June - September) |  |  |  |  |  |  | 
Resources Tested: | 179 |  |  |  |  |  | 
Distinct Resources Tested: | 84 |  |  |  |  |  | 
Distinct QSE's Tested: | 55 |  |  |  |  |  | 
Capacity of Resources Tested: | 75232 |  |  |  |  |  | 
Resources Passed: |  | 114 | Resources Failed: |  | 65 |  | 
Cap. of Resources Passed: |  | 47090 |  | Cap. Of Resources Failed: | 28142 |  | 
HSL Reached and Sustained: |  | 114 |  |  |  |  | 
HSL Not Reached: |  |  |  |  | 4 |  | 
HSL Not Reached and Not Sustained: |  |  |  |  | 39 |  | 
HSL Reached but Not Sustained: |  |  |  |  | 22 |  | 
Total MW Capacity Excess of Passed Resources: |  |  |  | 547.4 |  |  | 
Total MW Capacity Shortfall of Failed Resources: |  |  |  | -361.04 |  |  | 
Net MW Capacity Excess of All Resources: |  |  |  | 186.36 |  |  | 
0.5%

## Slide 8: Summer 2014 & 2015 Unannounced Unit Testing Summary
Unannounced Resource Capacity Testing Summary |  |  |  |  |  |  | 
Summer 2014 & Summer 2015 (June - September) |  |  |  |  |  |  | 
Resources Tested: | 179 |  |  |  |  |  | 
Distinct Resources Tested: | 84 |  |  |  |  |  | 
Distinct QSE's Tested: | 55 |  |  |  |  |  | 
Capacity of Resources Tested: | 75232 |  |  |  |  |  | 
Resources Passed: |  | 114 | Resources Failed: |  | 65 |  | 
Cap. of Resources Passed: |  | 47090 |  | Cap. Of Resources Failed: | 28142 |  | 
HSL Reached and Sustained: |  | 114 |  |  |  |  | 
HSL Not Reached: |  |  |  |  | 4 |  | 
HSL Not Reached and Not Sustained: |  |  |  |  | 39 |  | 
HSL Reached but Not Sustained: |  |  |  |  | 22 |  | 
Total MW Capacity Excess of Passed Resources: |  |  |  | 547.4 |  |  | 
Total MW Capacity Shortfall of Failed Resources: |  |  |  | -361.04 |  |  | 
Net MW Capacity Excess of All Resources: |  |  |  | 186.36 |  |  | 
Net Tested MW Actually Higher than Telemetered HSLs

## Slide 9: Summer 2014 & 2015 Unannounced Unit Testing Summary
Chart: Capacity Testing Results by Ambient Temperature for Summer 2014 & Summer 2015
| T <= 85 | 85 < T <= 95 | 95 < T
Pass | 35 | 70 | 9
Fail | 14 | 44 | 7
Capacity Shortfall (T > 95) | 
Excess | 44
Shortfall | -35.54
Net | 8.46
Notes: T>95(6,588 MW), 85<T<=95 (46,062 MW), T<=85 (22,582 MW)

## Slide 10: Summary
ERCOT conducted 253 unannounced tests in 2014 and 2015.
  Passed tests exceeded HSLs after compensating for failed tests by 328 MW
  Average error for each unit was excess of 1.29 MW
Of the 253 tests, 179 tests were conducted during the summer months (June through September)
  Passed tests exceeded HSLs after compensating for failed tests by 186 MW
  Average error for each unit was excess of 1.03 MW
  Of the 179 tests conducted during summer, 16 tests were conducted when temperature was above 95 F
  There were only 16 tests for temperature greater than 95 F
  Passed tests exceeded HSLs after compensating for failed tests by 8.46 MW
  Average error for each unit was excess of 0.53 MW

## Slide 11: Recommendation
  Based on the review of unannounced tests;
  ERCOT suggests not discounting Resources HSLs (RDF = 1) for temperature below 95 F
  ERCOT also suggests that for temperature greater than 95 F, we continue to discount HSLs, but only by 1% (RDF=0.99)
  ERCOT will procure additional RRS equivalent to 1% of RDF during those hours where temperature is estimated to be higher than 95 F
    Details about the method will be captured in the Ancillary Service Methodology
  ERCOT will perform this analysis annually to see whether or not HSLs should be discounted.