## Slide 1
Multi-Interval Real-Time Market (MIRTM) Updates
SAWG
Sean Chang
Market Analysis
February 22, 2016
ERCOT Public
Version 0.9.3

## Slide 2: Table of Contents
Introduction
Improving Demand Estimation
Performance of All Intervals
Performance of Intervals where System Lambda >= $75/MWh
Performance on Specific Days
Improving Wind HSL Estimation
Performance of All Intervals
Performance of Intervals where System Lambda >= $75/MWh
Performance on Specific Days
MAE of All Methodologies
Next Steps

## Slide 3: Introduction
1. Improving Demand Estimation
Short-Term Load Forecast (STLF)
Generation-To-Be-Dispatched (GTBD) Calculation Methodology
2. Improving Wind HSL Estimation
Indicative Pricing Tool currently uses a heuristically determined linear equation to estimate wind HSL
Currently, proposal is for MIRTM to use Persistence (HSL telemetry only) to forecast wind HSL
Improvements to linear regression was devised to show potential improvement in short-term wind HSL estimation

## Slide 4
Improving Demand Estimation

## Slide 5: Short Term Load Forecast (STLF)
Both STLFs use weather and calendar variables as basic inputs.
Current STLF (Legacy system in the EMMS)
  Based on regression similar day model using lagged load values as well as lagged load from 24 hours ago of a similar day
New STLF (Blended Model)
  First 15 minutes is based on a regression model using lagged load values (forecast of total MW for a weather zone)
  Next 45+ minutes is based on a regression model of ramp rates (forecast of total MW change from last actual value)
See May 2015 SAWG meeting page for previous presentation: http://www.ercot.com/calendar/2015/5/27/55033-SAWG

## Slide 6: Improving Demand Estimation
A new methodology for calculating GTBD of MIRTM intervals has been found to be an improvement over current methodology
Applying Look-Ahead SCED methodology:
Modified methodology for MIRTM:
TelemMW0 = Sum of Telemetered Gen output at MIRTM Run time
i = 5-Minute MIRTM Intervals Within Study Window
(ex: i=6 represents 30 Min. Ahead)

## Slide 7: Improving Demand Estimation
Both the current STLF and new STLF are used in the analysis along with the modified methodology for four combinations:
  MIRTM GTBD with current STLF
  MIRTM GTBD with new STLF
  MIRTM GTBD Modified with current STLF
  MIRTM GTBD Modified with new STLF
The calculated MIRTM GTBD errors are benchmarked using Estimated – Reference where Reference is:
  First interval (i=1): Actual SCED GTBD
  Intervals 2 – 6 (i=2…6): Sum of generator output at end of SCED interval

## Slide 8
MIRTM Demand Estimation Performance
July 1, 2015 – December 31, 2015
All Intervals

## Slide 9: MAE of Estimated GTBD vs. Reference

## Slide 10: MAE of Estimated GTBD vs. Reference

## Slide 11: Standard Deviation of Estimated GTBD vs. Reference

## Slide 12: Standard Deviation of Estimated GTBD vs. Reference

## Slide 13: Mean of Estimated GTBD vs. Reference

## Slide 14: Mean of Estimated GTBD vs. Reference

## Slide 15: MIRTM GTBD Error by Reference (Interval = 6)

## Slide 16: MIRTM GTBD Error by Reference (Interval = 5)

## Slide 17: MIRTM GTBD Error by Reference (Interval = 4)

## Slide 18: MIRTM GTBD Error by Reference (Interval = 3)

## Slide 19: MIRTM GTBD Error by Reference (Interval = 2)

## Slide 20: MIRTM GTBD Error by Reference (Interval = 1)

## Slide 21: MIRTM GTBD Error by Delivery Time (Interval = 6)

## Slide 22: MIRTM GTBD Error by Delivery Time (Interval = 5)

## Slide 23: MIRTM GTBD Error by Delivery Time (Interval = 4)

## Slide 24: MIRTM GTBD Error by Delivery Time (Interval = 3)

## Slide 25: MIRTM GTBD Error by Delivery Time (Interval = 2)

## Slide 26: MIRTM GTBD Error by Delivery Time (Interval = 1)

## Slide 27
MIRTM Demand Estimation Performance
July 1, 2015 – December 31, 2015
547 Intervals when System Lambda >= $75/MWh

## Slide 28: MAE of Estimated GTBD vs. Reference

## Slide 29: MAE of Estimated GTBD vs. Reference
For intervals 4-6, we are investigating why the current STLF performs better than the new STLF for the high price intervals using the modified methodology.

## Slide 30: Standard Deviation of Estimated GTBD vs. Reference

## Slide 31: Standard Deviation of Estimated GTBD vs. Reference

## Slide 32: Mean of Estimated GTBD vs. Reference

## Slide 33: Mean of Estimated GTBD vs. Reference

## Slide 34: MIRTM GTBD Error by Reference (Interval = 6)

## Slide 35: MIRTM GTBD Error by Reference (Interval = 5)

## Slide 36: MIRTM GTBD Error by Reference (Interval = 5)

## Slide 37: MIRTM GTBD Error by Reference (Interval = 4)

## Slide 38: MIRTM GTBD Error by Reference (Interval = 3)

## Slide 39: MIRTM GTBD Error by Reference (Interval = 2)

## Slide 40: MIRTM GTBD Error by Reference (Interval = 1)

## Slide 41: MIRTM GTBD Error by Delivery Time (Interval = 6)

## Slide 42: MIRTM GTBD Error by Delivery Time (Interval = 5)

## Slide 43: MIRTM GTBD Error by Delivery Time (Interval = 4)

## Slide 44: MIRTM GTBD Error by Delivery Time (Interval = 3)

## Slide 45: MIRTM GTBD Error by Delivery Time (Interval = 2)

## Slide 46: MIRTM GTBD Error by Delivery Time (Interval = 1)

## Slide 47: MIRTM Demand Estimation Performance on Specific Days
In the following slides, the estimation performance of the following specific days are analyzed:
  August 13, 2015
  October 23, 2015
  November 11, 2015
  November 27, 2015
For each of these four dates, the two highest priced SCED intervals are further examined.
The LDL-HDL energy offer curve is shown along with the effects that the New STLF and Modified GTBD Methodology have on the resulting price based the curve.
This is not the actual LDL-HDL curve MIRTM would use for each interval (i). It is the LDL-HDL curve at the SCED snapshot (i =1) simply to give a representation of how sensitive the energy offer curve is to differing GTBD values.

## Slide 48
MIRTM Demand Estimation Performance
August 13, 2015

## Slide 49: MIRTM GTBD Error on August 13, 2015 (Interval = 6)

## Slide 50: MIRTM GTBD Error on August 13, 2015 (Interval = 5)

## Slide 51: MIRTM GTBD Error on August 13, 2015 (Interval = 4)

## Slide 52: MIRTM GTBD Error on August 13, 2015 (Interval = 3)

## Slide 53: MIRTM GTBD Error on August 13, 2015 (Interval = 2)

## Slide 54: MIRTM GTBD Error on August 13, 2015 (Interval = 1)

## Slide 55: LDL to HDL Energy Offer Curve from August 13, 2015 15:05 SCED Run
Notes: GTBD Estimation uses New STLF and Modified GTBD Methodology
No DC tie change

## Slide 56: LDL to HDL Energy Offer Curve from August 13, 2015 15:05 SCED Run
Notes: GTBD Estimation uses New STLF and Modified GTBD Methodology
No DC tie change

## Slide 57: LDL to HDL Energy Offer Curve from August 13, 2015 15:05 SCED Run
At SCED Snapshot:
1.3 * 95 = 123.5 MW Load Ramp Component
0.5 * 156 = 78 MW Regulation Up Component
Recall that SCED GTBD =
= Sum of Generator Output (at snapshot)
+ K3 * Predicted Load Ramp
+ K4 * Regulation Deployed
Notes: GTBD Estimation uses New STLF and Modified GTBD Methodology
No DC tie change

## Slide 58: LDL to HDL Energy Offer Curve from August 13, 2015 15:05 SCED Run
Notes: GTBD Estimation uses New STLF and Modified GTBD Methodology
No DC tie change

## Slide 59: LDL to HDL Energy Offer Curve from August 13, 2015 15:05 SCED Run
At 15:10:
-22 MW Regulation Down Deployed
Notes: GTBD Estimation uses New STLF and Modified GTBD Methodology
No DC tie change

## Slide 60: LDL to HDL Energy Offer Curve from August 13, 2015 15:05 SCED Run
Notes: GTBD Estimation uses New STLF and Modified GTBD Methodology
No DC tie change

## Slide 61: LDL to HDL Energy Offer Curve from August 13, 2015 15:05 SCED Run
Notes: GTBD Estimation uses New STLF and Modified GTBD Methodology
No DC tie change

## Slide 62: LDL to HDL Energy Offer Curve from August 13, 2015 15:05 SCED Run
Notes: GTBD Estimation uses New STLF and Modified GTBD Methodology
No DC tie change

## Slide 63: LDL to HDL Energy Offer Curve from August 13, 2015 15:05 SCED Run
Notes: GTBD Estimation uses New STLF and Modified GTBD Methodology
No DC tie change

## Slide 64: LDL to HDL Energy Offer Curve from August 13, 2015 15:05 SCED Run
Notes: GTBD Estimation uses New STLF and Modified GTBD Methodology
No DC tie change

## Slide 65: LDL to HDL Energy Offer Curve from August 13, 2015 15:05 SCED Run
At SCED Snapshot:
1.3 * 95 = 123.5 MW Load Ramp Component
0.5 * 156 = 78 MW Regulation Up Component
Recall that SCED GTBD =
= Sum of Generator Output (at snapshot)
+ K3 * Predicted Load Ramp
+ K4 * Regulation Deployed
At 15:10:
-22 MW Regulation Down Deployed
Notes: GTBD Estimation uses New STLF and Modified GTBD Methodology
No DC tie change

## Slide 66: LDL to HDL Energy Offer Curve on August 13, 2015 15:55 SCED Run
At SCED Snapshot:
1.3 * 17 = 22.1 MW Load Ramp Component
0.5 * 211 = 105.5 MW Regulation Up Component
At 16:00:
56 MW Regulation Up Deployed
Notes: GTBD Estimation uses New STLF and Modified GTBD Methodology
No DC tie change

## Slide 67
MIRTM Demand Estimation Performance
October 23, 2015

## Slide 68: MIRTM GTBD Error on October 23, 2015 (Interval = 6)

## Slide 69: MIRTM GTBD Error on October 23, 2015 (Interval = 5)

## Slide 70: MIRTM GTBD Error on October 23, 2015 (Interval = 4)

## Slide 71: MIRTM GTBD Error on October 23, 2015 (Interval = 3)

## Slide 72: MIRTM GTBD Error on October 23, 2015 (Interval = 2)

## Slide 73: MIRTM GTBD Error on October 23, 2015 (Interval = 1)

## Slide 74: LDL to HDL Energy Offer Curve on October 23, 2015 06:10 SCED Run
At SCED Snapshot:
1.2 * 409 = 490.8 MW Load Ramp Component
0.4 * 660 = 264 MW Regulation Up Component
At 06:15:
208 MW Regulation Up Deployed
Notes: GTBD Estimation uses New STLF and Modified GTBD Methodology
+62MW DC import change

## Slide 75: LDL to HDL Energy Offer Curve on October 23, 2015 06:35 SCED Run
At SCED Snapshot:
1.2 * 308 = 369.6 MW Load Ramp Component
0.4 * 173 = 69.2 MW Regulation Up Component
At 06:40:
-70 MW Regulation Down Deployed
Notes: GTBD Estimation uses New STLF and Modified GTBD Methodology
-46MW DC export change

## Slide 76
MIRTM Demand Estimation Performance
November 11, 2015

## Slide 77: MIRTM GTBD Error on November 11, 2015 (Interval = 6)

## Slide 78: MIRTM GTBD Error on November 11, 2015 (Interval = 5)

## Slide 79: MIRTM GTBD Error on November 11, 2015 (Interval = 4)

## Slide 80: MIRTM GTBD Error on November 11, 2015 (Interval = 3)

## Slide 81: MIRTM GTBD Error on November 11, 2015 (Interval = 2)

## Slide 82: MIRTM GTBD Error on November 11, 2015 (Interval = 1)

## Slide 83: LDL to HDL Energy Offer Curve on November 11, 2015 17:25 SCED Run
At SCED Snapshot:
1.2 * 321 = 385.2 MW Load Ramp Component
0.3 * 255 = 76.5 MW Regulation Up Component
At 17:30:
-88 MW Regulation Down Deployed
Notes: -25MW DC export change

## Slide 84: LDL to HDL Energy Offer Curve on November 11, 2015 17:35 SCED Run
At SCED Snapshot:
1.2 * 297 = 356.4 MW Load Ramp Component
0.3 * -26 = -7.8 MW Regulation Down Component
At 17:40:
0 MW Regulation Deployed
Notes: -5MW DC export change

## Slide 85
MIRTM Demand Estimation Performance
November 27, 2015

## Slide 86: MIRTM GTBD Error on November 27, 2015 (Interval = 6)

## Slide 87: MIRTM GTBD Error on November 27, 2015 (Interval = 5)

## Slide 88: MIRTM GTBD Error on November 27, 2015 (Interval = 4)

## Slide 89: MIRTM GTBD Error on November 27, 2015 (Interval = 3)

## Slide 90: MIRTM GTBD Error on November 27, 2015 (Interval = 2)

## Slide 91: MIRTM GTBD Error on November 27, 2015 (Interval = 1)

## Slide 92: LDL to HDL Energy Offer Curve on November 27, 2015 16:55 SCED Run
At SCED Snapshot:
1.2 * 77 = 92.4 MW Load Ramp Component
0.3 * 136 = 40.8 MW Regulation Up Component
At 17:00:
-129 MW Regulation Down Deployed
Notes: -34MW DC export change

## Slide 93: LDL to HDL Energy Offer Curve on November 27, 2015 17:40 SCED Run
At SCED Snapshot:
0.3 * -19 = -5.7 MW Regulation Down Component
1.2 * 63 = 75.6 MW Load Ramp Component
At 17:45:
-85 MW Regulation Down Deployed
Notes: +65 DC import change

## Slide 94
Improving Wind HSL Estimation

## Slide 95: Improving Wind HSL Estimation in MIRTM
Applying Look-Ahead SCED Implementation
t = Current Time
TelemHSL = Current telemetered HSL
STWPF = AWS Short-Term wind Power Forecast
Current Look-Ahead SCED coefficients:
Coefficients using Persistence:
New coefficients calculated using ARIMA (4,0,0) autoregressive model on 2014 wind:
Notes: Performance is calculated using system-wide wind. Actual implementation would require each unit to be treated separate. Further work is being done.

## Slide 96
Wind Estimation Performance
January 1, 2015 – December 31, 2015
All Intervals

## Slide 97: MAE of Estimated Wind HSL vs. Actual Wind HSL

## Slide 98: MAE of Estimated Wind HSL vs. Actual Wind HSL

## Slide 99: Standard Deviation of Estimated Wind HSL vs. Actual Wind HSL

## Slide 100: Standard Deviation of Estimated Wind HSL vs. Actual Wind HSL

## Slide 101: Mean of Estimated Wind HSL vs. Actual Wind HSL

## Slide 102: Mean of Estimated Wind HSL vs. Actual Wind HSL

## Slide 103: MIRTM Wind HSL Error by Actual Wind HSL (Interval = 6)

## Slide 104: MIRTM Wind HSL Error by Actual Wind HSL (Interval = 5)

## Slide 105: MIRTM Wind HSL Error by Actual Wind HSL (Interval = 4)

## Slide 106: MIRTM Wind HSL Error by Actual Wind HSL (Interval = 3)

## Slide 107: MIRTM Wind HSL Error by Actual Wind HSL (Interval = 2)

## Slide 108: MIRTM Wind HSL Error by Actual Wind HSL (Interval = 1)

## Slide 109: MIRTM Wind HSL Error by Delivery Time (Interval = 6)

## Slide 110: MIRTM Wind HSL Error by Delivery Time (Interval = 5)

## Slide 111: MIRTM Wind HSL Error by Delivery Time (Interval = 4)

## Slide 112: MIRTM Wind HSL Error by Delivery Time (Interval = 3)

## Slide 113: MIRTM Wind HSL Error by Delivery Time (Interval = 2)

## Slide 114: MIRTM Wind HSL Error by Delivery Time (Interval = 1)

## Slide 115
MIRTM Wind HSL Estimation Performance
January 1, 2015 – December 31, 2015
1160 Intervals when System Lambda >= $75/MWh

## Slide 116: MAE of Estimated Wind HSL vs. Actual Wind HSL

## Slide 117: MAE of Estimated Wind HSL vs. Actual Wind HSL

## Slide 118: Standard Deviation of Estimated Wind HSL vs. Actual Wind HSL

## Slide 119: Standard Deviation of Estimated Wind HSL vs. Actual Wind HSL

## Slide 120: Mean of Estimated Wind HSL vs. Actual Wind HSL

## Slide 121: Mean of Estimated Wind HSL vs. Actual Wind HSL

## Slide 122: MIRTM Wind HSL Error by Actual Wind HSL (Interval = 6)

## Slide 123: MIRTM Wind HSL Error by Actual Wind HSL (Interval = 5)

## Slide 124: MIRTM Wind HSL Error by Actual Wind HSL (Interval = 4)

## Slide 125: MIRTM Wind HSL Error by Actual Wind HSL (Interval = 3)

## Slide 126: MIRTM Wind HSL Error by Actual Wind HSL (Interval = 2)

## Slide 127: MIRTM Wind HSL Error by Actual Wind HSL (Interval = 1)

## Slide 128: MIRTM Wind HSL Error by Delivery Time (Interval = 6)

## Slide 129: MIRTM Wind HSL Error by Delivery Time (Interval = 5)

## Slide 130: MIRTM Wind HSL Error by Delivery Time (Interval = 4)

## Slide 131: MIRTM Wind HSL Error by Delivery Time (Interval = 3)

## Slide 132: MIRTM Wind HSL Error by Delivery Time (Interval = 2)

## Slide 133: MIRTM Wind HSL Error by Delivery Time (Interval = 1)

## Slide 134: MIRTM Wind HSL Estimation Performance on Specific Days
In the following slides, the estimation performance of the following specific days are analyzed:
  August 13, 2015
  October 23, 2015
  November 11, 2015
  November 27, 2015
Notes: The effect of improving wind HSL estimation can be approximated by shifting the LDL-HDL energy offer curve, assuming dispatch does not change. They were not plotted in this analysis, but the relative magnitude of impact can be compared to the MIRTM Demand Estimation energy offer curve slides.

## Slide 135
MIRTM Wind HSL Estimation Performance
August 13, 2015
Notes: The effect of improving wind HSL estimation can be observed by shifting the LDL-HDL curve, assuming dispatch did not change. I wasn’t able to show sensitivity graphs on the energy offer curve since it was a bit more complicated.

## Slide 136: MIRTM Wind HSL on August 13, 2015

## Slide 137: MIRTM Wind HSL Error on August 13, 2015 (Interval = 6)

## Slide 138: MIRTM Wind HSL Error on August 13, 2015 (Interval = 5)

## Slide 139: MIRTM Wind HSL Error on August 13, 2015 (Interval = 4)

## Slide 140: MIRTM Wind HSL Error on August 13, 2015 (Interval = 3)

## Slide 141: MIRTM Wind HSL Error on August 13, 2015 (Interval = 2)

## Slide 142: MIRTM Wind HSL Error on August 13, 2015 (Interval = 1)

## Slide 143
MIRTM Wind HSL Estimation Performance
October 23, 2015

## Slide 144: MIRTM Wind HSL on October 23, 2015

## Slide 145: MIRTM Wind HSL Error on October 23, 2015 (Interval = 6)

## Slide 146: MIRTM Wind HSL Error on October 23, 2015 (Interval = 5)

## Slide 147: MIRTM Wind HSL Error on October 23, 2015 (Interval = 4)

## Slide 148: MIRTM Wind HSL Error on October 23, 2015 (Interval = 3)

## Slide 149: MIRTM Wind HSL Error on October 23, 2015 (Interval = 2)

## Slide 150: MIRTM Wind HSL Error on October 23, 2015 (Interval = 1)

## Slide 151
MIRTM Wind HSL Estimation Performance
November 11, 2015

## Slide 152: MIRTM Wind HSL on November 11, 2015

## Slide 153: MIRTM Wind HSL Error on November 11, 2015 (Interval = 6)

## Slide 154: MIRTM Wind HSL Error on November 11, 2015 (Interval = 5)

## Slide 155: MIRTM Wind HSL Error on November 11, 2015 (Interval = 4)

## Slide 156: MIRTM Wind HSL Error on November 11, 2015 (Interval = 3)

## Slide 157: MIRTM Wind HSL Error on November 11, 2015 (Interval = 2)

## Slide 158: MIRTM Wind HSL Error on November 11, 2015 (Interval = 1)

## Slide 159
MIRTM Wind HSL Estimation Performance
November 27, 2015

## Slide 160: MIRTM Wind HSL on November 27, 2015

## Slide 161: MIRTM Wind HSL Error on November 27, 2015 (Interval = 6)

## Slide 162: MIRTM Wind HSL Error on November 27, 2015 (Interval = 5)

## Slide 163: MIRTM Wind HSL Error on November 27, 2015 (Interval = 4)

## Slide 164: MIRTM Wind HSL Error on November 27, 2015 (Interval = 3)

## Slide 165: MIRTM Wind HSL Error on November 27, 2015 (Interval = 2)

## Slide 166: MIRTM Wind HSL Error on November 27, 2015 (Interval = 1)

## Slide 167: MAE of All Methodologies

## Slide 168: Next Steps for Forecast data input to MIRTM
Continue maintaining metrics on MIRTM GTBD, Wind HSL forecasting and report to SAWG
  Request feedback on methodology and suggest improvements
For studies use:
  MIRTM GTBD Modified with new STLF
  ARIMA regression coefficients for Wind HSL estimation
Please provide feedback on other ways to present or analyze the data

## Slide 169
Questions?