## Slide 1
Next Steps on Reserve Discount Factor and 2016 Ancillary Service Methodology
ERCOT Staff
Date 02/25/2016

## Slide 2: Update on Unannounced Testing and RDF
  ERCOT presented analysis of 2014 and 2015 Unannounced Testing at 02/04/2015 ROS meeting (see the link below for details).
      http://www.ercot.com/content/wcm/key_documents_lists/77584/07._Results_of_Unannounced_Testing_and_Reserve_Discount_Factor_02022016.pptx
  As a result of this analysis, ERCOT will be recommending changes to the Reserve Discount Factors (RDFs) used in the Physical Responsive Capability (PRC) calculation:
    For temperature below 95 F, do not discount Resources HSLs (RDF = 1).
    For temperature greater than 95F, continue to discount HSLs, but only by 1% (RDF=0.99) instead of current 2% (RDF=0.98).
  This change will be submitted to ROS for approval pursuant to Protocol Section 8.1.1.2 (7)
  ERCOT will recommend to ROS changing the RDF regardless of any changes to AS Methodology for 2016.
  ERCOT will continue to review the unannounced tests annually to see whether the RDFs should be modified in the future.
Notes: 8.1.1.2 (7) ERCOT shall maintain historical records of unannounced Generation Resource test results, using the information contained therein to adjust the Reserve Discount Factor (RDF) subject to the approval of the appropriate TAC subcommittee. ERCOT shall report to the Reliability and Operations Subcommittee (ROS) annually or as requested by ERCOT NODAL ROS the aggregated results of such unannounced testing (excluding retests), including, but not limited to, the number and total capacity of Resources tested, the percentage of Resources that met or exceeded their HSL reported by telemetry, the percentage that failed to meet their HSL reported by telemetry, and the total MW capacity shortfall of those Resources that failed to meet their HSL reported by telemetry.

## Slide 3: Ancillary Service Methodology Changes
  To better align the quantity of Responsive Reserve Service (RRS) procured with PRC calculation, ERCOT will be recommending to procure additional RRS equivalent to the effect of discounting HSLs by the RDF on PRC during those hours when the RDF is expected to be <1.0.
  ERCOT will initiate revisions to the 2016 AS Methodology to reflect the change in RRS procurement quantities for hours when RDF <1.0.
  ERCOT seeks feedback from TAC on its intent to present the proposed change to the 2016 Ancillary Service Methodology to the stakeholders according to the schedule on the following slide.

## Slide 4: Proposed timeline for review of AS Methodology
Date | Stakeholder Group
03/11/2016 | QMWG
03/24/2016 | OWG
04/06/2016 | WMS
04/07/2016 | ROS (also Change to RDF)
04/28/2016 | TAC
06/14/2016 | ERCOT Board
7/1/2016 | Effective July 1, 2016

## Slide 5
Thank You!!