## Summary
Release Date: March 1, 2016
PRELIMINARY
Seasonal Assessment of Resource Adequacy for the ERCOT Region (SARA)
Summer 2016
SUMMARY
The ERCOT Region is expected to have sufficient installed generating capacity to serve forecasted peak demands in the upcoming summer season (June - September 2016).
This preliminary SARA report includes a 70,588 MW summer peak load forecast based on current expectations for average weather. The summer peak load forecast for the final report, to be released in May, will reflect the weather conditions expected at that time. Regarding generation resources, expected new installed capacity additions include 1,068 MW of gas-fired generation (based on summer ratings) and 723 MW of wind with a summer peak capacity contribution of 174 MW. The unit outage forecast is 3,245 MW, developed from historical summer season outage data gathered since the start of the Texas Nodal Market in December 2010.
This SARA report reflects a change in the methodology for calculating the summer peak solar unit capacity. This methodology change was triggered by operational solar capacity registered with ERCOT reaching the 200 MW threshold as specified in ERCOT Nodal Protocol Section 3.2.6.2.2. The summer peak solar capacity contribution percentage is now 80% based on three years of historical summer solar production data, whereas the previous capacity contribution percentage was 100%. The impact of this change is a reduction in total available installed and planned solar capacity from 295 MW to 236 MW.
This SARA report also includes a new scenario that combines an extreme peak load event with low wind output. The expected summer peak capacity for wind is 2,879 MW, equivalent to a 17.3% capacity contribution based on contributions of 12% for non-coastal wind resources and 55% for coastal wind resources. In contrast, the extreme peak load/low wind scenario includes wind peak capacity of 679 MW, equivalent to a 4.1% summer peak capacity contribution. This low wind level is based on a 10th percentile value of wind output over the prior three summer seasons, and is meant to be consistent with the 90th percentile outage value used for the "extreme load/extreme generation outage" scenario.
At this time, ERCOT does not anticipate changes to available generation capacity for the summer season due to compliance with environmental regulations. The final compliance date for the Mercury and Air Toxics Standards (MATS) for coal units with compliance extensions is April 15, 2016. Confidential survey information gathered in December 2015 indicated that coal generators are expected to be compliant with MATS by the compliance date. ERCOT continues to monitor implementation and consults with generation resource owners on their compliance plans for MATS and other environmental regulations.

## Scenarios
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Summer 2016 - Preliminary
Release Date: March 1, 2016
Forecasted Capacity and Demand
|  | Operational Resources (thermal and hydro), MW | 66314.44 | Based on current Seasonal Maximum Sustainable Limits reported through the unit registration process
|  | Switchable Capacity Total, MW | 3496 | Installed capacity of units that can interconnect with other Regions and are available to ERCOT
|  | less Switchable Capacity Unavailable to ERCOT, MW | -300 | Based on survey responses of Switchable Resource owners
|  | Mothball Resources, MW | 805 | Based on seasonal Mothball units plus Probability of Return responses of Mothball Resource owners
|  | Private Use Network Capacity Contribution, MW | 4284 | Average capability of the top 20 hours in the summer peak seasons for the past three years (2012-2014)
|  | Non-Coastal Wind Resources Capacity Contribution, MW | 1690.2 | Based on 12% of installed capacity for non-coastal wind resources per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Coastal Wind Resources Capacity Contribution, MW | 1014.97 | Based on 55% of installed capacity for coastal wind resources per ERCOT Nodal Protocols Section 3.2.6.2.2
|  | Solar Utility-Scale, Peak Average Capacity Contribution, MW | 230.16 | Based on 80% of rated capacity for solar resources per Nodal Protocols Section 3.2.6.2.2
|  | RMR Resources to be under Contract, MW | 0 | No RMR Resources currently under contract
|  | Non-Synchronous Ties Capacity Contribution, MW | 577 | Average capability of the top 20 hours in the summer peak seasons for the past three years (2012-2014)
|  | Planned Resources (not wind) with signed IA and Air Permit, MW | 1068.4 | Based on in-service dates provided by developers of generation resources
|  | Planned Non-Coastal Wind with signed IA , MW | 62.556 | Based on in-service dates provided by developers of generation resources and 12% of installed capacity for non-coastal wind resources
|  | Planned Coastal Wind with signed IA , MW | 111.1 | Based on in-service dates provided by developers of generation resources and 55% of installed capacity for coastal wind resources
|  | Planned Solar Utility-Scale with signed IA, MW | 5.92 | Based on 80% of rated capacity for solar resources per Nodal Protocols Section 3.2.6.2.2
| [a] Total Resources, MW |  | 79353.826
| [b] Peak Demand, MW |  | 70588 | Based on normal weather from 2002-2014
| [c] Reserve Capacity [a - b], MW |  | 8765.826
Range of Potential Risks
|  |  | Forecasted Summer Season Peak Load | Extreme Load / Typical Generation Outages | Extreme Load / Low Wind Output | Extreme Load / Extreme Generation Outages
|  | Seasonal Load Adjustment |  | 2754 | 2754 | 2754 | Based on extreme weather forecast using 2011 weather data.
|  | Typical Maintenance Outages | 347 | 347 | 347 | 347 | Based on historical average of planned outages for June through September weekdays (starting in August 2010).
|  | Typical Forced Outages, Thermal | 2898 | 2898 | 2898 | 2898 | Based on historical average of forced outages for June through September weekdays (starting in August 2010).
|  | 90th Percentile Forced Outages, Thermal | 0 | 0 | 0 | 1831 | Based on historical forced outages assuming a 90% confidence interval
|  | Low Wind Output Adjustment | 0 | 0 | 2200 | 0 | Based on the 10th percentile of wind output associated with the 100 highest Net Load hours (Load minus wind output) for the 2013-2015 summer Peak Load seasons; this wind output level is 679 MW.
| [d] Total Uses of Reserve Capacity |  | 3245 | 5999 | 8199 | 7830
| [e] Capacity Available for Operating Reserves (c-d), MW |  | 5520.826 | 2766.826 | 566.826 | 935.826
Less than 2,300 MW indicates risk of EEA1

## Summer_Capacity
Unit Capacities - Summer
| UNIT NAME | GENERATION INTERCONNECTION PROJECT CODE | UNIT CODE | COUNTY | FUEL | ZONE | START YEAR | CAPACITY (MW)
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1205
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1195
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1286
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1295
8 | BIG BROWN U1 |  | BBSES_UNIT1 | FREESTONE | COAL | NORTH | 1971 | 606
9 | BIG BROWN U2 |  | BBSES_UNIT2 | FREESTONE | COAL | NORTH | 1972 | 602
10 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 660
11 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 604
12 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 599
13 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 437
14 | GIBBONS CREEK U1 |  | GIBCRK_GIB_CRG1 | GRIMES | COAL | NORTH | 1983 | 470
15 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560
16 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 775
17 | J T DEELY U1 |  | CALAVERS_JTD1 | BEXAR | COAL | SOUTH | 1977 | 420
18 | J T DEELY U2 |  | CALAVERS_JTD2 | BEXAR | COAL | SOUTH | 1978 | 420
19 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 831
20 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 858
21 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 800
22 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 805
23 | MONTICELLO U1 |  | MNSES_UNIT1 | TITUS | COAL | NORTH | 1974 | 535
24 | MONTICELLO U2 |  | MNSES_UNIT2 | TITUS | COAL | NORTH | 1975 | 535
25 | MONTICELLO U3 |  | MNSES_UNIT3 | TITUS | COAL | NORTH | 1978 | 795
26 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 840
27 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 825
28 | OKLAUNION U1 |  | OKLA_OKLA_G1 | WILBARGER | COAL | WEST | 1986 | 650
29 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 391
30 | SANDOW U5 |  | SD5SES_UNIT5 | MILAM | COAL | SOUTH | 2010 | 600
31 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 970
32 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 156
33 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 156
34 | W A PARISH U5 |  | WAP_WAP_G5 | FT. BEND | COAL | HOUSTON | 1977 | 659
35 | W A PARISH U6 |  | WAP_WAP_G6 | FT. BEND | COAL | HOUSTON | 1978 | 658
36 | W A PARISH U7 |  | WAP_WAP_G7 | FT. BEND | COAL | HOUSTON | 1980 | 577
37 | W A PARISH U8 |  | WAP_WAP_G8 | FT. BEND | COAL | HOUSTON | 1982 | 610
38 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS | SOUTH | 2000 | 149
39 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS | SOUTH | 2000 | 149
40 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS | SOUTH | 2000 | 160
41 | BARNEY M DAVIS REPOWER CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS | COASTAL | 2010 | 157
42 | BARNEY M DAVIS REPOWER CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS | COASTAL | 2010 | 157
43 | BARNEY M DAVIS REPOWER STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS | COASTAL | 1976 | 319
44 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS | SOUTH | 2002 | 150
45 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS | SOUTH | 2002 | 150
46 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS | SOUTH | 2002 | 233
47 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS | NORTH | 2000 | 148.9
48 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS | NORTH | 2001 | 81.4
49 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS | NORTH | 2000 | 148.9
50 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS | NORTH | 2001 | 150.2
51 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS | NORTH | 2009 | 214.9
52 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS | HOUSTON | 2003 | 166
53 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS | HOUSTON | 2003 | 166
54 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS | HOUSTON | 2003 | 270
55 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS | WEST | 1987 | 75
56 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS | WEST | 1987 | 75
57 | CALENERGY-FALCON SEABOARD STG 3 |  | FLCNS_UNIT3 | HOWARD | GAS | WEST | 1988 | 70
58 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS | HOUSTON | 2009 | 163
59 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS | HOUSTON | 2009 | 163
60 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS | HOUSTON | 2009 | 178
61 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS | SOUTH | 2007 | 70
62 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS | SOUTH | 2007 | 62
63 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS | SOUTH | 2007 | 101
64 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS | SOUTH | 2008 | 69
65 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS | SOUTH | 2008 | 63
66 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS | SOUTH | 2008 | 103
67 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS | HOUSTON | 2008 | 172
68 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS | HOUSTON | 2008 | 164
69 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS | HOUSTON | 2008 | 164
70 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS | HOUSTON | 2008 | 146
71 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS | HOUSTON | 2002 | 181
72 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS | HOUSTON | 2002 | 193
73 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS | HOUSTON | 2002 | 181
74 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS | HOUSTON | 2002 | 193
75 | DEER PARK ENERGY CENTER STG |  | DDPEC_ST1 | HARRIS | GAS | HOUSTON | 2002 | 290
76 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS | HOUSTON | 2014 | 165
77 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS | NORTH | 2002 | 196
78 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS | NORTH | 2002 | 116
79 | FERGUSON REPLACEMENT CTG1 |  | FERGCC_FERGGT1 | LLANO | GAS | SOUTH | 2014 | 161.9
80 | FERGUSON REPLACEMENT CTG2 |  | FERGCC_FERGGT2 | LLANO | GAS | SOUTH | 2014 | 161.9
81 | FERGUSON REPLACEMENT STG |  | FERGCC_FERGST1 | LLANO | GAS | SOUTH | 2014 | 186
82 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS | NORTH | 2003 | 169
83 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS | NORTH | 2003 | 161
84 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS | NORTH | 2003 | 161
85 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS | NORTH | 2003 | 169
86 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS | NORTH | 2003 | 161
87 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS | NORTH | 2003 | 161
88 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS | NORTH | 2003 | 420
89 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS | NORTH | 2003 | 420
90 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS | NORTH | 2002 | 151.6
91 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS | NORTH | 2002 | 151.6
92 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS | NORTH | 2002 | 176.2
93 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS | NORTH | 2002 | 151.7
94 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS | NORTH | 2002 | 151.7
95 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS | NORTH | 2002 | 174.5
96 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS | SOUTH | 2000 | 148
97 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS | SOUTH | 2000 | 148
98 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS | SOUTH | 2000 | 148
99 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS | SOUTH | 2000 | 148
100 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS | SOUTH | 2000 | 197
101 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS | SOUTH | 2000 | 197
102 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS | SOUTH | 2002 | 216
103 | HAYS ENERGY FACILITY CSG 2 |  | HAYSEN_HAYSENG2 | HAYS | GAS | SOUTH | 2002 | 216
104 | HAYS ENERGY FACILITY CSG 3 |  | HAYSEN_HAYSENG3 | HAYS | GAS | SOUTH | 2002 | 225
105 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS | SOUTH | 2002 | 225
106 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS | SOUTH | 2000 | 143
107 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS | SOUTH | 2000 | 143
108 | HIDALGO ENERGY CENTER STG |  | DUKE_DUKE_ST1 | HIDALGO | GAS | SOUTH | 2000 | 172
109 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS | NORTH | 2005 | 150
110 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS | NORTH | 2005 | 150
111 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS | NORTH | 2005 | 295
112 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS | NORTH | 2011 | 150
113 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS | NORTH | 2011 | 150
114 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS | NORTH | 2011 | 295
115 | JOHNSON COUNTY GEN FACILITY CTG |  | TEN_CT1 | JOHNSON | GAS | NORTH | 1997 | 163
116 | JOHNSON COUNTY GEN FACILITY STG |  | TEN_STG | JOHNSON | GAS | NORTH | 1997 | 106
117 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS | NORTH | 2000 | 163
118 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS | NORTH | 2000 | 153
119 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS | NORTH | 2000 | 153
120 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS | NORTH | 2000 | 163
121 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS | NORTH | 2000 | 204
122 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS | NORTH | 2000 | 204
123 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS | SOUTH | 2001 | 170
124 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS | SOUTH | 2001 | 170
125 | LOST PINES POWER STG |  | LOSTPI_LOSTPST1 | BASTROP | GAS | SOUTH | 2001 | 188
126 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS | SOUTH | 2001 | 208.6
127 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS | SOUTH | 2001 | 208.6
128 | MAGIC VALLEY STATION STG |  | NEDIN_NEDIN_G3 | HIDALGO | GAS | SOUTH | 2001 | 253
129 | MIDLOTHIAN ENERGY FACILITY CS 1 |  | MDANP_CT1 | ELLIS | GAS | NORTH | 2001 | 235
130 | MIDLOTHIAN ENERGY FACILITY CS 2 |  | MDANP_CT2 | ELLIS | GAS | NORTH | 2001 | 235
131 | MIDLOTHIAN ENERGY FACILITY CS 3 |  | MDANP_CT3 | ELLIS | GAS | NORTH | 2001 | 235
132 | MIDLOTHIAN ENERGY FACILITY CS 4 |  | MDANP_CT4 | ELLIS | GAS | NORTH | 2001 | 235
133 | MIDLOTHIAN ENERGY FACILITY CS 5 |  | MDANP_CT5 | ELLIS | GAS | NORTH | 2002 | 252
134 | MIDLOTHIAN ENERGY FACILITY CS 6 |  | MDANP_CT6 | ELLIS | GAS | NORTH | 2002 | 252
135 | NUECES BAY REPOWER CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS | COASTAL | 2010 | 157
136 | NUECES BAY REPOWER CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS | COASTAL | 2010 | 157
137 | NUECES BAY REPOWER STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS | COASTAL | 1972 | 319
138 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS | WEST | 2001 | 146.4
139 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS | WEST | 2001 | 143.6
140 | ODESSA-ECTOR POWER CTG 21 |  | OECCS_CT21 | ECTOR | GAS | WEST | 2001 | 141.9
141 | ODESSA-ECTOR POWER CTG 22 |  | OECCS_CT22 | ECTOR | GAS | WEST | 2001 | 137.7
142 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS | WEST | 2001 | 210
143 | ODESSA-ECTOR POWER STG 2 |  | OECCS_UNIT2 | ECTOR | GAS | WEST | 2001 | 210
144 | PANDA SHERMAN POWER CTG1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS | NORTH | 2014 | 196
145 | PANDA SHERMAN POWER CTG2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS | NORTH | 2014 | 195
146 | PANDA SHERMAN POWER STG |  | PANDA_S_SHER1ST1 | GRAYSON | GAS | NORTH | 2014 | 326
147 | PANDA TEMPLE I POWER CTG1 |  | PANDA_T1_TMPL1CT1 | BELL | GAS | NORTH | 2014 | 195
148 | PANDA TEMPLE I POWER CTG2 |  | PANDA_T1_TMPL1CT2 | BELL | GAS | NORTH | 2014 | 195
149 | PANDA TEMPLE I POWER STG |  | PANDA_T1_TMPL1ST1 | BELL | GAS | NORTH | 2014 | 312
150 | PANDA TEMPLE II POWER CTG1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS | NORTH | 2015 | 191.2
151 | PANDA TEMPLE II POWER CTG2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS | NORTH | 2015 | 191.2
152 | PANDA TEMPLE II POWER STG |  | PANDA_T2_TMPL2ST1 | BELL | GAS | NORTH | 2015 | 334.7
153 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS | NORTH | 1989 | 76
154 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS | NORTH | 1989 | 76
155 | PARIS ENERGY CENTER STG |  | TNSKA_STG | LAMAR | GAS | NORTH | 1990 | 87
156 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS | HOUSTON | 2000 | 164
157 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS | HOUSTON | 2000 | 164
158 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS | HOUSTON | 2000 | 167
159 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS | WEST | 2007 | 74
160 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS | WEST | 2007 | 74
161 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS | WEST | 2007 | 98
162 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS | WEST | 2008 | 72
163 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS | WEST | 2008 | 72
164 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS | WEST | 2008 | 98
165 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS | SOUTH | 2002 | 154
166 | RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | GUADALUPE | GAS | SOUTH | 2002 | 154
167 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS | SOUTH | 2002 | 154
168 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS | SOUTH | 2002 | 323
169 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS | SOUTH | 2003 | 50
170 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS | SOUTH | 2003 | 50
171 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS | SOUTH | 2003 | 50
172 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS | SOUTH | 2003 | 40
173 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS | SOUTH | 2004 | 150
174 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS | SOUTH | 2004 | 145
175 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS | COASTAL | 1962 | 20
176 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS | COASTAL | 1996 | 38
177 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS | HOUSTON | 1972 | 57
178 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS | HOUSTON | 1972 | 57
179 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS | HOUSTON | 1972 | 57
180 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS | HOUSTON | 1972 | 57
181 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS | HOUSTON | 1974 | 104
182 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS | HOUSTON | 1972 | 57
183 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS | HOUSTON | 1972 | 57
184 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS | HOUSTON | 1974 | 57
185 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS | HOUSTON | 1974 | 57
186 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS | HOUSTON | 1974 | 104
187 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS | HOUSTON | 2000 | 96.6
188 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS | HOUSTON | 2000 | 96.6
189 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS | HOUSTON | 2000 | 96.6
190 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS | HOUSTON | 2000 | 131.6
191 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS | SOUTH | 2009 | 160
192 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS | SOUTH | 1963 | 125
193 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS | WEST | 1987 | 20
194 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS | WEST | 1987 | 20
195 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS | WEST | 1987 | 20
196 | WICHITA FALLS STG 4 |  | WFCOGEN_UNIT4 | WICHITA | GAS | WEST | 1987 | 17
197 | WISE-TRACTEBEL POWER CTG 1 |  | WCPP_CT1 | WISE | GAS | NORTH | 2004 | 212
198 | WISE-TRACTEBEL POWER CTG 2 |  | WCPP_CT2 | WISE | GAS | NORTH | 2004 | 212
199 | WISE-TRACTEBEL POWER STG 1 |  | WCPP_ST1 | WISE | GAS | NORTH | 2004 | 241
200 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS | NORTH | 2002 | 212.5
201 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS | NORTH | 2002 | 212.5
202 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS | NORTH | 2002 | 280
203 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS | NORTH | 1973 | 18
204 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS | NORTH | 2004 | 45
205 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS | NORTH | 2010 | 47
206 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS | SOUTH | 1989 | 48
207 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS | SOUTH | 1989 | 48
208 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS | SOUTH | 1989 | 48
209 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS | SOUTH | 1989 | 48
210 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS | NORTH | 1990 | 71
211 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS | NORTH | 1990 | 70
212 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS | NORTH | 1990 | 69
213 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS | NORTH | 1990 | 68
214 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS | WEST | 2015 | 147
215 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS | WEST | 2015 | 147
216 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS | HOUSTON | 2009 | 38
217 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS | HOUSTON | 2009 | 38
218 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS | HOUSTON | 2009 | 38
219 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS | HOUSTON | 2009 | 38
220 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS | HOUSTON | 1976 | 46
221 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS | HOUSTON | 1976 | 46
222 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS | HOUSTON | 1976 | 46
223 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS | HOUSTON | 1976 | 58
224 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS | HOUSTON | 1976 | 56
225 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS | HOUSTON | 1976 | 46
226 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_1 | HUNT | GAS | NORTH | 2010 | 8.4
227 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_2 | HUNT | GAS | NORTH | 2010 | 8.4
228 | GREENVILLE IC ENGINE PLANT |  | STEAM_ENGINE_3 | HUNT | GAS | NORTH | 2010 | 8.4
229 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS | SOUTH | 2008 | 90.1
230 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS | SOUTH | 2008 | 87.3
231 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS | SOUTH | 2004 | 45
232 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS | SOUTH | 2004 | 46
233 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS | SOUTH | 2004 | 44
234 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS | SOUTH | 2004 | 46
235 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS | WEST | 1988 | 68
236 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS | WEST | 1988 | 68
237 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS | WEST | 1988 | 68
238 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS | WEST | 1988 | 68
239 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS | WEST | 1988 | 68
240 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS | WEST | 1988 | 67
241 | PEARSALL IC ENGINE PLANT A |  | PEARSAL2_AGR_A | FRIO | GAS | SOUTH | 2012 | 50.6
242 | PEARSALL IC ENGINE PLANT B |  | PEARSAL2_AGR_B | FRIO | GAS | SOUTH | 2012 | 50.6
243 | PEARSALL IC ENGINE PLANT C |  | PEARSAL2_AGR_C | FRIO | GAS | SOUTH | 2012 | 50.6
244 | PEARSALL IC ENGINE PLANT D |  | PEARSAL2_AGR_D | FRIO | GAS | SOUTH | 2012 | 50.6
245 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS | WEST | 1988 | 68
246 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS | WEST | 1988 | 65
247 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS | WEST | 1988 | 68
248 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS | WEST | 1990 | 69
249 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS | WEST | 1990 | 70
250 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS | NORTH | 1994 | 104
251 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS | NORTH | 1994 | 104
252 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS | NORTH | 2001 | 75
253 | SAM RAYBURN CTG 1 |  | RAYBURN_RAYBURG1 | VICTORIA | GAS | SOUTH | 1963 | 11
254 | SAM RAYBURN CTG 2 |  | RAYBURN_RAYBURG2 | VICTORIA | GAS | SOUTH | 1963 | 11
255 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS | HOUSTON | 1995 | 81
256 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS | HOUSTON | 1995 | 81
257 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS | SOUTH | 2001 | 47
258 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS | SOUTH | 2001 | 47
259 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS | SOUTH | 2001 | 47
260 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS | SOUTH | 2001 | 47
261 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS | SOUTH | 2010 | 47
262 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS | SOUTH | 2010 | 47
263 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS | COASTAL | 2004 | 46
264 | T H WHARTON CTG 51 |  | THW_THWGT51 | HARRIS | GAS | HOUSTON | 1975 | 57
265 | T H WHARTON CTG 52 |  | THW_THWGT52 | HARRIS | GAS | HOUSTON | 1975 | 57
266 | T H WHARTON CTG 53 |  | THW_THWGT53 | HARRIS | GAS | HOUSTON | 1975 | 57
267 | T H WHARTON CTG 54 |  | THW_THWGT54 | HARRIS | GAS | HOUSTON | 1975 | 57
268 | T H WHARTON CTG 55 |  | THW_THWGT55 | HARRIS | GAS | HOUSTON | 1975 | 57
269 | T H WHARTON CTG 56 |  | THW_THWGT56 | HARRIS | GAS | HOUSTON | 1975 | 57
270 | T H WHARTON CTG G1 |  | THW_THWGT_1 | HARRIS | GAS | HOUSTON | 1967 | 13
271 | TEXAS GULF SULPHUR |  | TGF_TGFGT_1 | WHARTON | GAS | SOUTH | 1985 | 79
272 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS | SOUTH | 2009 | 48
273 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS | SOUTH | 2009 | 48
274 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS | SOUTH | 2009 | 48
275 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS | SOUTH | 2009 | 47
276 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FT. BEND | GAS | HOUSTON | 1967 | 13
277 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS | SOUTH | 2009 | 44
278 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS | SOUTH | 2009 | 44
279 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS | SOUTH | 2009 | 44
280 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS | SOUTH | 2009 | 44
281 | B M DAVIS STG U1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS | COASTAL | 1974 | 330
282 | CEDAR BAYOU STG U1 |  | CBY_CBY_G1 | CHAMBERS | GAS | HOUSTON | 1970 | 745
283 | CEDAR BAYOU STG U2 |  | CBY_CBY_G2 | CHAMBERS | GAS | HOUSTON | 1972 | 749
284 | DANSBY STG U1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS | NORTH | 1978 | 107
285 | DECKER CREEK STG U1 |  | DECKER_DPG1 | TRAVIS | GAS | SOUTH | 1971 | 315
286 | DECKER CREEK STG U2 |  | DECKER_DPG2 | TRAVIS | GAS | SOUTH | 1978 | 420
287 | GRAHAM STG U1 |  | GRSES_UNIT1 | YOUNG | GAS | WEST | 1960 | 234
288 | GRAHAM STG U2 |  | GRSES_UNIT2 | YOUNG | GAS | WEST | 1969 | 390
289 | GREENS BAYOU STG U5 |  | GBY_GBY_5 | HARRIS | GAS | HOUSTON | 1973 | 371
290 | HANDLEY STG U3 |  | HLSES_UNIT3 | TARRANT | GAS | NORTH | 1963 | 395
291 | HANDLEY STG U4 |  | HLSES_UNIT4 | TARRANT | GAS | NORTH | 1976 | 435
292 | HANDLEY STG U5 |  | HLSES_UNIT5 | TARRANT | GAS | NORTH | 1977 | 435
293 | LAKE HUBBARD STG U1 |  | LHSES_UNIT1 | DALLAS | GAS | NORTH | 1970 | 392
294 | LAKE HUBBARD STG U2 |  | LHSES_UNIT2A | DALLAS | GAS | NORTH | 1973 | 523
295 | MOUNTAIN CREEK STG U6 |  | MCSES_UNIT6 | DALLAS | GAS | NORTH | 1956 | 122
296 | MOUNTAIN CREEK STG U7 |  | MCSES_UNIT7 | DALLAS | GAS | NORTH | 1958 | 118
297 | MOUNTAIN CREEK STG U8 |  | MCSES_UNIT8 | DALLAS | GAS | NORTH | 1967 | 568
298 | O W SOMMERS STG U1 |  | CALAVERS_OWS1 | BEXAR | GAS | SOUTH | 1972 | 420
299 | O W SOMMERS STG U2 |  | CALAVERS_OWS2 | BEXAR | GAS | SOUTH | 1974 | 410
300 | PEARSALL STG U1 |  | PEARSALL_PEARS_1 | FRIO | GAS | SOUTH | 1961 | 19
301 | PEARSALL STG U2 |  | PEARSALL_PEARS_2 | FRIO | GAS | SOUTH | 1961 | 22
302 | PEARSALL STG U3 |  | PEARSALL_PEARS_3 | FRIO | GAS | SOUTH | 1961 | 20
303 | POWERLANE PLANT STG U1 |  | STEAM1A_STEAM_1 | HUNT | GAS | NORTH | 1966 | 20
304 | POWERLANE PLANT STG U2 |  | STEAM_STEAM_2 | HUNT | GAS | NORTH | 1967 | 26
305 | POWERLANE PLANT STG U3 |  | STEAM_STEAM_3 | HUNT | GAS | NORTH | 1978 | 41
306 | R W MILLER STG U1 |  | MIL_MILLERG1 | PALO PINTO | GAS | NORTH | 1968 | 75
307 | R W MILLER STG U2 |  | MIL_MILLERG2 | PALO PINTO | GAS | NORTH | 1972 | 120
308 | R W MILLER STG U3 |  | MIL_MILLERG3 | PALO PINTO | GAS | NORTH | 1975 | 208
309 | RAY OLINGER STG U1 |  | OLINGR_OLING_1 | COLLIN | GAS | NORTH | 1967 | 78
310 | RAY OLINGER STG U2 |  | OLINGR_OLING_2 | COLLIN | GAS | NORTH | 1971 | 107
311 | RAY OLINGER STG U3 |  | OLINGR_OLING_3 | COLLIN | GAS | NORTH | 1975 | 146
312 | SIM GIDEON STG U1 |  | GIDEON_GIDEONG1 | BASTROP | GAS | SOUTH | 1965 | 130
313 | SIM GIDEON STG U2 |  | GIDEON_GIDEONG2 | BASTROP | GAS | SOUTH | 1968 | 135
314 | SIM GIDEON STG U3 |  | GIDEON_GIDEONG3 | BASTROP | GAS | SOUTH | 1972 | 336
315 | SPENCER STG U4 |  | SPNCER_SPNCE_4 | DENTON | GAS | NORTH | 1966 | 61
316 | SPENCER STG U5 |  | SPNCER_SPNCE_5 | DENTON | GAS | NORTH | 1973 | 61
317 | STRYKER CREEK STG U1 |  | SCSES_UNIT1A | CHEROKEE | GAS | NORTH | 1958 | 167
318 | STRYKER CREEK STG U2 |  | SCSES_UNIT2 | CHEROKEE | GAS | NORTH | 1965 | 502
319 | TRINIDAD STG U6 |  | TRSES_UNIT6 | HENDERSON | GAS | NORTH | 1965 | 235
320 | V H BRAUNIG STG U1 |  | BRAUNIG_VHB1 | BEXAR | GAS | SOUTH | 1966 | 220
321 | V H BRAUNIG STG U2 |  | BRAUNIG_VHB2 | BEXAR | GAS | SOUTH | 1968 | 230
322 | V H BRAUNIG STG U3 |  | BRAUNIG_VHB3 | BEXAR | GAS | SOUTH | 1970 | 412
323 | W A PARISH STG U1 |  | WAP_WAP_G1 | FT. BEND | GAS | HOUSTON | 1958 | 169
324 | W A PARISH STG U2 |  | WAP_WAP_G2 | FT. BEND | GAS | HOUSTON | 1958 | 169
325 | W A PARISH STG U3 |  | WAP_WAP_G3 | FT. BEND | GAS | HOUSTON | 1961 | 246
326 | W A PARISH STG U4 |  | WAP_WAP_G4 | FT. BEND | GAS | HOUSTON | 1968 | 536
327 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 105
328 | LUFKIN BIOMASS |  | LFBIO_UNIT1 | ANGELINA | BIOMASS | NORTH | 2012 | 45
329 | BIOENERGY AUSTIN WALZEM RD LFG |  | DG_WALZE_4UNITS | BEXAR | BIOMASS | SOUTH | 2002 | 9.8
330 | BIOENERGY TEXAS COVEL GARDENS LFG |  | DG_MEDIN_1UNIT | BEXAR | BIOMASS | SOUTH | 2005 | 9.6
331 | FORT WORTH METHANE LFG |  | DG_RDLML_1UNIT | TARRANT | BIOMASS | NORTH | 2011 | 1.6
332 | GRAND PRAIRIE LFG |  | DG_TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4
333 | MCKINNEY LFG |  | DG_MKNSW_2UNITS | COLLIN | BIOMASS | NORTH | 2011 | 3.2
334 | NELSON GARDENS LFG |  | DG_78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.24
335 | SKYLINE LFG |  | DG_FERIS_4 UNITS | DALLAS | BIOMASS | NORTH | 2007 | 6.4
336 | TRINITY OAKS LFG |  | DG_KLBRG_1UNIT | DALLAS | BIOMASS | NORTH | 2011 | 3.2
337 | VIRIDIS ENERGY-ALVIN LFG |  | DG_AV_DG1 | GALVESTON | BIOMASS | HOUSTON | 2002 | 6.7
338 | VIRIDIS ENERGY-HUMBLE LFG |  | DG_HB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 10
339 | VIRIDIS ENERGY-LIBERTY LFG |  | DG_LB_DG1 | HARRIS | BIOMASS | HOUSTON | 2002 | 3.9
340 | VIRIDIS ENERGY-TRINITY BAY LFG |  | DG_TRN_DG1 | CHAMBERS | BIOMASS | HOUSTON | 2002 | 3.9
341 | WM RENEWABLE-AUSTIN LFG |  | DG_SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4
342 | WM RENEWABLE-DFW GAS RECOVERY LFG |  | DG_BIO2_4UNITS | DENTON | BIOMASS | NORTH | 2009 | 6.4
343 | WM RENEWABLE-BIOENERGY PARTNERS LFG |  | DG_BIOE_2UNITS | DENTON | BIOMASS | NORTH | 1988 | 6.2
344 | WM RENEWABLE-MESQUITE CREEK LFG |  | DG_FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2
345 | WM RENEWABLE-WESTSIDE LFG |  | DG_WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8
346 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2012 | 0
347 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 66070.24
348
349 | Operational Resources (Hydro)
350 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
351 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9
352 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 8
353 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9
354 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 16
355 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 16
356 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 17
357 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 40
358 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 40
359 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12
360 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12
361 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12
362 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29
363 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29
364 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 14
365 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21
366 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20
367 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36
368 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36
369 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 29
370 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 24
371 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 24
372 | ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | TARRANT | HYDRO | NORTH | 2014 | 1.35
373 | EAGLE PASS HYDRO |  | DG_EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 2005 | 9.6
374 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | DG_CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1989 | 6
375 | GUADALUPE BLANCO RIVER AUTH-LAKEWOOD TAP |  | DG_LKWDT_2UNITS | GONZALES | HYDRO | SOUTH | 2031 | 4.8
376 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | DG_MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 2028 | 7.7
377 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | DG_SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 2028 | 3.6
378 | LEWISVILLE HYDRO-CITY OF GARLAND |  | DG_LWSVL_1UNIT | DENTON | HYDRO | NORTH | 1991 | 2.2
379 | Operational Capacity Total (Hydro) | [6 empty] | 555.05
380 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  |  |  |  | 437.2
381
382 | Operational Capacity Unavailable due to Extended Outage or Derate |  | OPERATION_UNAVAIL |  |  |  |  | -193
383 | Operational Capacity Total (Including Hydro) |  | OPERATION_TOTAL |  |  |  |  | 66314.44
384
385 | Operational Resources (Switchable)
386 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS | NORTH | 2003 | 153
387 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS | NORTH | 2003 | 155
388 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS | NORTH | 2003 | 315
389 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS | NORTH | 2003 | 153
390 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS | NORTH | 2003 | 155
391 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS | NORTH | 2003 | 315
392 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS | NORTH | 2000 | 160
393 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS | NORTH | 2000 | 160
394 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS | NORTH | 2000 | 160
395 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS | NORTH | 2000 | 400
396 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS | NORTH | 2001 | 156
397 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS | NORTH | 2001 | 135
398 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS | NORTH | 2001 | 153
399 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS | NORTH | 2001 | 402
400 | FRONTERA GENERATION CTG 1 |  | FRONTERA_FRONTEG1 | HIDALGO | GAS | SOUTH | 1999 | 170
401 | FRONTERA GENERATION CTG 2 |  | FRONTERA_FRONTEG2 | HIDALGO | GAS | SOUTH | 1999 | 170
402 | FRONTERA GENERATION STG |  | FRONTERA_FRONTEG3 | HIDALGO | GAS | SOUTH | 2000 | 184
403 | Switchable Capacity Total | [6 empty] | 3496
404
405 | Switchable Capacity Unavailable to ERCOT |  | SWITCH_UNAVAIL |  | GAS |  |  | -300
406
407 | Available Mothball Capacity based on Seasonal Schedule or Return Probability |  | MOTH_AVAIL |  | COAL |  |  | 805
408
409 | Private-Use Network Capacity Contribution (Top 20 Hours) |  | PUN_CAP_CONT |  | GAS |  |  | 4258
410 | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) | [6 empty] | 26
411
412 | Operational Resources (Wind)
413 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND | SOUTH | 2012 | 99.8
414 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND | NORTH | 2007 | 120
415 | BLUE SUMMIT WIND 5 |  | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND | WEST | 2013 | 9
416 | BLUE SUMMIT WIND 6 |  | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND | WEST | 2013 | 126.4
417 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND | WEST | 2012 | 150
418 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND | PANHANDLE | 2015 | 149.8
419 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND | WEST | 2006 | 120.6
420 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND | WEST | 2007 | 115.5
421 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND | WEST | 2007 | 117
422 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND | WEST | 2008 | 170.2
423 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND | WEST | 2009 | 88
424 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND | WEST | 2009 | 90
425 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND | WEST | 2004 | 114
426 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND | WEST | 2007 | 130.5
427 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND | WEST | 2007 | 120
428 | CAPRICORN RIDGE WIND 1 |  | CAPRIDGE_CR1 | STERLING | WIND | WEST | 2007 | 214.5
429 | CAPRICORN RIDGE WIND 2 |  | CAPRIDGE_CR3 | STERLING | WIND | WEST | 2008 | 186
430 | CAPRICORN RIDGE WIND 3 |  | CAPRIDGE_CR2 | STERLING | WIND | WEST | 2007 | 149.5
431 | CAPRICORN RIDGE WIND 4 |  | CAPRIDG4_CR4 | COKE | WIND | WEST | 2008 | 112.5
432 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND | SOUTH | 2010 | 75
433 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND | SOUTH | 2010 | 75
434 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND | WEST | 2008 | 126.5
435 | DESERT SKY WIND 1 |  | INDNENR_INDNENR | PECOS | WIND | WEST | 2002 | 84
436 | DESERT SKY WIND 2 |  | INDNENR_INDNENR_2 | PECOS | WIND | WEST | 2002 | 76.5
437 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND | WEST | 2008 | 118.7
438 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND | WEST | 2007 | 124.2
439 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND | WEST | 2008 | 80
440 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND | WEST | 2010 | 69.6
441 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND | NORTH | 2014 | 148.6
442 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND | PANHANDLE | 2014 | 107.4
443 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND | PANHANDLE | 2014 | 103.8
444 | GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_WND1 | SCURRY | WIND | WEST | 2003 | 99
445 | GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_WND2 | SCURRY | WIND | WEST | 2003 | 61
446 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND | WEST | 2015 | 150
447 | GREEN PASTURES WIND 2 |  | GPASTURE_WIND_II | BAYLOR | WIND | WEST | 2015 | 150
448 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND | WEST | 2008 | 163.5
449 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND | PANHANDLE | 2015 | 99.9
450 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND | PANHANDLE | 2015 | 100
451 | HORSE HOLLOW WIND 1 |  | H_HOLLOW_WND1 | TAYLOR | WIND | WEST | 2005 | 206.6
452 | HORSE HOLLOW WIND 2 |  | HHOLLOW2_WIND1 | TAYLOR | WIND | WEST | 2006 | 158
453 | HORSE HOLLOW WIND 3 |  | HHOLLOW3_WND_1 | TAYLOR | WIND | WEST | 2006 | 208
454 | HORSE HOLLOW WIND 4 |  | HHOLLOW4_WND1 | TAYLOR | WIND | WEST | 2006 | 108
455 | INADALE WIND |  | INDL_INADALE1 | NOLAN | WIND | WEST | 2008 | 196.6
456 | INDIAN MESA WIND |  | INDNNWP_INDNNWP | PECOS | WIND | WEST | 2001 | 82.5
457 | JAVELINA WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND | SOUTH | 2015 | 19.7
458 | JAVELINA WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND | SOUTH | 2015 | 230
459 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND | PANHANDLE | 2015 | 146.2
460 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND | PANHANDLE | 2015 | 153.6
461 | KEECHI WIND 138 KV JOPLIN |  | KEECHI_U1 | JACK | WIND | NORTH | 2015 | 110
462 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND | WEST | 2001 | 79.3
463 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND | WEST | 2001 | 79.3
464 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND | WEST | 2001 | 40.3
465 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND | WEST | 2001 | 79.3
466 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND | WEST | 2009 | 155
467 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND | NORTH | 2015 | 103.8
468 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND | NORTH | 2015 | 106.3
469 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND | WEST | 2006 | 200
470 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND | WEST | 2007 | 100
471 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND | WEST | 2007 | 100
472 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND | PANHANDLE | 2015 | 100
473 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND | PANHANDLE | 2015 | 100
474 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND | WEST | 2009 | 49.5
475 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND | WEST | 2009 | 51
476 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND | WEST | 2011 | 25.5
477 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND | WEST | 2011 | 24
478 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND | SOUTH | 2015 | 200
479 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND | WEST | 2015 | 105.6
480 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND | WEST | 2015 | 105.6
481 | MIAMI WIND G1 |  | MIAM1_G1 | GRAY | WIND | PANHANDLE | 2014 | 144.3
482 | MIAMI WIND G2 |  | MIAM1_G2 | GRAY | WIND | PANHANDLE | 2014 | 144.3
483 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND | PANHANDLE | 2008 | 150
484 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND | WEST | 2009 | 92.6
485 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND | WEST | 2009 | 60
486 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND | WEST | 2008 | 58.8
487 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 109.2
488 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 109.2
489 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND | PANHANDLE | 2014 | 94.2
490 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND | PANHANDLE | 2014 | 96.6
491 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND | WEST | 2008 | 142.5
492 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND | WEST | 2008 | 115.5
493 | PANTHER CREEK WIND 3 |  | PC_SOUTH_PANTHER3 | HOWARD | WIND | WEST | 2009 | 199.5
494 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND | WEST | 2001 | 82.5
495 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND | WEST | 2001 | 77.2
496 | PYRON WIND |  | PYR_PYRON1 | SCURRY | WIND | WEST | 2008 | 249
497 | RATTLESNAKE DEN WIND PHASE 1 G1 |  | RSNAKE_G1 | GLASSCOCK | WIND | WEST | 2015 | 104.3
498 | RATTLESNAKE DEN WIND PHASE 1 G2 |  | RSNAKE_G2 | GLASSCOCK | WIND | WEST | 2015 | 103
499 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND | WEST | 2006 | 84
500 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND | WEST | 2008 | 209
501 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND | PANHANDLE | 2015 | 150
502 | SAND BLUFF WIND |  | MCDLD_SBW1 | GLASSCOCK | WIND | WEST | 2008 | 90
503 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND | SOUTH | 2015 | 76
504 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND | NORTH | 2012 | 150
505 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND | WEST | 2015 | 204.1
506 | SHERBINO 1 WIND |  | KEO_KEO_SM1 | PECOS | WIND | WEST | 2008 | 150
507 | SHERBINO 2 WIND |  | KEO_SHRBINO2 | PECOS | WIND | WEST | 2011 | 147.5
508 | SILVER STAR WIND |  | FLTCK_SSI | EASTLAND | WIND | NORTH | 2008 | 60
509 | SNYDER WIND |  | ENAS_ENA1 | SCURRY | WIND | WEST | 2007 | 63
510 | SOUTH PLAINS WIND I |  | SPLAIN1_WIND1 | FLOYD | WIND | WEST | 2015 | 102
511 | SOUTH PLAINS WIND 2 |  | SPLAIN1_WIND2 | FLOYD | WIND | WEST | 2015 | 98
512 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND | WEST | 2008 | 98.2
513 | SPINNING SPUR WIND TWO |  | SSPURTWO_WIND_1 | OLDHAM | WIND | PANHANDLE | 2014 | 161
514 | SPINNING SPUR 3 [WIND 1] |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND | PANHANDLE | 2015 | 96
515 | SPINNING SPUR 3 [WIND 2] |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND | PANHANDLE | 2015 | 98
516 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND | WEST | 2008 | 120
517 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND | WEST | 2014 | 211.2
518 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND | WEST | 2015 | 164.7
519 | SWEETWATER WIND 1 |  | SWEETWND_WND1 | NOLAN | WIND | WEST | 2003 | 36.6
520 | SWEETWATER WIND 2A |  | SWEETWN2_WND24 | NOLAN | WIND | WEST | 2006 | 15.9
521 | SWEETWATER WIND 2B |  | SWEETWN2_WND2 | NOLAN | WIND | WEST | 2004 | 97.5
522 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND | WEST | 2011 | 28.5
523 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND | WEST | 2011 | 100.5
524 | SWEETWATER WIND 4-5 |  | SWEETWN4_WND5 | NOLAN | WIND | WEST | 2007 | 79.2
525 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND | WEST | 2007 | 103.7
526 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND | WEST | 2007 | 117.8
527 | TEXAS BIG SPRING WIND a |  | SGMTN_SIGNALMT | HOWARD | WIND | WEST | 1999 | 27.7
528 | TEXAS BIG SPRING WIND b |  | SGMTN_SIGNALM2 | HOWARD | WIND | WEST | 1999 | 6.6
529 | TRENT WIND |  | TRENT_TRENT | NOLAN | WIND | WEST | 2001 | 150
530 | TRINITY HILLS WIND 1 |  | TRINITY_TH1_BUS1 | YOUNG | WIND | WEST | 2012 | 117.5
531 | TRINITY HILLS WIND 2 |  | TRINITY_TH1_BUS2 | YOUNG | WIND | WEST | 2012 | 107.5
532 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND | WEST | 2008 | 169.5
533 | WEST TEXAS WIND |  | SW_MESA_SW_MESA | UPTON | WIND | WEST | 1999 | 80.3
534 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND | PANHANDLE | 2007 | 57
535 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND | SOUTH | 2012 | 91
536 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND | WEST | 2014 | 67.6
537 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND | WEST | 2012 | 30
538 | WOLF RIDGE WIND |  | WHTTAIL_WR1 | COOKE | WIND | NORTH | 2008 | 112.5
539 | TSTC WEST TEXAS WIND |  | DG_ROSC2_1UNIT | NOLAN | WIND | WEST | 2008 | 2
540 | WOLF FLATS WIND (WIND MGT) |  | DG_TURL_UNIT1 | HALL | WIND | PANHANDLE | 2007 | 1
541 | Operational Wind Capacity Sub-total (Non-Coastal Counties) | [6 empty] | 14085
542 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PEAK_PCT_NC | % |  |  |  | 12
543
544 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2015 | 165
545 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2010 | 141.6
546 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2010 | 141.6
547 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1
548 | LOS VIENTOS WIND II |  | LV1_LV1B | WILLACY | WIND-C | COASTAL | 2013 | 201.6
549 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.8
550 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5
551 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.9
552 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.1
553 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8
554 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6
555 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8
556 | HARBOR WIND |  | DG_NUECE_6UNITS | NUECES | WIND-C | COASTAL | 2012 | 9
557 | Operational Wind Capacity Sub-total (Coastal Counties) | [6 empty] | 1845.4
558 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PEAK_PCT_C | % |  |  |  | 55
559
560 | Operational Wind Capacity Total (All Counties) |  | WIND_OPERATIONAL |  |  |  |  | 15930.4
561
562 | Operational Resources (Solar)
563 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10
564 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2014 | 22
565 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.2
566 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.6
567 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 95
568 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7
569 | BLUE WING 1 SOLAR |  | DG_BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6
570 | BLUE WING 2 SOLAR |  | DG_ELEM_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3
571 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | DG_STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4
572 | OCI ALAMO 3-WALZEM SOLAR |  | DG_WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5
573 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | DG_COSERVSS_CCS1 | DENTON | SOLAR | NORTH | 2015 | 2
574 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | DG_SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6
575 | SUNEDISON SOMERSET 2 SOLAR |  | DG_SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5
576 | SUNEDISON RABEL ROAD SOLAR |  | DG_VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
577 | SUNEDISON VALLEY ROAD SOLAR |  | DG_VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9
578 | Operational Capacity Total (Solar) | [6 empty] | 287.7
579 | Solar Peak Average Capacity Percentage |  | SOLAR_PEAK_PCT | % |  |  |  | 80
580
581 | Reliability Must-Run (RMR) Capacity |  | RMR_CAP_CONT |  | GAS |  |  | 0
582
583 | Non-Synchronous Tie Resources
584 | EAST TIE |  | DC_E | FANNIN |  | NORTH |  | 600
585 | NORTH TIE |  | DC_N | WILBARGER |  | WEST |  | 220
586 | EAGLE PASS TIE |  | DC_S | MAVERICK |  | SOUTH |  | 30
587 | LAREDO VFT TIE |  | DC_L | WEBB |  | SOUTH |  | 100
588 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO |  | SOUTH |  | 150
589 | SHARYLAND RAILROAD TIE 2 |  | DC_R2 | HIDALGO |  | SOUTH |  | 150
590 | Non-Synchronous Ties Total | [6 empty] | 1250
591 | Non-Synchronous Ties Capacity Contribution (Top 20 Hours) |  | DCTIE_CAP_CONT |  | OTHER |  |  | 577
592
593 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit and Water Rights
594 | COLARADO BEND III | 17INR0007 |  | WHARTON | GAS | SOUTH | 2017 | 0
595 | TEXAS CLEAN ENERGY PROJECT | 13INR0023 |  | ECTOR | COAL | WEST | 2019 | 0
596 | FGE TEXAS I PROJECT | 16INR0010 |  | MITCHELL | GAS | WEST | 2018 | 0
597 | ANTELOPE 1-3 IC & ELK CTG 1 (SWITCHABLE) | 13INR0028 |  | HALE | GAS | PANHANDLE | 2016 | 0
598 | LA PALOMA ENERGY CENTER PROJECT | 16INR0004 |  | CAMERON | GAS | COASTAL | 2018 | 0
599 | PHR PEAKERS [BAC_CTG1-6] | 14INR0038 |  | GALVESTON | GAS | HOUSTON | 2016 | 388
600 | SKY GLOBAL POWER ONE | 16INR0057 |  | COLORADO | GAS | SOUTH | 2016 | 51.4
601 | INDECK WHARTON ENERGY CENTER PROJECT | 15INR0023 |  | WHARTON | GAS | SOUTH | 2017 | 0
602 | PINECREST ENERGY CENTER PROJECT | 16INR0006 |  | ANGELINA | GAS | NORTH | 2017 | 0
603 | RED GATE IC PLANT [REDGATE_AGR_A-D] | 14INR0040 |  | HIDALGO | GAS | SOUTH | 2016 | 225
604 | ELK STATION CTG 2 (SWITCHABLE) | 15INR0032 |  | HALE | GAS | PANHANDLE | 2016 | 202
605 | ELK STATION CTG 3 | 15INR0033 |  | HALE | GAS | PANHANDLE | 2016 | 202
606 | WOLF HOLLOW 2 | 17INR0009 |  | HOOD | GAS | NORTH | 2017 | 0
607 | FRIENDSWOOD G | 13INR0049 |  | HARRIS | GAS | HOUSTON | 2017 | 0
608 | BETHEL CAES PROJECT | 15INR0013 |  | ANDERSON | STORAGE | NORTH | 2018 | 0
609 | Planned Capacity Total (Coal, Gas & Storage) | [6 empty] | 1068.4
610
611 | Planned Wind Resources with Executed SGIA
612 | ALBERCAS WIND | 15INR0049 |  | ZAPATA | WIND | SOUTH | 2016 | 0
613 | GUNSIGHT MOUNTAIN WIND | 08INR0018 |  | HOWARD | WIND | WEST | 2016 | 0
614 | BAFFIN WIND [BAFFIN_UNIT1-2] | 06INR0022c |  | KENEDY | WIND-C | COASTAL | 2016 | 202
615 | MIDWAY FARMS WIND | 11INR0054 |  | SAN PATRICIO | WIND-C | COASTAL | 2016 | 0
616 | LONGHORN WIND SOUTH | 14INR0023b |  | BRISCOE | WIND | PANHANDLE | 2016 | 0
617 | MARIAH WIND A | 13INR0010a |  | PARMER | WIND | PANHANDLE | 2017 | 0
618 | MARIAH WIND B | 13INR0010b |  | PARMER | WIND | PANHANDLE | 2016 | 0
619 | MIAMI WIND 1B | 14INR0012b |  | GRAY | WIND | PANHANDLE | 2016 | 111
620 | RATTLESNAKE DEN WIND 2 | 13INR0020b |  | GLASSCOCK | WIND | WEST | 2017 | 0
621 | PATRIOT WIND (PETRONILLA) | 11INR0062 |  | NUECES | WIND-C | COASTAL | 2016 | 0
622 | COMANCHE RUN WIND | 12INR0029 |  | SWISHER | WIND | PANHANDLE | 2016 | 0
623 | PAMPA WIND | 12INR0018 |  | GRAY | WIND | PANHANDLE | 2017 | 0
624 | SOUTH PLAINS WIND II | 14INR0025b |  | FLOYD | WIND | PANHANDLE | 2016 | 151.8
625 | SOUTH PLAINS WIND III | 14INR0025c |  | FLOYD | WIND | PANHANDLE | 2016 | 148.5
626 | WAKE WIND | 14INR0047 |  | DICKENS | WIND | PANHANDLE | 2016 | 0
627 | DOUG COLBECK'S CORNER (CONWAY) | 13INR0005b |  | CARSON | WIND | PANHANDLE | 2016 | 0
628 | GRANDVIEW WIND 3 (CONWAY) | 13INR0005c |  | CARSON | WIND | PANHANDLE | 2016 | 0
629 | SCANDIA WIND DEF | 13INR0010def |  | PARMER | WIND | PANHANDLE | 2017 | 0
630 | PULLMAN ROAD WIND | 15INR0079 |  | RANDALL | WIND | PANHANDLE | 2016 | 0
631 | PANHANDLE WIND 3 | 14INR0030c |  | CARSON | WIND | PANHANDLE | 2016 | 0
632 | SALT FORK WIND | 14INR0062 |  | GRAY | WIND | PANHANDLE | 2016 | 0
633 | LOS VIENTOS IV WIND | 15INR0037 |  | STARR | WIND | SOUTH | 2016 | 0
634 | LOS VIENTOS V WIND [LV5_UNIT_1] | 15INR0021 |  | STARR | WIND | SOUTH | 2016 | 110
635 | PALO DURO WIND | 15INR0050 |  | DEAF SMITH | WIND | PANHANDLE | 2016 | 0
636 | CAPROCK WIND | 10INR0009 |  | CASTRO | WIND | PANHANDLE | 2017 | 0
637 | SAN ROMAN WIND | 14INR0013 |  | CAMERON | WIND-C | COASTAL | 2016 | 0
638 | TORRECILLAS WIND A | 14INR0045a |  | WEBB | WIND | SOUTH | 2016 | 0
639 | TORRECILLAS WIND B | 14INR0045b |  | WEBB | WIND | SOUTH | 2016 | 0
640 | CHANGING WINDS | 13INR0045 |  | CASTRO | WIND | PANHANDLE | 2017 | 0
641 | ELECTRA WIND | 16INR0062 |  | WILBARGER | WIND | WEST | 2016 | 0
642 | HORSE CREEK WIND | 14INR0060 |  | HASKELL | WIND | WEST | 2016 | 0
643 | WILLOW SPRINGS WIND | 14INR0060b |  | HASKELL | WIND | WEST | 2016 | 0
644 | MUENSTER WIND | 15INR0085 |  | COOKE | WIND | NORTH | 2016 | 0
645 | HAPPY WHITEFACE WIND | 15INR0074 |  | DEAF SMITH | WIND | PANHANDLE | 2016 | 0
646 | CHAPMAN RANCH WIND I | 16INR0055 |  | NUECES | WIND-C | COASTAL | 2016 | 0
647 | HIDALGO & STARR WIND | 16INR0024 |  | HIDALGO | WIND | SOUTH | 2016 | 0
648 | BLANCO CANYON WIND (COTTON PLAINS) | 16INR0037 |  | FLOYD | WIND | PANHANDLE | 2016 | 0
649 | BLANCO CANYON WIND (OLD SETTLER) | 16INR0037b |  | FLOYD | WIND | PANHANDLE | 2016 | 0
650 | ROCK SPRINGS VAL VERDE WIND | 11INR0082a |  | VAL VERDE | WIND | WEST | 2016 | 0
651 | MAGIC VALLEY WIND II (REDFISH 2A and 2B) | 14INR0041a |  | WILLACY | WIND-C | COASTAL | 2017 | 0
652 | SALT FORK WIND 2 | 16INR0082 |  | CARSON | WIND | PANHANDLE | 2016 | 0
653 | SANTA RITA WIND | 16INR0091 |  | REAGAN | WIND | WEST | 2016 | 0
654 | SWISHER WIND | 13INR0038 |  | SWISHER | WIND | PANHANDLE | 2016 | 0
655 | BUCKTHORN WIND 1 | 14INR0057 |  | ERATH | WIND | NORTH | 2016 | 0
656 | FLUVANNA RENEWABLE 1 | 13INR0056 |  | SCURRY | WIND | WEST | 2017 | 0
657 | RTS WIND | 16INR0087 |  | MCCULLOCH | WIND | SOUTH | 2016 | 0
658 | Planned Capacity Total (Wind) | [6 empty] | 723.3
659
660 | Planned Wind Capacity Sub-total (Non-Coastal Counties) |  | WIND_PLANNED_NC |  |  |  |  | 521.3
661 | Wind Peak Average Capacity Percentage (Non-Coastal) |  | WIND_PL_PEAK_PCT_NC | % |  |  |  | 12
662
663 | Planned Wind Capacity Sub-total (Coastal Counties) |  | WIND_PLANNED_C |  |  |  |  | 202
664 | Wind Peak Average Capacity Percentage (Coastal) |  | WIND_PL_PEAK_PCT_C | % |  |  |  | 55
665
666 | Planned Solar Resources with Executed SGIA
667 | FS BARILLA SOLAR 1B [HOVEY_UNIT2] | 12INR0059b |  | PECOS | SOLAR | WEST | 2016 | 7.4
668 | FS BARILLA SOLAR 2 | 12INR0059c |  | PECOS | SOLAR | WEST | 2016 | 0
669 | RE ROSEROCK SOLAR | 16INR0048 |  | PECOS | SOLAR | WEST | 2016 | 0
670 | OCI ALAMO 6 (WEST TEXAS) | 15INR0070_1 |  | PECOS | SOLAR | WEST | 2016 | 0
671 | OCI ALAMO 6 (WEST TEXAS PHASE II) | 15INR0070_1b |  | PECOS | SOLAR | WEST | 2016 | 0
672 | SE BUCKTHORN WESTEX SOLAR (RIGGINS SOLAR) | 15INR0045 |  | PECOS | SOLAR | WEST | 2016 | 0
673 | FS EAST PECOS SOLAR | 16INR0073 |  | PECOS | SOLAR | WEST | 2016 | 0
674 | OCI ALAMO 7 (PAINT CREEK) | 16INR0052 |  | HASKELL | SOLAR | WEST | 2016 | 0
675 | LC NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2016 | 0
676 | PECOS SOLAR POWER I | 15INR0059 |  | PECOS | SOLAR | WEST | 2017 | 0
677 | BNB LAMESA SOLAR | 16INR0023 |  | DAWSON | SOLAR | WEST | 2016 | 0
678 | CAPRICORN RIDGE SOLAR | 16INR0019 |  | COKE | SOLAR | WEST | 2016 | 0
679 | UPCO POWER 1 (SP-TX-12) | 16INR0065 |  | UPTON | SOLAR | WEST | 2016 | 0
680 | SP-TX-12-PHASE B | 16INR0065B |  | UPTON | SOLAR | WEST | 2016 | 0
681 | SOLAIREHOLMAN 1 | 15INR0061 |  | BREWSTER | SOLAR | WEST | 2016 | 0
682 | Upton Solar | 16INR0114 |  | UPTON | SOLAR | WEST | 2017 | 0
683 | Planned Capacity Total (Solar) | [6 empty] | 7.4
684 | Solar Peak Average Capacity Percentage |  | SOLAR_PL_PEAK_PCT | % |  |  |  | 80
685
686 | Seasonal Mothballed Resources
687 | MARTIN LAKE U2 (SINCE 10/10/2015) |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 805
688 | Total Seasonal Mothballed Capacity | [6 empty] | 805
689
690 | Mothballed Resources
692 | J T DEELY U1 (AS OF 12/31/2018) |  | CALAVERS_JTD1_M | BEXAR | COAL | SOUTH | 2018 | 420
693 | J T DEELY U2 (AS OF 12/31/2018) |  | CALAVERS_JTD2_M | BEXAR | COAL | SOUTH | 2018 | 420
694 | SILAS RAY CTG 5 (RETIRES ON 4/6/2016) |  | SILASRAY_SILAS_5 | CAMERON | GAS | COASTAL | 1953 | 10
695 | S R BERTRON CTG 2 (SINCE 5/15/2013) |  | SRB_SRBGT_2 | HARRIS | GAS | HOUSTON | 1967 | 13
696 | S R BERTRON U1 (SINCE 5/15/2013) |  | SRB_SRB_G1 | HARRIS | GAS | HOUSTON | 1958 | 118
697 | S R BERTRON U2 (SINCE 5/15/2013) |  | SRB_SRB_G2 | HARRIS | GAS | HOUSTON | 1956 | 174
698 | S R BERTRON U3 (SINCE 5/22/2013) |  | SRB_SRB_G3 | HARRIS | GAS | HOUSTON | 1959 | 211
699 | S R BERTRON U4 (SINCE 5/22/2013) |  | SRB_SRB_G4 | HARRIS | GAS | HOUSTON | 1960 | 211
700 | W A PARISH - PETRA NOVA CTG (AS OF 5/19/2016) |  | PNPI_GT2 | FORT BEND | GAS | HOUSTON | 2013 | 74
701 | Total Mothballed Capacity | [6 empty] | 1651

## Background
Release Date: March 1, 2016
Seasonal Assessment of Resource Adequacy for the ERCOT Region
Background
The Seasonal Assessment of Resource Adequacy (SARA) report is a deterministic approach to considering the impact of potential variables that may affect the sufficiency of installed resources to meet the peak electrical demand on the ERCOT System during a particular season.
The standard approach to assessing resource adequacy for one or more years into the future is to account for projected load and resources on a normalized basis and to require sufficient reserves (resources in excess of peak demand, on this normalized basis) to cover the uncertainty in peak demand and resource availability to meet a one-in-ten-years loss-of-load event criteria on a probabilistic basis.
For seasonal assessments that look ahead less than a year, specific information may be available (such as seasonal climate forecasts or anticipated common-mode events such as drought) which can be used to consider the range of resource adequacy in a more deterministic manner.
In contrast to the Capacity, Demand and Reserves (CDR) report, which addresses the sufficiency of planning reserves on an annual basis as described above, the SARA report focuses on the availability of sufficient operating reserves to avoid emergency actions such as deployment of voluntary load reduction resources. Consequently, load reduction resources included in the CDR report, such as Emergency Response Service (ERS) and Load Resources that provide operating reserves (LRs), are excluded from the SARA.
The SARA report is intended to illustrate the range of resource adequacy outcomes that might occur, and thus help fulfill the reporting requirement per Public Utility Commission of Texas rule 25.362(i)(2)(H). Several sensitivity analyses are developed by varying the value of certain parameters that affect resource adequacy. The variation in these parameters is based on historic values of these parameters or adjustments by any known or expected changes.