## Slide 1: Data Requirements For Calculating Geomagnetically Induced Currents ROS Meeting
March 3, 2016
Michael Juricek
PGDTF Chairman
<number>

## Slide 2
Space Storm
<number>
Michael Juricek – 3/3/2016 ROS Meeting
Notes: <number>

## Slide 3: What are Geomagnetically Induced Currents (GIC)?
Highly charged cloud of plasma is ejected from the sun – coronal mass ejection (CME)
Some of the plasma enters the earth’s ionosphere
The electro-magnetic interaction with earth’s magnetic field results in time varying electrojets of current in the ionosphere producing the auroras
The fluctuating electrojet currents induce voltages and currents in the earth’s crust and electric transmission systems
Michael Juricek – 3/3/2016 ROS Meeting
<number>
Notes: <number>

## Slide 4: What are Geomagnetically Induced Currents (GIC)?
Induced voltage in the earth causes GIC in the lines
Currents are “zero sequence” “quasi dc” currents
  Not displaced by 120 degrees like 60 Hz load currents
To flow the currents need a path to circulate
Path is typically provided by transformers and shunt grounding connections
TSPs and Resource Entities are affected
Michael Juricek – 3/3/2016 ROS Meeting
<number>
Notes: <number>

## Slide 5: Major Geomagnetic Storms in Past
1859 Carrington Storm
  Damaged telegraph systems
  Some operated without damaged batteries
  Sparks shocked operators and caused fires
  Lasted for 12 days
1921 Storm
  Less severe than 1859, but still damaged telegraph systems
March 13, 1989 Storm
  1/10th strength of 1921 storm
  Damaged transformers in USA and other countries
  Blackout in Canada (Hydro Quebec/Hydro One) in 92 seconds
  Auroral zone expanded to Gulf Coast
Michael Juricek – 3/3/2016 ROS Meeting
<number>
Notes: <number>

## Slide 6: GIC data files for PSS/E Model
Michael Juricek – 3/3/2016 ROS Meeting
<number>

## Slide 7: GIC Data
Required data from TSPs and Resource Entities
  Geographic location of substations (longitude and latitude)
  Grounding resistance data for substations
  Bus substation numbers (allows all substation components in one location to be grouped together into one substation)
  DC resistance of transformer windings
  Winding grounding dc resistance
  Identification of GIC blocking device in the grounding connection
  Transformer vector group
  Bus Shunts
  DC resistance of transmission lines
  Number of cores in transformer
  K Factor
Michael Juricek – 3/3/2016 ROS Meeting
<number>
Notes: <number>

## Slide 8: Substation Data
I, NAME, UNIT, LATITUDE, LONGITUDE, RG, EARTHMDL
Where:
Michael Juricek – 3/3/2016 ROS Meeting
<number>
I | Substation Number
NAME | Substation Name
UNIT | Unit for geophysical location (latitude and longitude) data = 0 for degrees At this time, only allowed unit for latitude and longitude is degrees.
LATITUDE | Substation latitude, positive for North and negative for South
LONGITUDE | Substation longitude, positive for East and negative for West
RG | Substation grounding resistance, Default =0.1 ohm If RG<=0.0 or RG>=99.0, assumed that substation is ungrounded
EARTHMDL | Name of the Earth Model
Notes: <number>

## Slide 9: Bus Substation Data
BUSNUM, SUBNUM
Where:
Michael Juricek – 3/3/2016 ROS Meeting
<number>
BUSNUM | Bus Number
SUBNUM | Substation Number. This is a substation number to which bus “BUSNUM” belongs to. The following restrictions apply: Two buses connected by a transmission line (non-transformer branch) must be in different substations. Two buses connected by a two winding transformer must be in same substation. Three buses connected by a three winding transformer must be in same substation. Two buses connected by zero impedance line must have same substation number.
Notes: <number>

## Slide 10: Bus Substation Data
Michael Juricek – 3/3/2016 ROS Meeting
<number>
Notes: <number>

## Slide 11: Bus Substation Data
Michael Juricek – 3/3/2016 ROS Meeting
<number>
Notes: <number>

## Slide 12: Transformer Data
I, J, K, CKT, WRI, WRJ, WRK, GICBDI, GICBGJ, GICBDK, VECGRP, CORE, KFACTOR, GRDWRI, GRDWRJ, GRDWRK, TMODEL
Where:
Michael Juricek – 3/3/2016 ROS Meeting
<number>
I | Winding Bus Number 1
J | Winding Bus Number 2
K | Winding Bus Number 3
CKT | Alphanumeric Circuit Identifier
WRI | DC Resistance of Winding 1 in ohms/phase. When WRI is not specified, load flow data resistance is used.
WRJ | DC Resistance of Winding 2 in ohms/phase. When WRJ is not specified, load flow data resistance is used.
WRK | DC Resistance of Winding 3 in ohms/phase. When WRK is not specified, load flow data resistance is used.
GICBDI | GIC blocking device in neutral of Winding 1
GICBDJ | GIC blocking device in neutral of Winding 2
GICBDK | GIC blocking device in neutral of Winding 3
VECGRP | Alphanumeric identifier specifying vector group based on transformer winding grounding connections and phase angles.
CORE | Number of cores. This data used to calculate transformer reactive power loss from GIC flowing in winding
KFACTOR | Factor to calculate transformer reactive power loss from GIC flowing through winding (MVAR/AMP)
GRDWRI | Winding 1 grounding DC resistance in ohms
GRDWRJ | Winding 2 grounding DC resistance in ohms
GRDWRK | Winding 3 grounding DC resistance in ohms
TMODEL | Transformer Model in GIC DC Network
Notes: <number>

## Slide 13: Bus Fixed Shunt Data
I, ID, R, RG
Where:
Michael Juricek – 3/3/2016 ROS Meeting
<number>
I | Bus Number
ID | Alphanumeric shunt identifier
R | DC resistance in ohm/phase.
RG | Grounding DC resistance in ohms
Notes: <number>

## Slide 14: Branch Data
I, J, CKT, RBRN, INDVP, INDVQ
Where:
Michael Juricek – 3/3/2016 ROS Meeting
<number>
I | Branch from bus number
J | Branch to bus number
CKT | Alphanumeric branch circuit identifier
RBRN | Branch DC resistance in ohms/phase. When RBRN is not specified, load flow data branch resistance is used as is.
INDVP | Real part of total branch GMD induced electric field in volts.
INDVQ | Imaginary part of total branch GMD induced electric field in volts.
Notes: <number>

## Slide 15: User Earth Model Data
NAME, BETAFTR, DESC, RESISTIVITY1, THICKNESS1, RESISTIVITYn, THICKNESSn
Where:
Michael Juricek – 3/3/2016 ROS Meeting
<number>
NAME | Alphanumeric identifier assigned to this earth model.
BETAFTR | Earth Model scaling factor used when calculating branch induced electric field for Benchmark GMD event.
DESC | Description of the earth model.
RESISTIVITY1 | Layer 1 Resistivity in ohm-m.
THICKNESS1 | Layer 1 Thickness in km.
RESISTIVITYn | Nth Layer Resistivity in ohm-m. Up to 25 layers allowed.
THICKNESSn | Nth Layer Thickness in km. Up to 25 layers allowed.
Notes: <number>

## Slide 16: Default Data Versus Actual Data
Software developer used actual data to develop default data which is assumed conservative data
Default data may produce higher GICs and reactive loading than actual data
Experienced TSPs highly recommend actual data
Consultants highly recommend actual data
PGDTF has decided to use actual data, where possible
Michael Juricek – 3/3/2016 ROS Meeting
<number>
Notes: <number>

## Slide 17: FERC March 1, 2016 Technical Conference
FERC commissioners and staff participated
Benchmark GMD event and geomagnetic fields
Earth conductivity model
Harmonics and vibrational effects during benchmark GMD events
Selection of 75 Ampere threshold for thermal assessments
Modeling capabilities regarding transformer thermal assessments
Non-uniform geoelectric fields
Corrective action plans
Current state of monitoring
Potential for additional monitoring
Improvement in modeling and analysis tools
Michael Juricek – 3/3/2016 ROS Meeting
<number>
Notes: <number>

## Slide 18: FERC March 1, 2016 Technical Conference continued
Comments
  Adopt standard as proposed and revise as better data and analysis techniques indicate
  Make benchmark event more severe in standard
  Lower GIC threshold for transformer thermal assessment such as 15 Amperes in standard
  Use actual GIC data to validate benchmark event
  Increase monitoring of GIC geomagnetic fields and geoelectric fields
  Improve earth models
  Provide real-time GIC readings to control rooms
  Study multiple GMD scenarios to determine the system’s strength
  Share GIC measurements with public
Michael Juricek – 3/3/2016 ROS Meeting
<number>
Notes: <number>

## Slide 19: Proposed Modeling Schedule
June 1 – TSPs and REs start providing data to ERCOT
November 1 – All data must be submitted to ERCOT
Michael Juricek – 3/3/2016 ROS Meeting
<number>
Notes: <number>

## Slide 20: PGDTF Meeting
March 21, 2016
Met Center room 206B
9:30 a.m. to 3:00 p.m.
Discuss modeling and other topics
Need all TSPs and Resource Entities
Michael Juricek – 3/3/2016 ROS Meeting
<number>
Notes: <number>

## Slide 21: Questions and Answers
<number>
Michael Juricek – 3/3/2016 ROS Meeting