| NPRR Number | 756 | NPRR Title | Enhanced Ancillary Services |
| --- | --- | --- | --- |
| Date of Decision |  | March 10, 2016 |  |
| Action |  | Tabled |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | To be determined |  |
| Priority and Rank Assigned |  | To be determined |  |
| Nodal Protocol Sections Requiring Revision |  | 2.1, Definitions 2.2, Acronyms and Abbreviations 3.16, Standards for Determining Ancillary Service Quantities 3.17.1, Regulation Service 3.17.1, Fast Frequency Response Service (FFRS) (new) 3.17.2, Primary Frequency Response Service (PFRS) (new) 3.17.2, Responsive Reserve Service 3.18, Resource Limits in Providing Ancillary Service 4.2.1.1, Ancillary Service Plan 4.4.7.1, Self-Arranged Ancillary Service Quantities 4.4.7.1.1, Negative Self-Arranged Ancillary Service Quantities 4.4.7.3, Ancillary Service Trades 4.4.7.3.1, Ancillary Service Trade Criteria 4.5.1, DAM Clearing Process 8.1, QSE and Resource Performance Monitoring 8.1.1.1, Ancillary Service Qualification and Testing 8.1.1.2, General Capacity Testing Requirements 8.1.1.2.1, Ancillary Service Technical Requirements and Qualification Criteria and Test Methods 8.1.1.2.1.1, Regulation Service Qualification 8.1.1.2.1.2, Fast Frequency Response Service Qualification (new) 8.1.1.2.1.2, Responsive Reserve Service Qualification (deleted) 8.1.1.2.1.3, Primary Frequency Response Service Qualification (new) 8.1.1.3.2, Fast Frequency Response Service Capacity Monitoring Criteria (new) 8.1.1.3.2, Responsive Reserve Service Capacity Monitoring Criteria (deleted) 8.1.1.3.3, Primary Frequency Response Service Capacity Monitoring Criteria (new) 8.1.1.4.2, Fast Frequency Response Service Energy Deployment Criteria (new) 8.1.1.4.2, Responsive Reserve Service Energy Deployment Criteria (deleted) 8.1.1.4.3, Primary Frequency Response Service Energy Deployment Criteria (new) |  |
| Related Documents Requiring Revision/Related Revision Requests |  | - Operating Procedures - Telemetry Standards - Nodal Operating Guides |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) replaces and aims to achieve most of the objectives and benefits of NPRR667, Ancillary Services Redesign, (also known as Future Ancillary Services (FAS)) while minimizing the cost impact on the market, particularly loads. This NPRR enhances the current Ancillary Services as follows: - Incorporate the equivalency ratio between Primary Frequency Response Service (PFRS) and Fast Frequency Response Service (FFRS) into the Responsive Reserve (RRS) procurement process while maintaining a single clearing price for RRS. Substitution of PFRS for FFRS would be on 1:1 ratio. - Remove the 50% limit on participation of Load Resources (providing Fast Frequency Response Service Provided by Sub-group 2 Resources (FFRS2)) that exists for RRS. - Introduce the Fast Frequency Response Service Provided by Sub-group 1 Resources (FFRS1) product to enable new technologies as an additional Resource type that can provide RRS. After a contingency, this will more readily arrest frequency decay by deploying very fast Resources providing FFRS1 (e.g., advanced batteries). This saves other frequency response (FFRS2) providers in reserve in case a larger contingency occurs shortly thereafter. - Rate providers of frequency response based on their past performance. This mechanism ensures that the system always has as much capability as intended and provides incentive for Resources to improve their performance. In contrast, the current design allows all qualified Resources to provide up to 20% of their maximum capacity towards RRS, irrespective of their performance in past events. - Continue to use RRS to meet both Frequency Response Obligation (FRO) of North American Electric Reliability Corporation (NERC) Reliability Standard BAL-003-1, Frequency Response and Frequency Bias Setting,and help restore frequency in a cost-effective, efficient manner. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | The benefits of this proposal are: - Captures almost all of the benefits of NPRR667. Substitution of PFRS for FFRS on 1:1 ratio may introduce some slight inefficiencies - however, the ratio during the critical peak hours of the summer is 1:1 anyway. There may be enough of a buffer in RRS amounts compared to the amount required to maintain adequate reliability that there is no inefficiency introduced. And the added liquidity in Ancillary Service markets by maintaining a 1:1 ratio may more than offset any slight inefficiency. - Loads save considerable amounts by not having to pay up to 2.2 times the PFRS price for FFRS - FFRS has, from the beginning of Ancillary Service markets, been paid the same price as PFRS. This multiple price payment to FFRS is not the mathematically derived price from the optimization in the first place - it results from deliberately ignoring the shadow price of the FFRS limit constraint whenever FFRS is oversubscribed. The 1:1 substitution ratio under this NPRR also helps alleviate the risk of FFRS providers in the event of having to replace their FFRS capacity with PFRS capacity. - There is no distruption in the Ancillary Service market and likely reduction in liquidity in an already illiquid market with FAS. Going from four Ancillary Services: RRS, Regulation Up Service (Reg-Up), Regulation Down Service (Reg-Down), and Non-Spinning Reserve (Non-Spin), to many more products: FFRS1 and FFRS2 (both of whose values may change from year to year based on equivalence ratio), PFRS, Contingency Reserve Service Provided by Sub-group 1 Resources (CRS1), Contingency Reserve Service Provided by Sub-group 2 Resources (CRS2), Fast Responding Regulation Up Service (FRRS-Up) and Fast Responding Regulation Down Service (FRRS-Down) (both of whose values may change from year to year based on equivalence ratio), Reg-Up, Reg-Down, Supplemental Reserve Service Provided by Sub-group 1 Resources (SRS1), and Supplemental Reserve Service Provided by Sub-group 2 Resources (SRS2) in FAS is likely to greatly impact the liquidity of the Ancillary Service market. - There is no impact on Qualified Scheduling Entity (QSE) systems not providing Ancillary Service(s) and minimal impact on QSE systems providing Ancillary Service(s). - The system changes required to implement this NPRR should be minimal as compared to FAS. The Ancillary Service set remains the same as today negating the need for redesigning, coding, testing, etc. of new Ancillary Services set under FAS. - The optimized use of RRS to provide both frequency response and help restore frequency is likely to be more efficient and cost effective than constraining by design the same RRS capacity (i.e. FFRS and PFRS capacity) to providing only frequency response under FAS. |  |
| Credit Work Group Review |  | To be determined |  |
| PRS Decision |  | On 3/10/16, PRS unanimously voted to table NPRR756. All Market Segments were present for the vote. |  |
| Summary of PRS Discussion |  | On 3/10/16, the sponsor reviewed the key points of NPRR756 with participants. Participants requested additional time to file comments on NPRR756 and investigate the costs and benefits of this proposal as compared with FAS. |  |

| Sponsor |  |
| --- | --- |
| Name | Shams Siddiqi |
| E-mail Address | shams@crescentpower.net |
| Company | Freeport LNG Development, L.P. |
| Phone Number | 512-619-3532 |
| Cell Number | 512-619-3532 |
| Market Segment | Industrial Consumer |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Cory Phillips |
| E-Mail Address | cory.phillips@ercot.com |
| Phone Number | 512-248-6464 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

Please note that the baseline Protocol language in the following sections has been updated to reflect the incorporation of the following NPRR(s) into the Protocols:

- NPRR588, Clarifications for PV Generation Resources (unboxed 2/10/16)

  - Section 8.1.1.2

Please also note the following NPRR(s) also propose revisions to the following section(s):

- NPRR667, Ancillary Service Redesign

  - Section 2.1

  - Section 2.2

  - Section 3.16

  - Section 3.17.1

  - Section 3.17.2

  - Section 3.18

  - Section 4.2.1.1

  - Section 4.4.7.1

  - Section 4.4.7.1.1

  - Section 4.4.7.3

  - Section 4.4.7.3.1

  - Section 4.5.1

  - Section 8.1

  - Section 8.1.1.1

  - Section 8.1.1.2

  - Section 8.1.1.2.1

  - Section 8.1.1.2.1.1

  - Section 8.1.1.2.1.2

  - Section 8.1.1.3.2

  - Section 8.1.1.4.2

- NPRR754, Revise Load Distribution Factors Report Posting Frequency

  - Section 4.5.1

Proposed Protocol Language Revision

## 2.1	DEFINITIONS

- Fast Frequency Response  (FFR)

- The automatic self-deployment and provision by a Resource of their full response within 30 cycles after frequency meets or drops below a preset threshold.

- Fast Frequency Response Service (FFRS)

- An Ancillary Service provided by Resources with capacity reserved for Fast Frequency Response (FFR).

- FFRS may be provided by two FFRS sub-groups:

- Sub-group FFRS1 includes Resources capable of sustaining a full response for at least ten minutes and, once recalled, restoring their full FFRS Ancillary Service Resource Responsibility within 15 minutes.

- Sub-group FFRS2 includes Resources capable of sustaining a full response until receiving an ERCOT recall instruction or until the Resource’s FFRS Ancillary Service Resource Responsibility expires, whichever occurs first, and, once recalled, restoring their full FFRS Ancillary Service Resource Responsibility within 180 minutes.

- Primary Frequency Response (PFR)

The instantaneous proportional increase or decrease in real power output provided by a Resource and the natural real power dampening response provided by Load in response to system frequency deviations.  This response is in the direction that stabilizes frequency.

- Primary Frequency Response Service (PFRS)

An Ancillary Service provided by Resources with capacity reserved for Primary Frequency Response (PFR).

- Responsive Reserve (RRS)

An Ancillary Service consisting of Primary Frequency Response Service (PFRS) and Fast Frequency Response Service (FFRS) that provides operating reserves that is intended to:

(a) 	Arrest frequency decay within the first few seconds of a significant frequency deviation on the ERCOT Transmission Grid using Primary Frequency Response (PFR) and Fast Frequency Response (FFR) to meet North American Electric Reliability Corporation (NERC) Reliability Standards;

(b)	After the first few seconds of a significant frequency deviation, help restore frequency to its scheduled value to return the system to normal;

(c)	Provide energy or continued Load interruption during the implementation of the EEA; and

(d)	Provide backup regulation.

## 2.2	ACRONYMS AND ABBREVIATIONS

FFR	Fast Frequency Response

FFRS	Fast Frequency Response Service

FFRS1	Fast Frequency Response Service Provided by Sub-group 1 Resources

FFRS2	Fast Frequency Response Service Provided by Sub-group 2 Resources

PFR	Primary Frequency Response

PFRS	Primary Frequency Response Service

Reg-Down	Regulation Down Service

Reg-Up	Regulation Up Service

3.16	Standards for Determining Ancillary Service Quantities

(1)	ERCOT shall comply with the requirements for determining Ancillary Service quantities as specified in these Protocols and the ERCOT Operating Guides.

(2)	ERCOT shall, at least annually, determine with supporting data, the methodology for determining the quantity requirements for each Ancillary Service needed for reliability, including minimum amounts and/or maximum amounts for each Ancillary Service, equivalency ratio between applicable Ancillary Services, and limitations on the quantity of an Ancillary Service that can be provided by various Resource types and the Direct Current (DC) Ties.

(3)	The ERCOT Board shall review and approve ERCOT's methodology for determining all quantities and equivalency ratios as described in paragraph (2) above.

(4)	If ERCOT determines a need for additional Ancillary Service Resources under these Protocols or the ERCOT Operating Guides, after an Ancillary Service Plan for a specified day has been posted, ERCOT shall inform the market by posting notice on the Market Information System (MIS) Public Area, of ERCOT’s intent to procure additional Ancillary Service Resources under Section 6.4.9.2, Supplemental Ancillary Services Market.  ERCOT shall post the reliability reason for the increase in service requirements.

(5)

ERCOT shall monitor synchronous inertia from all On-Line Resources and post the quantity to the MIS Public Area in Real-Time.

3.17.1	Fast Frequency Response Service (FFRS)

Fast Frequency Response Service (FFRS) is a service intended to arrest system frequency decay.  FFRS is automatically deployed when system frequency is at or below a predetermined threshold value established by ERCOT.  Resources providing FFRS must provide their full FFRS capacity within 30 cycles (0.5 seconds).  ERCOT may also deploy FFRS manually to maintain reliable and secure operations. FFRS may be provided by two FFRS sub-groups, FFRS Provided by Sub-group 1 Resources (FFRS1) and FFRS Provided by Sub-group 2 Resources (FFRS2), as defined in Section 2.1, Definitions.

3.17.2	Primary Frequency Response Service (PFRS)

Primary Frequency Response Service (PFRS) is a continuous service intended to arrest and stabilize or maintain the frequency of the ERCOT System.  PFRS is automatically deployed when system frequency deviation exceeds a predetermined threshold value.  Resources providing PFRS must deliver their required response, up to their full PFRS Ancillary Service Resource Responsibility, within 16 seconds.  Resources that provide PFRS must reserve capacity for this Ancillary Service and be able to assist in arresting and stabilizing over or under-frequency excursions.

3.17.3	Regulation Service

(1)	Regulation Up Service (Reg-Up) is a service that provides capacity that can respond to signals from ERCOT within five seconds.  The amount of Reg-Up  Ancillary Service Resource Responsibility is the amount of capacity available from a Resource that may be called on to increase or decrease output or consumption as necessary to maintain proper system frequency. A Generation Resource providing Reg-Up must be able to increase energy output when deployed and decrease energy output when recalled.  A Load Resource providing Reg-Up must be able to decrease Load when deployed and increase Load when recalled.  Fast-Responding Regulation Service Up (FRRS-Up) is a subset of Reg-Up in which the participating Resource provides Reg-Up capacity to ERCOT within 60 cycles of either its receipt of an ERCOT Dispatch Instruction or the detection of a trigger frequency independent of an ERCOT Dispatch Instruction.  ERCOT dispatches Reg-Up by a Load Frequency Control (LFC) signal.  The LFC signal for FRRS-Up is separate from the LFC signal for other Reg-Up.

(2)	Regulation Down Service (Reg-Down) is a service that provides capacity that can respond to signals from ERCOT within five seconds.  The amount of Reg-Down Ancillary Service Resource Responsibility is the amount of capacity available from a Resource that may be called on to increase or decrease output or consumption as necessary to maintain proper system frequency.  A Generation Resource providing Reg-Down must be able to decrease energy output when deployed and increase energy output when recalled. A Load Resource providing Reg-Down must be able to increase Load when deployed and decrease Load when recalled.  Fast-Responding Regulation Service Down (FRRS-Down) is a subset of Reg-Down in which a participating Resource provides Reg-Down capacity to ERCOT within 60 cycles of either its receipt of an ERCOT Dispatch Instruction or the detection of a trigger frequency independent of an ERCOT Dispatch Instruction.  ERCOT dispatches Reg-Down by an LFC signal.  The LFC signal for FRRS-Down is separate from the LFC signal for other Reg-Down.

(3)	A single Resource shall not be allowed to carry more than 25% of the system-wide Reg-Up or Reg-Down requirement for any hour.

3.17.4	Responsive Reserve Service

(1)	Responsive Reserve (RRS) Service is a service used to restore or maintain the frequency of the ERCOT System:

(a)	In response to, or to prevent, significant frequency deviations;

(b)	As backup Regulation Service; and

(c)	By providing energy during an Energy Emergency Alert (EEA).

(2)	RRS may be provided through one or more of the following means:

(a)	By using frequency-dependent response from On-Line Resources as prescribed in the Operating Guides to help restore the frequency within the first few seconds of an event that causes a significant frequency deviation in the ERCOT System; and

(b)	Either manually or by using a four-second signal to provide energy on deployment by ERCOT.

(3)	RRS Service may be used to provide energy during the implementation of an EEA.  Under the EEA, RRS provides generation capacity, capacity from Controllable Load Resources or interruptible Load available for deployment on ten minutes’ notice.

(4)	RRS Service may be provided by:

(a)	Unloaded, On-Line Generation Resource capacity;

(b)	Load Resources controlled by high-set, under-frequency relays;

(c)	Controllable Load Resources;

(d)	Hydro Responsive Reserves as defined in the Operating Guides;

(e)	Direct Current Tie (DC Tie) response that stops frequency decay as defined in the Operating Guides; and

(f)	Resources capable of automatically self-deploying and sustaining a full response for at least ten minutes and, once recalled, restoring their full FFRS Ancillary Service Resource Responsibility within 15 minutes.

- 3.18	Resource Limits in Providing Ancillary Service

- (1)	For both On-Line Generation Resources and Load Resources, the High Sustained Limit (HSL) must be greater than or equal to the sum of the Low Sustained Limit (LSL) and the Ancillary Service Resource Responsibilitiess.

(2)	For Non-Spin, the amount of Non-Spin provided must be less than or equal to the HSL for Off-Line Generation Resources.

4.2.1.1	Ancillary Service Plan

(1)	ERCOT shall analyze the expected Load conditions for the Operating Day and develop an Ancillary Service Plan that identifies the Ancillary Service MW necessary for each hour of the Operating Day.  The MW of each Ancillary Service required may vary from hour to hour depending on ERCOT System conditions.  ERCOT must post the Ancillary Service Plan to the Market Information System (MIS) Public Area by 0600 of the Day-Ahead.  This posting shall include equivalency ratios between applicable Ancillary Services.

(2)	If ERCOT determines that an Emergency Condition may exist that would adversely affect ERCOT System reliability, it may increase the requirement amounts of each Ancillary Service from the monthly amounts determined previously, as described in Section 3.16, Standards for Determining Ancillary Service Quantities, and must post any change  to the MIS Public Area by 0600 of the Day-Ahead.

(3)	ERCOT shall determine the total required amount of each Ancillary Service under Section 3.16, or use its operational judgment and experience to change the daily quantity of each required Ancillary Service.

(4)	ERCOT shall include in the Ancillary Service Plan enough capacity to automatically control frequency with the intent to meet North American Electric Reliability Corporation (NERC) Reliability Standards.

(5)	ERCOT shall notify the Qualified Scheduling Entity (QSE) representing a Reliability Must-Run (RMR) Unit for any unit that is being committed in the Day-Ahead Market (DAM) or the Day-Ahead Reliability Unit Commitment (DRUC) at the same time that the DAM and DRUC participants are notified of the results of that respective process.

(6)	Once specified by ERCOT for an hour and published on the MIS Public Area, Ancillary Service quantity requirements for an Operating Day may not be decreased.

- 4.4.7.1	Self-Arranged Ancillary Service Quantities

(1)	For each Ancillary Service, a QSE may self-arrange all or a portion of the Ancillary Service Obligation allocated to it by ERCOT.  In addition, a QSE may self-arrange up to 100 MW of Responsive Reserve (RRS) Service, 25 MW of Regulation Up Service (Reg-Up), 25 MW of Regulation Down Service (Reg-Down), and 100 MW of Non-Spinning Reserve (Non-Spin) in excess of its corresponding Ancillary Service Obligation, provided that the amount self-arranged from the QSE’s Resources for a given Ancillary Service shall not exceed the amount of the QSE’s Ancillary Services Obligation for that Ancillary Service.  If a QSE elects to self-arrange Ancillary Service capacity, then ERCOT shall not pay the QSE for the Self-Arranged Ancillary Service Quantities for the portion that meets its Ancillary Service Obligation.  Any Self-Arranged Ancillary Service Quantities in excess of a QSE’s Ancillary Service Obligation will be considered to be offered in the DAM or Supplemental Ancillary Service Market (SASM), as applicable, for $0/MWh.

(2)	The QSE must indicate before 1000 in the Day-Ahead the Self-Arranged Ancillary Service Quantities, by service, so ERCOT can determine how much Ancillary Service capacity, by service, needs to be obtained through the DAM.

(3)	At or after 1000 in the Day-Ahead, a QSE may not change its Self-Arranged Ancillary Service Quantities unless ERCOT opens a SASM.

(4)	Before 1430 in the Day-Ahead, all Self-Arranged Ancillary Service Quantities must be represented by physical capacity, either by Generation Resources or Load Resources, or backed by Ancillary Service Trades.

(5)	The QSE may self-arrange:

(a)	Reg-Up, with the option of self-arranging Fast Responding Regulation Up Service (FRRS-Up), which counts towards Reg-Up self-arrangement, as described in paragraph (8) below;

(b)	Reg-Down, with the option of self-arranging Fast Responding Regulation Down Service (FRRS-Down), which counts towards Reg-Down self-arrangement, as described in paragraph (8) below;

(c)	RRS, and

(d)	Non-Spin.

(6)	The QSE may self-arrange Ancillary Services from one or more Resources it represents and/or through an Ancillary Service Trade.

(7)	The additional Self-Arranged Ancillary Service Quantity specified by the QSE in response to a SASM notice by ERCOT to obtain additional Ancillary Services in the Adjustment Period cannot be more than 100 MWs of RRS, 25 MWs of Reg-Up, 25 MWs of Reg-Down, and 100 MWs of Non-Spin greater than the additional Ancillary Service amount allocated by ERCOT to that QSE, as stated in the SASM notice, and cannot be changed once committed to ERCOT.

(8)	If a QSE does not self-arrange all of its Ancillary Service Obligation, ERCOT shall procure the remaining amount of that QSE’s Ancillary Service Obligation.

(a)	For self-arranged FRRS-Up, the QSE shall not self-arrange more than its Load Ratio Share (LRS) multiplied by the maximum amount of FRRS-Up allowed in the posted Ancillary Service Plan for a given hour.  Self-arranged FRRS-Up MW quantities multiplied by the equivalency ratio between Reg-Up and FRRS-Up is counted towards the self-arrangement of Reg-Up.

(b)	For self-arranged FRRS-Down, the QSE shall not self-arrange more than its LRS multiplied by the maximum amount of FRRS-Down allowed in the posted Ancillary Service Plan for a given hour.  Self-arranged FRRS-Down MW quantities multiplied by the equivalency ratio between Reg-Down and FRRS-Down is counted towards the self-arrangement of Reg-Down.

(c)	For self-arranged FFRS Provided by Sub-group 1 Resources (FFRS1), the QSE shall not self-arrange more than its LRS multiplied by the maximum amount of FFRS1 allowed in the posted Ancillary Service Plan for a given hour. In addition, the total FFRS (FFRS1 plus FFRS Provided by Sub-group 2 Resources (FFRS2)) that is self-arranged cannot exceed the QSE’s LRS multiplied by the maximum amount of FFRS allowed as posted in the Ancillary Service Plan for a given hour.

(9)	For self-arranged RRS Service, the QSE shall indicate the quantity of the service that is provided from:

(a)	Primary Frequency Response Service (PFRS);

(b)	FFRS1; and

(c)	FFRS2.

- 4.4.7.1.1	Negative Self-Arranged Ancillary Service Quantities

(1)	A QSE may submit a negative Self-Arranged Ancillary Service Quantity in the DAM.  ERCOT shall procure all negative Self-Arranged Ancillary Service Quantities submitted by a QSE.

(2)	Procurements of negative Self-Arranged Ancillary Service Quantities by ERCOT shall be settled in the same manner as Ancillary Service Obligations that are not self-arranged and according to the charges defined in Section 4.6.4.2, Charges for Ancillary Services Procurement in the DAM, and Section 6.7, Real-Time Settlement Calculations for the Ancillary Services.

(3)	A QSE may not submit a negative Self-Arranged Ancillary Service Quantity in the DAM that is less than -500 MW per Ancillary Service.  For compliance purposes, a QSE may not submit a negative Self-Arranged Ancillary Service Quantity in the DAM that is greater in magnitude than the absolute value of the net sales of its Ancillary Service Trades per Ancillary Service.

4.4.7.3	Ancillary Service Trades

(1)	An Ancillary Service Trade is the information for a QSE-to-QSE transaction that transfers an obligation to provide Ancillary Service capacity between a buyer and a seller.

(2)	An Ancillary Service Trade that is reported to ERCOT by 1430 in the Day-Ahead changes the Ancillary Service Supply Responsibility of the buyer and seller in the DRUC process.  An Ancillary Service Trade that is reported to ERCOT after 1430 in the Day-Ahead changes the Ancillary Service Supply Responsibility of the buyer and seller in any applicable HRUC process, the deadline for which is after the trade is submitted.

(3)	As soon as practicable, ERCOT shall notify each QSE through the Messaging System of any of its Ancillary Service Trades that are invalid Ancillary Service Trades.  The QSE may correct and resubmit any invalid Ancillary Service Trade, but the reporting time of the trade is determined by when the validated Ancillary Service Trade was submitted and not when the original invalid Ancillary Service Trade was submitted.

(4)	A QSE with an FFRS obligation may transfer its obligation to another QSE via Ancillary Service Trade(s) for PFRS.  A QSE with a PFRS obligation may not transfer its obligation to another QSE via Ancillary Service Trade(s) for FFRS.

(5)	A QSE with an FRRS-Up Ancillary Service Supply Responsibility has the option of transferring its Ancillary Service Supply Responsibility to another QSE via Ancillary Service Trade(s) for Reg-Up.  A QSE with a Reg-Up Ancillary Service Supply Responsibility shall not transfer its Ancillary Service Supply Responsibility to another QSE via Ancillary Service Trade(s) for FRRS-Up.

(6)	A QSE with an FRRS-Down Ancillary Service Supply Responsibility has the option of transferring its Ancillary Service Supply Responsibility to another QSE via Ancillary Service Trade(s) for Reg-Down.  A QSE with a Reg-Down Ancillary Service Supply Responsibility shall not transfer its Ancillary Service Supply Responsibility to another QSE via Ancillary Service Trade(s) for FRRS-Down.

4.4.7.3.1	Ancillary Service Trade Criteria

(1)	Each Ancillary Service Trade must be reported by a QSE and must include the following information:

(a)	The buying QSE;

(b)	The selling QSE;

(c)	The type of Ancillary Service;

(d)	The quantity in MW; and

(e)	The first and last hours of the trade.

(f)	For Responsive Reserve Service, the QSE shall indicate the quantity of the service that is provided from:

(i)	PFRS;

(ii)	FFRS1; and

(iii)	FFRS2.

(2)	An Ancillary Service Trade must be confirmed by both the buying QSE and selling QSE to be considered valid and to be used in an ERCOT process.

- 4.5.1	DAM Clearing Process

(1)	At 1000 in the Day-Ahead, ERCOT shall start the Day-Ahead Market (DAM) clearing process.  If the processing of DAM bids and offers after 0900 is significantly delayed or impacted by a failure of ERCOT software or systems that directly impacts the DAM, ERCOT shall post a Notice as soon as practicable on the Market Information System (MIS) Public Area, in accordance with paragraph (1) of Section 4.1.2, Day-Ahead Process and Timing Deviations, extending the start time of the execution of the DAM clearing process by an amount of time at least as long as the duration of the processing delay plus ten minutes.  In no event shall the extension exceed more than one hour from when the processing delay is resolved.

(2)	ERCOT shall complete a Day-Ahead Simultaneous Feasibility Test (SFT).  This test uses the Day-Ahead Updated Network Model topology and evaluates all Congestion Revenue Rights (CRRs) for feasibility to determine hourly oversold quantities.

(3)	The purpose of the DAM is to economically and simultaneously clear offers and bids described in Section 4.4, Inputs into DAM and Other Trades.

(4)	The DAM uses a multi-hour mixed integer programming algorithm to maximize bid-based revenues minus the offer-based costs over the Operating Day, subject to security and other constraints, and ERCOT Ancillary Service procurement requirements.

- The bid-based revenues include revenues from DAM Energy Bids and Point-to-Point (PTP) Obligation bids.

(b)	The offer-based costs include costs from the Startup Offer, Minimum Energy Offer, and Energy Offer Curve of any Resource that submitted a Three-Part Supply Offer, DAM Energy-Only Offers and Ancillary Service Offers.

(c)	Security constraints specified to prevent DAM solutions that would overload the elements of the ERCOT Transmission Grid include the following:

(i)	Transmission constraints – transfer limits on energy flows through the ERCOT Transmission Grid, e.g., thermal or stability limits.  These limits must be satisfied by the intact network and for certain specified contingencies.

These constraints may represent:

(A)	Thermal constraints – protect Transmission Facilities against thermal overload.

(B)	Generic constraints – protect the ERCOT Transmission Grid against transient instability, dynamic stability or voltage collapse.

(C)	Power flow constraints – the energy balance at required Electrical Buses in the ERCOT Transmission Grid must be maintained.

(ii)	Resource constraints – the physical and security limits on Resources that submit Three-Part Supply Offers:

(A)	Resource output constraints – the Low Sustained Limit (LSL) and High Sustained Limit (HSL) of each Resource; and

(B)	Resource operational constraints – includes minimum run time, minimum down time, and configuration constraints.

(iii)	Other constraints –

(A)	Linked offers – the DAM may not select any one part of that Resource capacity to provide more than one Ancillary Service or to provide both energy and an Ancillary Service in the same Operating Hour.  The DAM may, however, select part of that Resource capacity to provide one Ancillary Service and another part of that capacity to provide a different Ancillary Service or energy in the same Operating Hour, provided that a Generation Resource may not offer, and the DAM may not select, linked Energy and Off-Line Non-Spinning Reserve (Non-Spin) Ancillary Service Offers in the same Operating Hour.

(B)	The sum of the awarded Ancillary Service capacities and energy for each Resource must be within the Resource limits specified in the Current Operating Plan (COP) and Section 3.18, Resource Limits in Providing Ancillary Service, and the Resource Parameters as described in Section 3.7, Resource Parameters.

(C)	Block Ancillary Service Offers for a Load Resource – blocks will not be cleared unless the entire quantity block can be awarded.  Because block Ancillary Service Offers cannot set the Market Clearing Price for Capacity (MCPC), a block Ancillary Service Offer may clear below the Ancillary Service Offer price for that block.

(D)	Block DAM Energy Bids, DAM Energy-Only Offers, and PTP Obligation bids – blocks will not be cleared unless the entire time and/or quantity block can be awarded.  Because quantity block bids and offers cannot set the Settlement Point Price, a quantity block bid or offer may clear in a manner inconsistent with the bid or offer price for that block.

(E)	Combined Cycle Generation Resources – The DAM may commit a Combined Cycle Generation Resource in a time period that includes the last hour of the Operating Day only if that Combined Cycle Generation Resource can transition to a shutdown condition in the DAM Operating Day.

(d)	Ancillary Service needs for each Ancillary Service include the needs specified in the Ancillary Service Plan that are not part of the Self-Arranged Ancillary Service Quantity and that must be met from available DAM Ancillary Service Offers while co-optimizing with DAM Energy Offers.  Based on Fast Frequency Response Service (FFRS) offers and the equivalency ratio between FFRS and Primary Frequency Response Service (PFRS), ERCOT shall determine the quantity of RRS to be procured in the DAM.  ERCOT may not buy more of one Ancillary Service in place of the quantity of a different service.  See Section 4.5.2, Ancillary Service Insufficiency, for what happens if insufficient Ancillary Service Offers are received in the DAM.

(5)	ERCOT shall determine the appropriate Load distributions to allocate offers, bids, and source and sink of CRRs at a Load Zone across the Electrical Buses that are modeled with Load in that Load Zone.  The default distribution is the State Estimator hourly distribution for the seven days before the Operating Day.  If ERCOT decides, in its sole discretion, to change this distribution for reasons such as anticipated weather events or holidays, ERCOT shall select a State Estimator distribution from a proxy day reasonably reflecting the anticipated distribution in the Operating Day.  ERCOT may also modify this distribution to account for predicted differences in network topology between the proxy day and Operating Day.  ERCOT shall develop a methodology, subject to Technical Advisory Committee (TAC) approval, to describe the modification of the proxy day bus-load distribution for this purpose.

(6)	ERCOT shall allocate offers, bids, and source and sink of CRRs at a Hub using the distribution factors specified in the definition of that Hub in Section 3.5.2, Hub Definitions.

(7)	A Resource that has a Three-Part Supply Offer cleared in the DAM may be eligible for Make-Whole Payment of the Startup Offer and Minimum Energy Offer submitted by the Qualified Scheduling Entity (QSE) representing the Resource under Section 4.6, DAM Settlement.

(8)	The DAM Settlement is based on hourly MW awards and on Day-Ahead hourly Settlement Point Prices.  All PTP Options settled in the DAM are settled based on the Day-Ahead Settlement Point Prices (DASPPs).  ERCOT shall assign a Locational Marginal Price (LMP) to de-energized Electrical Buses for use in the calculation of the DASPPs by using heuristic rules applied in the following order:

(a)	Use an appropriate LMP predetermined by ERCOT as applicable to a specific Electrical Bus; or if not so specified

(b)	Use the following rules in order:

(i)	Use average LMP for Electrical Buses within the same station having the same voltage level as the de-energized Electrical Bus, if any exist.

(ii)	Use average LMP for all Electrical Buses within the same station, if any exist.

(iii)	Use System Lambda.

(9)	The Day-Ahead MCPC for each hour for each Ancillary Service is the Shadow Price for that Ancillary Service for the hour as determined by the DAM algorithm.

(10)	If the Day-Ahead MCPC cannot be calculated by ERCOT, the Day-Ahead MCPC for the particular Ancillary Service is equal to the Day-Ahead MCPC for that Ancillary Service in the same Settlement Interval of the preceding Operating Day.

(11)	If the DASPPs cannot be calculated by ERCOT, all CRRs shall be settled based on Real-Time prices.  Settlements for all CRRs shall be reflected on the Real-Time Settlement Statement.

- 8.1	QSE and Resource Performance Monitoring

(1)	Each QSE and Resource shall meet performance measures as described in this Section and in the Operating Guides.

(2)	ERCOT shall monitor and post the following categories of performance:

(a)	Real-Time data, for QSEs:

(i)	Telemetry performance

(b)	Regulation control performance, for QSEs and as applicable, Resource-specific performance (see also Section 8.1.1, QSE Ancillary Service Performance Standards);

(c)	Primary Frequency Response Service (PFRS) tests from hydro  Generation Resources operating in the synchronous condenser fast response mode ;

(d)	Supplying and validating data for generator models, as requested by ERCOT, for Generation Resources;

(e)	Outage scheduling and coordination, for QSEs and Resources;

(f)	Resource-specific Fast Frequency Response Service (FFRS) performance, for QSEs and Resources;

(g)	Resource-specific PFRS performance, for QSEs and Resources;

(h)	Resource-specific Non-Spinning Reserve (Non-Spin) performance, for QSEs and Resources;

(i)	Resource-specific Fast Responding Regulation Service (FRRS) performance, for QSEs and Resources;

(j)	Outage reporting, by QSEs for Resources;

(k)	Current Operating Plan (COP) metrics, for QSEs; and

(l)	Day-Ahead Reliability Unit Commitment (DRUC) and Hourly Reliability Unit Commitment (HRUC) commitment performance by QSEs and Generation Resources.

[NPRR257: Replace paragraph (3) above with the following upon system implementation:] (3) ERCOT shall monitor and post the following categories of performance: (a) Net dependable real power capability testing, for Resources; (b) Reactive testing, for Generation Resources, to validate Corrected Unit Reactive Limit (CURL) and Unit Reactive Limit (URL); (c) Real-Time data, for QSEs: (i) Telemetry performance; (ii) Communications system performance; (iii) Operational data requirements required under Section 6.5.5.2, Operational Data Requirements. (d) Regulation control performance, for QSEs and as applicable, Resource-specific performance (see also Section 8.1.1, QSE Ancillary Service Performance Standards); (e) Primary Frequency Response Service (PFRS) testing from Hydro Generation Resources operating in the synchronous condenser fast response mode ; (f) Black Start Service (BSS) test results for QSEs and Generation Resources posted to the Market Information System (MIS) Certified Area; (g) Supplying and validating data for generator models, as requested by ERCOT, for Generation Resources; (h) Outage scheduling and coordination, for QSEs and Resources; (i) Resource-specific Fast Frequency Response Service (FFRS) performance for QSEs and Resources; (j) Resource-specific PFRS performance for QSEs and Resources; (k) The QSE backup control plan for Resource energy deployment in the event of the loss of a communication path with ERCOT. ERCOT will test these plans randomly at least once a year for QSEs representing Resources; (l) Resource-specific Non-Spinning Reserve (Non-Spin) performance, for QSEs and Resources; (m) Resource-specific Fast Responding Regulation Service (FRRS) performance, for QSEs and Resources; (n) Resource-specific Supplemental Reserve Service (SRS) performance, for QSEs and Resources; (o) 24 hours per day, seven days per week qualified staffing requirement, as described in the Operating Guides, for QSEs; (p) Automatic Voltage Regulator (AVR) requirements, for QSEs and Generation Resources; (q) Staffing plan for a backup control facility or procedures in the event that the primary facility is unusable, for QSEs; (r) Outage reporting, by QSEs for Resources; (s) Current Operating Plan (COP) metrics, for QSEs; and (t) Day-Ahead Reliability Unit Commitment (DRUC) and Hourly Reliability Unit Commitment (HRUC) commitment performance by QSEs and Generation Resources.

- 8.1.1.1	Ancillary Service Qualification and Testing

(1)	Each QSE and the Resource providing Ancillary Service must meet qualification criteria to operate satisfactorily with ERCOT.  ERCOT shall use the Ancillary Service qualification and testing program that is approved by TAC and included in the Operating Guides.  Each QSE for the Resources that it represents may only provide Ancillary Services on those Resources for which it has met the qualification criteria.

(2)	General capacity testing must be used to verify a Resource’s telemetered High Sustained Limit (HSL).  Qualification tests allow the Resource and QSE to demonstrate the minimum capabilities necessary to deploy an Ancillary Service.

(3)	A Resource may be provisionally qualified for a period of 90 days and may be eligible to participate as a Resource providing Ancillary Service.  Resources that have installed the appropriate equipment with verifiable testing data may be provisionally qualified as providers of Ancillary Service.

(4)	A Load Resource may be provisionally qualified for a period of 90 days to participate as a Resource providing Ancillary Service, if the Load Resource is metered with an Interval Data Recorder (IDR) to ERCOT’s reasonable satisfaction.  A Load Resource providing Ancillary Service in Real-Time must meet the following requirements:

(a)	Electric Service Identifier (ESI ID) registration of Load Resources providing Ancillary Service by the QSE; and

(b)	Load Resource telemetry is installed and tested between QSE and ERCOT.

(5)	Provisional qualification as described herein may be revoked by ERCOT at any time for any non-compliance with provisional qualification requirements.

(6)	For those Settlement Intervals during which a Generation Resource or Load Resource behind the Generation Resource Node is engaged in testing in accordance with this Section, the provisions of Section 6.6.5, Generation Resource Base-Point Deviation Charge, will not apply to the Resource being tested beginning with the Settlement Interval immediately preceding the Settlement Interval in which ERCOT issues a Dispatch Instruction that begins the test and continuing until the end of the Settlement Interval in which the test completes.  During the same Settlement Intervals for the testing period, the Generation Resource Energy Deployment Performance (GREDP) calculated in accordance with Section 8.1.1.4.1, Regulation Service and Generation Resource/Controllable Load Resource Energy Deployment Performance, will not apply.

(7)	ERCOT shall monitor and post by Resource and by QSE the quantity of each Ancillary Service that each Resource is qualified to provide to the MIS Certified Area.  Any updates to the qualified quantities shall be posted by the twentieth of each month, to be effective beginning the first of the following month.  ERCOT may reduce the amount a Resource may contribute toward Ancillary Service if it determines unsatisfactory performance of the Resource as defined in Section 8.1.1, QSE Ancillary Service Performance Standards.

(8)	To maintain qualification with ERCOT to provide FFRS2, each Load Resource, excluding Controllable Load Resources, will be subject to a Load interruption test at a date and time determined by ERCOT and known only to ERCOT and the affected Transmission Service Provider (TSP), to verify the ability to respond to an ERCOT Dispatch Instruction.  To successfully pass this test, within ten minutes of the receipt of the ERCOT Dispatch Instruction by the Load Resource’s QSE, the Load Resource’s response shall not be less than 95% of the requested MW deployment, nor more than 150% of the lesser of the following:

(a)	The Resource’s Responsibility for FFRS2, or

(b)	The requested MW deployment.

The requested MW deployment will be the sum of the Resource’s Responsibility for FFRS2 and the telemetered additional capacity between the net power consumption and the Low Power Consumption (LPC).  If a Load Resource has responded to an actual ERCOT Dispatch Instruction in compliance with (a) and (b) above in the rolling 365-day period, ERCOT will use that response in lieu of a Load interruption test.  If a Load Resource has not responded to an ERCOT Dispatch Instruction in compliance with (a) and (b) above, either in a deployment event or a Load interruption test, in any rolling 365-day period, it is subject to a Load interruption test by ERCOT.  QSEs may request to have individual Load Resources aggregated for the purposes of Load interruption tests.  All performance evaluations will apply on an individual Resource basis.

(9)	ERCOT may revoke the Ancillary Service qualification of any Load Resource providing FFRS2 if that Load Resource has two performance failures, in either a deployment event or a Load interruption test, within any rolling 365-day period.  A performance failure is defined as a response less than 95% or greater than 150% of a Load Resource’s  ft % of its Ancillasource Responsibility for FFRS2 within 30 cycles of a triggering event or within ten minutes of an ERCOT Dispatch Instruction, that response shal pedisqualification, the Load Resource may reapply for qualification provided it submits a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies and the disqualified Load Resource successfully passes a new Load interruption test as specified in this Section 8.1.1.1.

(10)	To maintain qualification with ERCOT to provide FFRS1, each Resource, excluding Controllable Load Resources, will be subject to an FFRS1 test at a date and time determined by ERCOT and known only to ERCOT and the affected Transmission Service Provider (TSP), to verify the ability to respond to an ERCOT Dispatch Instruction.  To successfully pass this test, within ten minutes of the receipt of the ERCOT Dispatch Instruction by the Resource’s QSE, the Resource’s response shall not be less than 95% of the requested MW deployment, nor more than 110% of the lesser of the following:

(a)	The Resource’s Ancillary Service Resource Responsibility for FFRS1; or

(b)	The requested MW deployment.

The requested MW deployment will be the sum of the Resource’s Ancillary Service Resource Responsibility for FFRS1 and the telemetered additional capacity between the net power consumption and the Low Power Consumption (LPC).  If a Resource has responded to an actual ERCOT Dispatch Instruction in compliance with items (a) and (b) above in the rolling 365-day period, ERCOT will use that response in lieu of an FFRS1 test.  If a Resource has not responded to an ERCOT Dispatch Instruction in compliance with items (a) and (b) above, in either a deployment event or an FFRS1 test, in any rolling 365-day period, it is subject to an FFRS1 test by ERCOT.  QSEs may request to have individual Load Resources aggregated for the purposes of Load interruption tests.  All performance evaluations will apply on an individual Resource basis.

(11)	ERCOT may revoke the Ancillary Service qualification of any Resource providing FFRS1 if that Resource has two Resource performance failures, either in a manual deployment event or a frequency triggered event, within any rolling 365-day period.  A performance failure is defined as a response less than95% or more than 110% of the Resource’s Ancillary Service Resource Responsibility for FFRS1 within 30 cycles of a triggering event or within ten minutes of an ERCOT Dispatch Instruction.  This shall result in disqualification of that Resource.  After six months of disqualification, a Resource may reapply for qualification provided it submits a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies and the disqualified Resource successfully passes a new test as specified in Section 8.1.1.2.1.2, Fast Frequency Response Service Qualification.

- 8.1.1.2	General Capacity Testing Requirements

(1)	Within the first 15 days of each Season, each QSE shall provide ERCOT a Seasonal HSL for any Generation Resource with a capacity greater than ten MW that will be operated during that Season.  ERCOT shall provide an appropriate form for QSEs to submit their Seasonal HSL data.  The Seasonal HSL form shall take into account auxiliary Load and gross and net real power capability of the Generation Resource.  Each QSE shall update its COP and telemetry, as necessary, to reflect the HSL of each of its Generation Resources in a given operating interval as well as other operational limitations.  The HSL shown in the COP for a Generation Resource may not be ramp rate-limited while the Real-Time telemetered value of HSL for the Generation Resource may be ramp rate-limited by the QSE representing the Generation Resource in order for the Generation Resource to meet its HSL using the testing process described in paragraph (2) below.

(2)	To verify that the HSL reported by telemetry is achievable, ERCOT may, at its discretion, conduct an unannounced Generation Resource test.  At a time determined solely by ERCOT, ERCOT will issue a Verbal Dispatch Instruction (VDI) to the QSE to operate the designated Generation Resource at its HSL as shown in the QSE’s telemetry at the time the test is initiated.  The QSE shall immediately upon receiving the VDI release all Ancillary Service obligations carried by the unit to be tested and shall telemeter Resource Status as “ONTEST.”  The QSE shall not be required to start the designated Generation Resource if it is not already On-Line when ERCOT announces its intent to test the Resource.  If the designated Generation Resource is operating at its Low Sustained Limit (LSL) when ERCOT sends the VDI to begin the test, the QSE shall have up to 60 minutes to allow the Resource to reach 90% of its HSL as shown by telemetry and up to an additional 20 minutes for the Resource to reach the HSL shown by telemetry at the time the test is initiated.  This time requirement does not apply to nuclear-fueled Generation Resources.  If the designated Generation Resource is operating between its LSL and 50% of its HSL shown by telemetry when ERCOT begins the test, the QSE shall have 60 minutes for the Resource to reach its HSL.  If the Resource is operating at or above 50% of its HSL shown by telemetry when ERCOT begins the test, the QSE shall have 30 minutes for the Resource to reach its HSL.  Once the designated Generation Resource reaches its HSL, the QSE shall hold it at that output level for a minimum of 30 minutes.  The HSL for the designated Generation Resource shall be determined based on the Real-Time averaged MW telemetered by the Resource during the 30 minutes of constant output.  After each test, the QSE representing the Generation Resource will complete and submit the test form using the Net Dependable Capability and Reactive Capability (NDCRC) application located on the Market Information System (MIS) Secure Area within two Business Days.

(3)	ERCOT may test multiple Generation Resources within a single QSE within a single 24-hour period.  However, in no case shall ERCOT test more than two Generation Resources within one QSE simultaneously.  All Resources On-Line in a Combined-Cycle Configuration will be measured on an aggregate capacity basis.  All QSEs associated with a jointly owned unit will be tested simultaneously.  Hydro, wind, and PhotoVoltaic (PV) generation will be excluded from unannounced generation capacity testing.  ERCOT shall not perform an unannounced Generation Resource test during a Watch or Energy Emergency Alert (EEA) event.  If an unannounced Generation Resource test is underway when a Watch or EEA event commences, ERCOT may cancel the test.

(4)	Should the designated Generation Resource fail to reach its HSL shown in its telemetry within the time frame set forth herein, the Real-Time averaged MW telemetered during the test shall be the basis for the new HSL for the designated Generation Resource for that Season.  The QSE shall have the opportunity to request another test as quickly as possible (at a time determined by ERCOT) and may retest up to two times per month.  The QSE may also demonstrate an increased value of HSL by operating the Generation Resource at an Output Schedule for at least 30 minutes.  In order to raise an output schedule above the Seasonal HSL, the QSE may set the Resource telemetered HSL equal to its output temporarily for the purposes of the demonstration tests.  After either a retest or a demonstration test, the MW capability of the Generation Resource based on the average of the MW production telemetered during the test shall be the basis for the new HSL for the designated Generation Resource for that Season.  Any requested retest must take place within three Business Days after the request for retest.

(5)	The telemetered value of HSL for the Generation Resource shall only be used for testing purposes as described in this Section or for system reliability calculations.

(6)	A Resource Entity owning a hydro unit operating in the synchronous condenser fast response mode to provide PFRS shall evaluate the maximum capability of the Resource each Season.

(7)	ERCOT shall maintain historical records of unannounced Generation Resource test results, using the information contained therein to adjust the Reserve Discount Factor (RDF) subject to the approval of the appropriate TAC subcommittee.  ERCOT shall report to the Reliability and Operations Subcommittee (ROS) annually or as requested by ROS the aggregated results of such unannounced testing (excluding retests), including, but not limited to, the number and total capacity of Resources tested, the percentage of Resources that met or exceeded their HSL reported by telemetry, the percentage that failed to meet their HSL reported by telemetry, and the total MW capacity shortfall of those Resources that failed to meet their HSL reported by telemetry.

(8)	QSEs who receive a VDI to operate the designated Generation Resource for an unannounced Generation Resource test may be considered for additional compensation under Section 6.6.9, Emergency Operations Settlement.  Any unannounced Generation Resource test VDI that ERCOT issues as a result of a QSE-requested retest will not be considered for additional compensation under Section 6.6.9.

(9)	All unannounced Generation Resource test VDIs will be considered as an instructed deviation for compliance purposes.

(10)	Before the start of each Season, a QSE shall provide ERCOT a list identifying each Controllable Load Resource that is expected to operate in a Season as a provider of Ancillary Service.  Prior to the beginning of each Season, QSEs shall identify the Controllable Load Resources to be tested during the Season and the specific week of the test if known.  Any Controllable Load Resource for which the QSE desires qualification to provide Ancillary Services shall have its Net Dependable Capability verified prior to providing Ancillary Services.

(11)	ERCOT shall verify the telemetry attributes of each qualified Load Resource as follows:

(a)	ERCOT shall annually verify the telemetry attributes of each Load Resource that is not a Controllable Load Resource providing Ancillary Services.  In the case of an Aggregate Load Resource (ALR), ERCOT will follow the validation procedures described in the Other Binding Document “Requirements for Aggregate Load Resource Participation in the ERCOT Markets.”  In addition, once every two years, any Load Resource qualified to provide FFRS using a high-set under-frequency relay shall test the correct operation of the under-frequency relay or the output from the solid-state switch, whichever applies.  However, if a Load Resource’s performance has been verified through response to an actual event, the data from the event can be used to meet the annual telemetry verification requirement for that year and the biennial relay-testing requirement.

(b)	ERCOT shall periodically validate the telemetry attributes of each Controllable Load Resource.  In the case of an ALR, ERCOT will follow the validation procedures described in the document titled “Requirements for Aggregate Load Resource Participation in the ERCOT Markets.”  If a QSE fails to meet its telemetry validation requirements, ERCOT may suspend the QSE and/or the Controllable Load Resource from participation in the applicable services or markets.  If disqualified pursuant to this paragraph, a QSE or Controllable Load Resource may reestablish its qualification by submitting a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies and by successfully passing a new ERCOT telemetry validation test.

(12)	Telemetry values of a Load Resource may be adjusted to reflect Distribution Losses, based on the ERCOT-forecasted Distribution Loss Factors (DLFs).  Load Resources may be adjusted for Distribution Losses using the same distribution loss code as assigned to the ESI ID.

(13)	A specific Load Resource to be used for the first time to provide Regulation, Non-Spin, FFRS, PFRS, or energy by following Security-Constrained Economic Dispatch (SCED) Base Points, must be tested to ERCOT’s reasonable satisfaction using actual Demand response as part of its qualification.  The test must take place at a time mutually selected by the QSE representing the Load Resource and ERCOT.  ERCOT shall make available its standard test document for Load Resource qualification required under this Section on the MIS Public Area.

(14)	Any changes to a Load Resource including changes to its capability to provide Ancillary Service requires updates by the Load Resource to the registration information detailing the change.  For Non-Opt-In Entities (NOIEs) representing specific Load Resources that are located behind the NOIE Settlement Metering points, the NOIE shall provide an alternative unique descriptor of the qualified Load Resource for ERCOT’s records.

(15)	Qualification of a Resource, including a Load Resource, remains valid for that Resource in the event of a change of QSE for the Resource, provided that the new QSE demonstrates to ERCOT’s reasonable satisfaction that the new QSE has adequate communications and control capability for the Resource.

(16)	For purposes of qualifying Quick Start Generation Resources (QSGRs), ERCOT shall issue a unit-specific VDI for the MW amount that the QSE is requesting to qualify its QSGR to provide.  The QSE shall telemeter an ONTEST Resource Status.  The QSGR will only be qualified to provide an amount not to exceed the observed output at the end of a ten-minute test period.

(17)	ERCOT may revoke the QSGR qualification of any QSGR for failure to comply with the following performance standard:

(a)	A QSGR, available for deployment by SCED, is deemed to have failed to start for the purpose of this performance measure if the QSGR fails to achieve at least 90% of the minimum ERCOT SCED Base Point, including zero Base Points, within ten minutes of the initial ERCOT SCED Base Point that dispatched the QSGR above zero MW output.

(b)	ERCOT may revoke a QSGR’s qualification if within a rolling 90-day period the number of QSGR failures to start, as determined by paragraph (a) above, exceeds the higher of three failures or 10% of the number of quick start mode startups made in response to SCED deployments.

(18)	If disqualified pursuant to paragraph (17) above, a QSGR may reestablish its QSGR qualification by submitting a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies and by successfully passing a new ERCOT QSGR test.

- 8.1.1.2.1	Ancillary Service Technical Requirements and Qualification Criteria and Test Methods

(1)	A QSE and the Resource that it represents must be qualified to provide Ancillary Services.  ERCOT shall develop and operate a qualification and testing program that meets the requirements of this Section for each Ancillary Service.

(2)	A QSE and the Resource that it represents must be qualified in accordance with this Section as an Ancillary Service and reserve provider and at ERCOT’s discretion will be required to re-qualify to provide Ancillary Service or reserve if acceptable performance as determined in accordance with this Section has not been maintained.

- 8.1.1.2.1.1	Regulation Service Qualification

(1)	A QSE control system must be capable of receiving Regulation Up Service (Reg-Up) and Regulation Down Service (Reg-Down) control signals from ERCOT’s Load Frequency Control (LFC) system, and of directing its Resources to respond to the control signals, in an upward and downward direction to balance Real-Time Demand and Resources.  .

(2) 	A QSE shall demonstrate to ERCOT that they have the ability to switch control to constant frequency operation as specified in the Operating Guides.  ERCOT’s direction to the QSE to operate on constant frequency will be considered a Dispatch Instruction.

(3) 	A QSE providing Reg-Up or Reg-Down shall provide ERCOT with the data requirements of Section 6.5.5.2, Operational Data Requirements.  Resources providing Reg-Up or Reg-Down must be capable of delivering the full amount of regulating capacity offered to ERCOT within five minutes.

(4)	A Resource providing Fast Responding Regulation Service (FRRS) shall be capable of independently detecting and recording system frequency with an accuracy of at least one mHz and a resolution of no less than 30 samples per second.  The Resource shall also be capable of measuring and recording MW output with a resolution of no less than 30 samples per second.

(5)	A Reg-Up and Reg-Down qualification test for each Resource is conducted during a continuous 60-minute period agreed on in advance by the QSE and ERCOT.  QSEs may qualify a Resource to provide Reg-Up or Reg-Down, or both, in separate testing.  ERCOT shall administer the following test requirements:

(a)	ERCOT shall confirm the date and time of the test with the QSE.

(b)	For the 60-minute duration of the test, when market and reliability conditions allow, the ERCOT Control Area Operator shall send a random sequence of increasing ramp, hold, and decreasing ramp control signals to the QSE for a specific Resource.  ERCOT shall maintain a duration interval, for each increasing ramp, hold, or decreasing ramp sequence, of no less than two minutes.  The control signals may not request Resource performance beyond the HSL, LSL, and ramp rate limit agreed on prior to the test.  During the test, ERCOT shall structure the test sequence such that at least one five-minute test interval is used to test the Resource’s ability to achieve the entire amount of Reg-Up or Reg-Down requested for qualification.

(c)	ERCOT shall measure and record the average real power output for each minute of the Resource(s) being tested represented by the QSE.  During at least one five minute duration interval selected to evaluate each of the Reg-Up and Reg-Down amounts being tested, the Generation/Controllable Load Resource Energy Deployment Performance (GREDP/CLREDP) calculated in accordance with Section 8.1.1.4.1, Regulation Service and Generation Resource/Controllable Load Resource Energy Deployment Performance, over the entire five minute interval must be less than or equal to 3.5%.  Additionally, in all other test sequence intervals, the Resource’s measured GREDP/CLREDP must be less than or equal to 5% as calculated for the entire duration of each test interval.

(d)	On successful demonstration of the above test criteria, ERCOT shall qualify that the Resource is capable of providing Regulation Service and shall provide a copy of the certificate to the QSE and the Resource.  The certificate shall state the amount in MWs the Resource is qualified for Reg-Up and Reg-Down.

(e)	A QSE representing a Resource qualified to provide Regulation Service shall not offer to provide more Regulation Service than the maximum capacity that the Resource is qualified to provide, as shown in the certificate provided to the QSE and the Resource.

(6)	A QSE may also qualify a Resource to provide Fast Responding Regulation Up Service (FRRS-Up), Fast Responding Regulation Down Service (FRRS-Down), or both.  In addition to the test criteria described in paragraph (5) above, ERCOT shall verify the following capabilities through testing:

(a)	ERCOT shall confirm the date and time of the test with the QSE.

(b)	The Resource seeking FRRS qualification will be required to demonstrate that it can deploy within one second of either (i) receipt of a deployment signal from ERCOT, or (ii) a deviation of frequency in excess of +/-0.09 Hz from 60 Hz.

(c)	Upon deployment, the Resource will be required to demonstrate that it can sustain the deployment for a minimum of eight minutes at a minimum level of 95% and a maximum level of 110% of the proposed maximum capacity obligation.

(d)	ERCOT shall use the Resource’s high-resolution recorded frequency and MW output data to determine whether the Resource met its performance obligations during the test.

(e)	On successful demonstration of the above test criteria, ERCOT shall qualify that the Resource is capable of providing FRRS and shall provide a copy of the certificate to the QSE and the Resource.  The certificate shall state the amount in MWs the Resource is qualified for FRRS-Up and FRRS-Down.

(f) 	A QSE representing a Resource qualified to provide FRRS shall not offer to provide more FRRS than the maximum capacity that the Resource is qualified to provide, as shown in the certificate provided to the QSE and the Resource.

- 8.1.1.2.1.2	Fast Frequency Response Service Qualification

(1)	FFRS may be provided by:

(a) 	Unloaded Generation Resources that are On-Line;

(b) 	Load Resources controlled by high-set under-frequency relays or similar trigger mechanisms;

(c) 	Direct Current Tie (DC Tie) response that stops frequency decay; or

(d) 	Controllable Load Resources.

(2)	Each Resource providing FFRS1 must be On-Line and shall also meet the following requirements:

(a) 	The under-frequency relay or similar trigger mechanism must have a delay of no more than 20 cycles (or 0.33 seconds for relays that do not count cycles). The total time from the time frequency first decays to a value low enough to initiate action up to the time when full Ancillary Service Resource Responsibility for FFRS1 is delivered should be no more than 30 cycles, including all relay and breaker operating times;

(b)	The initiation setting of the under-frequency relay or similar trigger mechanism shall not be any lower than 59.80 Hz; and

(c)	A Resource must demonstrate its ability to sustain the scheduled level of deployment for ten minutes at a minimum level of 95% but not more than a maximum level of 110% of the MW capacity for which the Resource seeks qualification for FFRS1.

(d)	Unless it is deployed via breaker action, a Resource providing FFRS1 shall be capable of measuring and recording MW output with a resolution of no less than 30 samples per second.

(3)	Each Load Resource providing FFRS2 must be loaded and capable of unloading the scheduled amount of FFRS2 within ten minutes of instruction by ERCOT and must either be immediately responsive to system frequency or be interrupted by action of under-frequency relays or similar trigger mechanism as described in (4) below.

(4)	Resources providing FFRS2 shall also meet the following requirements:

(a)	The under-frequency relay or similar trigger mechanism must have a delay of no more than 20 cycles (or 0.33 seconds for relays that do not count cycles). The total time from the time frequency first decays to a value low enough to initiate action up to the time when full Ancillary Service Resource Responsibility for FFRS2 is delivered should be no more than 30 cycles, including all relay and breaker operating times;

(b)	The initiation setting of the under-frequency relay or similar trigger mechanism shall not be any lower than 59.70 Hz;

(c)	A Resource must demonstrate its ability to maintain the scheduled level of deployment for an hour at a minimum level of 95% but no more than a maximum level of 150% of the MW capacity that the Resource seeks qualification for FFRS2; and

(d)	Unless it is deployed via breaker action, a Resource providing FFRS2 shall be capable of measuring and recording MW output with a resolution of no less than 30 samples per second.

(5)	Any QSE providing FFRS shall be capable of receiving ERCOT telemetered control deployments of FFRS.

(6)	Load Resources on high-set under-frequency relays or similar trigger mechanisms providing FFRS must provide a telemetered output signal, including breaker status and status of the under-frequency relay or similar trigger mechanism.

(7)	A qualification test for each Resource to provide FFRS is conducted during a continuous eight-hour period agreed to by the QSE and ERCOT.  ERCOT shall confirm the date and time of the test with the QSE:

(8)	To become and remain fully qualified as a provider of FFRS a Resource shall pass simulated or actual testing according to ERCOT procedures.  A Load Resource shall also perform verification testing as described in Operating Guide Section 8, Attachment G, Load Resource Tests.

(9)	On successful demonstration of all test criteria, ERCOT shall qualify that the Resource is capable of providing FFRS and shall provide a copy of the certificate to the QSE and the Resource Entity. The certificate shall state the amount in MWs the Resource is qualified for FFRS1 and/or FFRS2.

(10)	A QSE representing a Resource qualified to provide FFRS shall not offer to provide more FFRS than the maximum capacity that the Resource is qualified to provide, as stated in the certificate provided to the QSE and the Resource.

- 8.1.1.2.1.3	Primary Frequency Response Service Qualification

(1)	PFRS may be provided by:

(a) 	Unloaded Generation Resources that are On-Line;

(b) 	Hydro Generation Resources operating in the synchronous condenser fast response mode; or

(c) 	Controllable Load Resources.

(2)	The amount of PFRS provided by an individual Resource is limited to the median of its actual performance for the last eight Measurable Events.  Each Resource providing PFRS must be On-Line and must be immediately responsive to system frequency.

(3)	Hydro Generation Resources operating in the synchronous condenser fast-response mode may qualify to provide PFRS up to the hydro Generation Resource’s proven ten-second response capability (which may be 100% of the HSL).  The initiation setting of the automatic under-frequency relay shall not be lower than 59.90 Hz;

(4)	For any hydro Generation Resource operating as a generator, the amount of PFRS provided will be based on its actual performance for the last eight Measurable Events.

(5)	Any QSE providing PFRS shall be capable of receiving ERCOT telemetered SCED Base Points during the implementation of an EEA.  A QSE shall be capable of updating its Resource’s PFRS Ancillary Service Schedule within 15 seconds following an ERCOT instruction to release PFRS capacity to SCED.

(6)	Generation Resources providing PFRS shall have their Governors in service with their settings as specified by North American Electric Reliability Corporation (NERC) Reliability Standard BAL-001-TRE-1, Primary Frequency Response in the ERCOT Region.

(7)	Each QSE shall ensure that each Resource is able to meet the Resource’s obligations to provide its Ancillary Service Resource Responsibility.

(8)	A new or previously disqualified Resource seeking PFRS qualification shall be qualified for providing PFRS up to a capacity level demonstrated in Governor tests as specified in the Operating Guides.

(9)	A Private Use Network with registered Resources may use the gross HSL for qualification and establishing a limit on the amount of PFRS capacity that the Resources within the Private Use Network can provide.

(10)	After the initial qualification, a Resource’s qualification will be adjusted based on its performance as measured pursuant to NERC Reliability Standard BAL-001-TRE-1, Requirements R9 and R10.  ERCOT will limit the PFRS capacity for which an individual Resource qualifies based on the median of its performance during the last eight Measurable Events. ERCOT will measure the MW/0.1 Hz response during these events and calculate Resource’s capability for 1% or 0.6 Hz changes in frequency.

(11)	In qualifying and establishing limits on Resources for providing PFRS, ERCOT will consider the performance abilities and limitations of the technology of each Resource seeking to qualify as a PFRS provider. Because qualification requirements for different technologies may reflect their technical capabilities and limitations, ERCOT may impose other administrative limitations, including but not limited to setting a maximum limit of the total amount of capacity reservation that can be awarded to each type of Resource technology.

(12)	On successful demonstration of all test criteria, ERCOT shall qualify that the Resource is capable of providing PFRS and shall provide a copy of the certificate to the QSE and the Resource Entity.

(13)     A QSE representing a Resource qualified to provide PFRS shall not offer to provide more PFRS than the maximum capacity that the Resource is qualified to provide, as posted in accordance with paragraph (7) of Section 8.1.1.1, Ancillary Service and Reserves Qualification and Testing.

- 8.1.1.3.2	Fast Frequency Response Service Capacity Monitoring Criteria

(1)	ERCOT shall continuously monitor the capacity of each Resource to provide FFRS.  ERCOT shall consider, for each Resource providing FFRS capacity, the qualification amount, the actual generation or Load, the Ancillary Service Schedule for FFRS, the HSL/Maximum Power Consumption (MPC), the LSL/Low Power Consumption (LPC), and any other commitments of Ancillary Service capacity.

(2)	For Load Resources providing FFRS, the amount of FFRS capacity provided must be measured as the Load Resource’s average Load level in the last five minutes before deployment.

- 8.1.1.3.3	Primary Frequency Response Service Capacity Monitoring Criteria

(1)	ERCOT shall continuously monitor the capacity of each Resource to provide PFRS.  ERCOT shall consider, for each Resource providing PFRS capacity, the qualification amount, the actual generation or Load, the dead-band, droop setting, the Ancillary Service Schedule for PFRS, the HSL/MPC, the LSL/LPC, and any other commitments of Ancillary Service capacity.

(2)	A hydro Generation Resource that is capable of providing PFRS and that has a Resource Status of ONPFR is considered to be providing frequency responsive capability to the extent that it is not using that capacity to provide energy.

- 8.1.1.4.2	Fast Frequency Response Service Energy Deployment Criteria

(1)	Each QSE providing FFRS shall so indicate by appropriate entries in the relevant Resources’ Ancillary Service Schedules and by setting the Ancillary Service Resource Responsibilities accordingly. Control performance during periods in which ERCOT has deployed FFRS shall be based on the requirements below.

(2)	Within one minute following a deployment instruction, the QSE must update the telemetered Ancillary Service Schedule for FFRS for Generation Resources and Load Resources to reflect the deployment amount.

(3)	For any FFRS deployment event, ERCOT will collect the following data:

(a)	High speed event data from Resources that are not deployed via breaker action;

(b)	High speed event data from the recorders at ERCOT’s primary and back-up facilities;

(c)	High speed event data from phasor measurement units available to ERCOT; and

(d)	Telemetry data for all FFRS Resources with the Ancillary Service Resource Responsibility during the event.

(4) 	The performance of a Load Resource providing FFRS in response to an FFRS Dispatch Instruction shall be determined by subtracting the Load Resource’s actual Load response from the average of the telemetered net real power consumption values for the five minutes preceding the Dispatch Instruction (“meter before / meter after”).  The actual Load response is the average of the real power consumption data being telemetered to ERCOT during the Settlement Interval indicated in the Dispatch Instruction.

(5) 	For an FFRS1 deployment event triggered by an under-frequency event (frequency at or below 59.8 Hz). ERCOT will use the collected data to determine if the following requirements were met:

(a)	If the frequency reached the trip threshold for at least 20 cycles at the vicinity of where the FFRS1 Resource is located, the Ancillary Service Resource Responsibility for the Resource providing FFRS1 was fully deployed;

(b)	The Resource deployed 95% to 110% of its Ancillary Service Resource Responsibility in 30 cycles after the frequency reached 59.8 Hz;

(c)	The Resource sustained 95% to 110% of its Ancillary Service Resource Responsibility for the duration of the sustained response period, defined as ten minutes or until the time of recall instruction from ERCOT, whichever occurred first; and

(d)	The Resource restored its capability to provide its Ancillary Service Resource Responsibility within 15 minutes from the end of the deployment period.

(6)	For an FFRS1 deployment through a VDI, during implementation of the EEA, in addition to the data listed in paragraph (3) above, ERCOT will collect a voice recording of the VDI to document the time of the instruction.  The official start of the ramp period for the FFRS1 deployment is the end of the ERCOT operator’s acknowledgement that the read back of the instruction was correct.  ERCOT will use the collected data to determine if the following requirements were met:

(a)	The Resource deployed 95% to 110% of its Ancillary Service Resource Responsibility within ten minutes after the start of the ramp period;

(b)	The Resource sustained 95% to 110% of its Ancillary Service Resource Responsibility for the duration of the sustained response period, defined as ten minutes or until the time of recall instruction from ERCOT, whichever occurred first; and

(c)	The Resource restored its capability to provide its Ancillary Service Resource Responsibility within 15 minutes after ERCOT declares that the EEA is no longer needed.

(7)	For a Resource providing FFRS1 that was unable to return to its Ancillary Service Resource Responsibility within 15 minutes from the end of the deployment period, its QSE may replace the quantity of deficient FFRS1 capacity within that same 15 minutes using other Resources qualified to provide FFRS1 but not already committed to provide FFRS1.  The QSE may also use FFRS2 or PFRS (subject to the equivalency ratio) to satisfy the Resource’s Ancillary Service Resource Responsibility for FFRS1.

(8)	For an FFRS2 deployment event triggered by an under-frequency event (frequency at or below 59.7 Hz), ERCOT shall use collected data to determine if the following requirements were met:

(a)	If the frequency reached the trip threshold for at least 20 cycles at the vicinity of where the FFRS2 Resource is located, the Ancillary Service Resource Responsibility for the Resource providing FFRS2 was fully deployed;

(b)	The Resource deployed 95% to 150% of its Ancillary Service Resource Responsibility in 30 cycles after the frequency reached 59.7 Hz;

(c)	The Resource sustained 95% to 150% of its Ancillary Service Resource Responsibility for the deployment period; and

(d)	The Resource returned to service by the end of the designated recovery period of 180 minutes.

(9)	For an FFRS2 deployment through a VDI, in addition to the data listed in paragraph (3) above, ERCOT will collect a voice recording of the VDI to document the time of the instruction. The official start of the ramp period for the FFRS2 deployment is the end of the ERCOT operator’s acknowledgement that the read back of the instruction was correct.  ERCOT will use the collected data to determine if the following requirements were met:

(a)	The Resource deployed 95% to 150% of its Ancillary Service Resource Responsibility by the end of the ramp period;

(b)	The Resource sustained 95% to 150% of its Ancillary Service Resource Responsibility for the deployment period; and

(c)	The Resource returned to service by the end of the designated recovery period.

(10)	For a Resource providing FFRS2 that is unable to return to its Ancillary Service Resource Responsibility within 180 minutes of recall instruction, its QSE may replace the quantity of deficient FFRS2 capacity within that same 180 minutes using Resources qualified to provide FFRS2 but not already committed to provide FFRS2.  The QSE may also use FFRS1 or PFRS (subject to the equivalency ratio) to satisfy the Resource’s Ancillary Service Resource Responsibility for FFRS2.

(11)	QSEs are responsible for meeting their FFRS performance requirements at the portfolio level.  If a failure occurs at the portfolio level, as part of any compliance review ERCOT shall identify the individual Resource(s) responsible for the failure.  QSEs representing Resources providing FFRS will have an opportunity to provide ERCOT with site-specific high resolution data (at least 30 samples per second) for further analysis.  Regardless of the QSE’s portfolio-level performance, ERCOT may require any individual Load Resource that fails to meet its FFRS performance criteria to submit a corrective action plan, may take additional compliance review action, and may suspend a Load Resource’s qualification to provide FFRS for a pattern of non-performance.  A suspended Load Resource shall be required to successfully pass a qualification test in order to be reinstated.

8.1.1.4.3	Primary Frequency Response Service Energy Deployment Criteria

(1)	Each QSE providing PFRS shall so indicate by appropriate entries in the relevant Resources’ Ancillary Service Schedules and by setting the Ancillary Service Resource Responsibilities accordingly.  For Controllable Load Resources, the QSE shall control its Resources to operate their Scheduled Power Consumption minus any Ancillary Service deployments.

(2)	For all Measurable Events, ERCOT shall use the recorded data for each two-second scan rate value of real power output for each Generation Resource and Controllable Load Resource.  ERCOT shall use the recorded MW data beginning one minute before the start of the frequency excursion event until ten minutes after the start of the frequency excursion event.  Satisfactory performance must be measured by comparing actual Primary Frequency Response (PFR) to the expected PFR as required by NERC Reliability Standard BAL-001-TRE-1, Primary Frequency Response in the ERCOT Region.

- (3)	ERCOT shall monitor the PFR that is delivered during Measurable Events from Resources providing PFRS.  PFR performance must be analyzed by TAC using the performance metric specified in NERC Reliability Standard BAL-001-TRE-1.

(4) 	Performance during EEA events in which ERCOT has manually deployed PFRS shall be based on the following: within 15 seconds following a deployment instruction, the QSE must update the telemetered Ancillary Service Schedule for PFRS for Generation Resources and Controllable Load Resources to reflect the deployment amount.  The difference between the sum of the QSE’s Resource PFR schedules and the sum of the QSE’s Resource PFR responsibilities must be equal to the QSE’s total PFRS deployment instruction.

(5) 	If a Resource fails to meet the PFRS performance requirements described above, ERCOT may disqualify the Resource from providing PFRS and may take additional compliance review action. If disqualified, a Resource may reestablish its PFRS qualification no earlier than 30 days following the disqualification by:

(a) 	Submitting a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies, and

(b) 	Successfully passing a requalification test.