## Slide 1
Impact of Generation Outages on Economic Project Evaluation
Sandeep Borkar
Supervisor, Transmission Planning Assessment
PLWG

## Slide 2
Agenda
Background
Study Result
Conclusion

## Slide 3: Background
In October 2013, Brattle in its report “Recommendations for Enhancing ERCOT’s Long-Term Transmission Planning Process” recommended a list of additional economic benefit metrics that may be included in ERCOTs transmission planning processes
Recommendation related to Generation Outages:
  “We recommend that ERCOT add the simulation of forced generating unit outages to its long-term planning simulations. To ensure consistency across Base and Change cases, the draw of forced unit outage should be held constant”

## Slide 4: Purpose
ERCOT uses “Production Cost Savings” as a metric to measure benefits of a transmission project
ERCOT’s current economic simulations include maintenance outages based on pre-defined technology specific maintenance schedules
Investigate the impact of including generation outages on the production cost savings resulting from a transmission project

## Slide 5: Methodology
2017 economic start cases from 2014 RTP were used as a starting point
Production cost simulations were run under various generation outage scenarios
Start with a base case and a change case and determine production cost savings for a given transmission project (Reference production cost savings)
Prepare new base case and change case using different assumption for Generation Outages and determine the production cost savings for the same transmission project
Compare the change in production cost savings between the two simulations

## Slide 6: Generation outage scenarios
Generation Assumption | Notes
No Generator Outages | 
Maintenance schedules | Follow current process
Maintenance schedules and forced outage rates | 
Historical outages from year 2011 | Based on data from ERCOT Outage Scheduler
Historical outages from year 2012 | Based on data from ERCOT Outage Scheduler
Historical outages from year 2013 | Based on data from ERCOT Outage Scheduler
Historical outages from year 2014 | Based on data from ERCOT Outage Scheduler
Comanche peak 1 and 2 unavailable for 2017 | 
STP 1 and 2 unavailable for 2017 | 

## Slide 7: Constraints Ranked by Scenario
Constraint | No outages | STP Out | CMPK Out | Main. Only | Main. & Forced | 2011 Outages | 2012 Outages | 2013 Outages | 2014 Outages
Glenrose-Meridian | 1 | 6 | 1 | 1 | 3 | 1 | 3 | 8 | 5
Morris-Eagle Mountain | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 2 | 2
Beeville-Normanna | 3 | 5 | 5 | 5 | 5 | 3 | 1 | 1 | 1
Wolfgang-Rotan | 4 | 3 | 3 | 3 | 2 | 4 | 4 | 5 | 4
Goldwaite-San Saba Switch | 5 | 4 | 36 | 4 | 4 | 9 | 5 | 4 | 3
DuPont Switch Ingleside | 6 | 7 | 6 | 6 | 6 | 11 | 6 | 7 | 6
Singleton-Zenith | 7 | 2 | 12 | 7 | 7 | 10 | 7 | 6 | 10
Jack Creek-Twin Oak | 8 | 8 | 14 | 8 | 12 | 12 | 8 | 10 | 7
Spur-Aspermont | 9 | 11 | 8 | 10 | 9 | 17 | 12 | 14 | 11
Loop 337-GPI Switch | 10 | 9 | 17 | 12 | 8 | 8 | 9 | 3 | 8
Hamilton-Maverick | 11 | 12 | 13 | 11 | 11 | 21 | 13 | 13 | 16
Goldwaithe Auto | 12 | 10 |  | 17 | 17 | 32 | 15 | 31 | 20
Panhandle | 13 | 14 | 11 | 13 | 15 | 26 | 18 | 19 | 29

## Slide 8: Shadow price change by scenario
Chart: Annual Shadow Price Change ($/MW)
| Glenrose-Meridian | Morris-Eagle Mountain | Beeville-Normanna | Wolfgang-Rotan | Goldwaite-San Saba Switch | Dupont Switch Ingleside | Singleton-Zenith | Jack Creek-Twin Oak | Spur-Aspermont | Loop 337-GPI Switch | Hamilton-Maverick | Goldwaithe Auto | Panhandle under Base Case
STP Out | -21873.14 | 7478.19 | -17365.75 | 600.46 | 1857.73 | 8106.81 | 37304.84 | 9097.35 | 47.91 | 8537.05 | 1975.41 | 5234.65 | 68.83
CMPK Out | 111288.48 | 1226.21 | -20728.5 | -1170.75 | -30477.84 | 3305.48 | -8259.49 | -6973.67 | 55.59 | -4720.13 | -1974.92 | -5400.66 | 157.07
Maintainance Only | -6.35 | 341.46 | -19554.17 | -500.37 | -2474.98 | 405.56 | 599.15 | -622.98 | 1.52 | -729.15 | 209.65 | -2128.3 | 50.07
Maintainance+Forced | -18256.4 | 17952.8 | -25193.34 | -48.93 | -2755.91 | 7176.06 | -717.15 | -3752.08 | 0.28 | 3576.24 | 1344.7 | -2342.09 | 43.71
#REF! | 1
2011 Outages | 30342.68 | 32051.7 | 21675.7 | -815.86 | -5400.96 | 7959.14 | 11545.77 | 2035.41 | -31.98 | 21036.44 | 1476.9 | -1673.89 | -9.43
2012 Outages | -10669.88 | 4686.16 | 24155.92 | -3058.57 | -5335.55 | 7117.31 | 4878.38 | 1644.67 | 221.43 | 4281.69 | 1773.53 | 1742.93 | 155.64
2013 Outages | -27997.48 | 33425.61 | 136016.18 | -631.11 | 8268.37 | 13557.51 | 19294.68 | 3753.67 | -668.43 | 46786.49 | 3252.96 | -2614.07 | 131.29
2014 Outages | -17095.09 | 18800.09 | 48202.82 | -526.06 | 22361.55 | 16381.39 | -38.34 | 8270.68 | 438.76 | 10375.21 | 1727.25 | -1597.49 | -2764.39

## Slide 9: Shadow price change by scenario
Chart: Annual Shadow Price Change ($/MW)
| Glenrose-Meridian | Morris-Eagle Mountain | Beeville-Normanna | Wolfgang-Rotan | Goldwaite-San Saba Switch | Dupont Switch Ingleside | Singleton-Zenith | Jack Creek-Twin Oak | Spur-Aspermont | Loop 337-GPI Switch | Hamilton-Maverick | Goldwaithe Auto | Panhandle under Base Case
Maintenance Only | -6.35 | 341.46 | -19554.17 | -500.37 | -2474.98 | 405.56 | 599.15 | -622.98 | 1.52 | -729.15 | 209.65 | -2128.3 | 50.07
Maintenance+Forced | -18256.4 | 17952.8 | -25193.34 | -48.93 | -2755.91 | 7176.06 | -717.15 | -3752.08 | 0.28 | 3576.24 | 1344.7 | -2342.09 | 43.71

## Slide 10: Shadow price change by scenario
Chart: Annual Shadow Price Change ($/MW)
| Glenrose-Meridian | Morris-Eagle Mountain | Beeville-Normanna | Wolfgang-Rotan | Goldwaite-San Saba Switch | Dupont Switch Ingleside | Singleton-Zenith | Jack Creek-Twin Oak | Spur-Aspermont | Loop 337-GPI Switch | Hamilton-Maverick | Goldwaithe Auto | Panhandle under Base Case
2011 Outages | 30342.68 | 32051.7 | 21675.7 | -815.86 | -5400.96 | 7959.14 | 11545.77 | 2035.41 | -31.98 | 21036.44 | 1476.9 | -1673.89 | -9.43
2012 Outages | -10669.88 | 4686.16 | 24155.92 | -3058.57 | -5335.55 | 7117.31 | 4878.38 | 1644.67 | 221.43 | 4281.69 | 1773.53 | 1742.93 | 155.64
2013 Outages | -27997.48 | 33425.61 | 136016.18 | -631.11 | 8268.37 | 13557.51 | 19294.68 | 3753.67 | -668.43 | 46786.49 | 3252.96 | -2614.07 | 131.29
2014 Outages | -17095.09 | 18800.09 | 48202.82 | -526.06 | 22361.55 | 16381.39 | -38.34 | 8270.68 | 438.76 | 10375.21 | 1727.25 | -1597.49 | -2764.39

## Slide 11: Shadow price change by scenario
Chart: Annual Shadow Price Change ($/MW)
| Glenrose-Meridian | Morris-Eagle Mountain | Beeville-Normanna | Wolfgang-Rotan | Goldwaite-San Saba Switch | Dupont Switch Ingleside | Singleton-Zenith | Jack Creek-Twin Oak | Spur-Aspermont | Loop 337-GPI Switch | Hamilton-Maverick | Goldwaithe Auto | Panhandle under Base Case
STP Out | -21873.14 | 7478.19 | -17365.75 | 600.46 | 1857.73 | 8106.81 | 37304.84 | 9097.35 | 47.91 | 8537.05 | 1975.41 | 5234.65 | 68.83
CMPK Out | 111288.48 | 1226.21 | -20728.5 | -1170.75 | -30477.84 | 3305.48 | -8259.49 | -6973.67 | 55.59 | -4720.13 | -1974.92 | -5400.66 | 157.07

## Slide 12: Shadow price change by scenario
Chart: Annual Shadow Price Change ($/MW)
| Glenrose-Meridian | Morris-Eagle Mountain | Beeville-Normanna | Wolfgang-Rotan | Goldwaite-San Saba Switch | Dupont Switch Ingleside | Singleton-Zenith | Jack Creek-Twin Oak | Spur-Aspermont | Loop 337-GPI Switch | Hamilton-Maverick | Goldwaithe Auto | Panhandle under Base Case
STP Out | -21873.14 | 7478.19 | -17365.75 | 600.46 | 1857.73 | 8106.81 | 37304.84 | 9097.35 | 47.91 | 8537.05 | 1975.41 | 5234.65 | 68.83
CMPK Out | 111288.48 | 1226.21 | -20728.5 | -1170.75 | -30477.84 | 3305.48 | -8259.49 | -6973.67 | 55.59 | -4720.13 | -1974.92 | -5400.66 | 157.07
Maintainance Only | -6.35 | 341.46 | -19554.17 | -500.37 | -2474.98 | 405.56 | 599.15 | -622.98 | 1.52 | -729.15 | 209.65 | -2128.3 | 50.07
Maintainance+Forced | -18256.4 | 17952.8 | -25193.34 | -48.93 | -2755.91 | 7176.06 | -717.15 | -3752.08 | 0.28 | 3576.24 | 1344.7 | -2342.09 | 43.71
#REF! | 1
2011 Outages | 30342.68 | 32051.7 | 21675.7 | -815.86 | -5400.96 | 7959.14 | 11545.77 | 2035.41 | -31.98 | 21036.44 | 1476.9 | -1673.89 | -9.43
2012 Outages | -10669.88 | 4686.16 | 24155.92 | -3058.57 | -5335.55 | 7117.31 | 4878.38 | 1644.67 | 221.43 | 4281.69 | 1773.53 | 1742.93 | 155.64
2013 Outages | -27997.48 | 33425.61 | 136016.18 | -631.11 | 8268.37 | 13557.51 | 19294.68 | 3753.67 | -668.43 | 46786.49 | 3252.96 | -2614.07 | 131.29
2014 Outages | -17095.09 | 18800.09 | 48202.82 | -526.06 | 22361.55 | 16381.39 | -38.34 | 8270.68 | 438.76 | 10375.21 | 1727.25 | -1597.49 | -2764.39

## Slide 13: Transmission Projects Tested
  Cross Valley Project
    The project was removed in the base case and added back in the change case
Economic projects tested during 2014 RTP
  Wolfgang-Rotan-Roby line upgrade
  Eagle Mountain-Rosen Heights line upgrade
  Normanna-Beeville line upgrade
  Glen Rose-Meridian line upgrade

## Slide 14: Results Summary
Scenarios Studied | Cross Valley (345-kV portion) | Wolfgang-Rotan-Roby Line Upgrade | Eagle Mountain-Rosen Heights Line Upgrade | Normanna-Beeville Line Upgrade | Glen Rose-Meridian Line Upgrade
No Generator Outages | 2.01 | - | - | - | -
Maintenance schedules using current methodology | 3.10 | 0.58 | 0.65 | 0.15 | (0.14)
Maintenance schedules and forced outage rates | 0.90 | - | - | - | -
Historical outages from year 2011 | 0.63 | 0.13 | 1.71 | 1.05 | 0.10
Historical outages from year 2012 | 1.97 | 0.75 | 1.49 | 0.29 | (0.03)
Historical outages from year 2013 | 20.60 | 0.30 | 0.99 | 1.88 | 0.11
Historical outages from year 2014 | 31.68 | 0.28 | (0.50) | (1.32) | (0.41)
Comanche peak 1 and 2 unavailable for 2017 | (0.17) | - | - | - | -
STP 1 and 2 unavailable for 2017 | 2.73 | - | - | - | -
($M)

## Slide 15: Conclusion & Next steps
Although the shadow price may vary due to placement and timing of outages majority of the top 15 constraints identified under different scenarios remained consistent
Lack of variance in the production cost savings following the inclusion of generator outages suggests a nominal improvement to the savings metric

## Slide 16: Feedback & Next steps
Is there a strong case to develop a standard practice or criteria for generation outage consideration in economic planning analysis?
Could there be projects which offer economic insurance against such events? – such projects can be evaluated using methodologies used in the study

## Slide 17: Thank You!!
Sandeep Borkar
Sandeep.borkar@ercot.com
512.248.6642
Hong Xiao
Hong.Xiao@ercot.com
512.248.6642