## Slide 1
Reserve Discount Factor (RDF) and Changes to 2016 Ancillary Service Methodology
ERCOT Staff

## Slide 2: Discussion Points
Proposed Timeline
ERCOT Weather Zones
Reserve Discount Factor (RDF) Adjustment Analysis
Proposed changes to the 2016 Ancillary Service Methodology

## Slide 3: Proposed timeline for review of AS Methodology

## Slide 4: ERCOT Weather Zones

## Slide 5: Weather Stations

## Slide 6: Reserve Discount Factor Reserve Discount Factor

## Slide 7: August 13th, 2015 Benchmark
Chart: August 13th, 2015 Peak Hours PRC Benchmark
| 14:00 | 14:05 | 14:10 | 14:15 | 14:20 | 14:25 | 14:30 | 14:35 | 14:40 | 14:45 | 14:50 | 14:55 | 15:00 | 15:05 | 15:10 | 15:15 | 15:20 | 15:25 | 15:30 | 15:35 | 15:40 | 15:45 | 15:50 | 15:55 | 16:00 | 16:05 | 16:10 | 16:15 | 16:20 | 16:25 | 16:30 | 16:35 | 16:40 | 16:45 | 16:50 | 16:55 | 17:00 | 17:05 | 17:10 | 17:15 | 17:20 | 17:25 | 17:30 | 17:35 | 17:40 | 17:45 | 17:50 | 17:55 | 18:00
Difference | 0.0010777 | 0.43001 | 0 | 0.20107 | 1.2124 | 0.70002 | 0.656 | 0 | 0.069745 | 0 | 0.78421 | 1.6049 | 0 | 0.033654 | 0.15869 | 0 | 0.37739 | 0 | 1.9833 | 0 | 0 | 0 | 0.033755 | 0.034681 | 0.17443 | 0 | 1.4553 | 0 | 0.29196 | 0.074203 | 0 | 1.7787 | 0.059038 | 0.296 | 0.46665 | 0.47347 | 0 | 0.94047 | 0.13408 | 0.87685 | 0.89027 | 0 | 1.3464 | 0.11711 | 0.55009 | 0.79376 | 1.2356 | 0 | 0.57759
PRC Actual (Calculated) | 3454.0389 | 3381.1588 | 3299.9421 | 3049.3412 | 2823.9526 | 2834.0643 | 2862.409 | 2845.2298 | 2804.0684 | 2822.2254 | 2754.9865 | 2723.7113 | 2541.0209 | 2367.2799 | 2463.2735 | 2484.5578 | 2465.2278 | 2507.2368 | 2579.9209 | 2650.5013 | 2590.6721 | 2489.2209 | 2465.976 | 2375.5227 | 2420.3364 | 2476.1564 | 2497.6 | 2429.0945 | 2438.0562 | 2452.0808 | 2408.765 | 2459.7312 | 2436.3747 | 2403.0435 | 2447.8581 | 2423.6788 | 2388.9068 | 2629.5232 | 2669.7824 | 2699.4696 | 2725.3972 | 2825.1849 | 2929.7899 | 3011.5384 | 3076.8265 | 3203.3352 | 3253.8425 | 3278.5803 | 3393.2902
PRC (Real-Time) | 3454.04 | 3381.5888 | 3299.9421 | 3049.5423 | 2825.165 | 2834.7643 | 2863.065 | 2845.2298 | 2804.1382 | 2822.2254 | 2755.7707 | 2725.3162 | 2541.0209 | 2367.3135 | 2463.4322 | 2484.5578 | 2465.6052 | 2507.2368 | 2581.9042 | 2650.5013 | 2590.6721 | 2489.2209 | 2466.0097 | 2375.5574 | 2420.5108 | 2476.1564 | 2499.0554 | 2429.0945 | 2438.3481 | 2452.155 | 2408.765 | 2461.5099 | 2436.4338 | 2403.3395 | 2448.3248 | 2424.1522 | 2388.9068 | 2630.4637 | 2669.9165 | 2700.3464 | 2726.2875 | 2825.1849 | 2931.1363 | 3011.6555 | 3077.3766 | 3204.129 | 3255.0782 | 3278.5803 | 3393.8678

## Slide 8: August 13th, 2015 Benchmark
Chart: August 13th, 2015 Peak Hours PRC Analysis
| 14:00 | 14:05 | 14:10 | 14:15 | 14:20 | 14:25 | 14:30 | 14:35 | 14:40 | 14:45 | 14:50 | 14:55 | 15:00 | 15:05 | 15:10 | 15:15 | 15:20 | 15:25 | 15:30 | 15:35 | 15:40 | 15:45 | 15:50 | 15:55 | 16:00 | 16:05 | 16:10 | 16:15 | 16:20 | 16:25 | 16:30 | 16:35 | 16:40 | 16:45 | 16:50 | 16:55 | 17:00 | 17:05 | 17:10 | 17:15 | 17:20 | 17:25 | 17:30 | 17:35 | 17:40 | 17:45 | 17:50 | 17:55 | 18:00
PRC Actual (Calculated) | 3454.0389 | 3381.1588 | 3299.9421 | 3049.3412 | 2823.9526 | 2834.0643 | 2862.409 | 2845.2298 | 2804.0684 | 2822.2254 | 2754.9865 | 2723.7113 | 2541.0209 | 2367.2799 | 2463.2735 | 2484.5578 | 2465.2278 | 2507.2368 | 2579.9209 | 2650.5013 | 2590.6721 | 2489.2209 | 2465.976 | 2375.5227 | 2420.3364 | 2476.1564 | 2497.6 | 2429.0945 | 2438.0562 | 2452.0808 | 2408.765 | 2459.7312 | 2436.3747 | 2403.0435 | 2447.8581 | 2423.6788 | 2388.9068 | 2629.5232 | 2669.7824 | 2699.4696 | 2725.3972 | 2825.1849 | 2929.7899 | 3011.5384 | 3076.8265 | 3203.3352 | 3253.8425 | 3278.5803 | 3393.2902
PRC (0.99 Minimum RDF) | 3647.3451 | 3591.5492 | 3508.6371 | 3232.307 | 3029.0871 | 3004.1226 | 3047.0735 | 3024.9342 | 2990.6794 | 3020.1772 | 2939.6969 | 2897.5311 | 2718.9664 | 2525.9011 | 2592.1555 | 2630.4737 | 2607.3144 | 2629.176 | 2715.3492 | 2788.1098 | 2743.251 | 2644.8678 | 2606.4896 | 2501.6674 | 2535.3106 | 2588.1954 | 2629.3813 | 2571.8446 | 2552.0636 | 2571.6091 | 2529.0279 | 2571.6021 | 2555.5927 | 2528.6255 | 2564.708 | 2552.7525 | 2528.9043 | 2775.6245 | 2819.0105 | 2868.0423 | 2896.1986 | 2982.8932 | 3111.7024 | 3190.7179 | 3260.3672 | 3375.0168 | 3439.9954 | 3479.7472 | 3587.8815
PRC (No RDF) | 3707.3993 | 3699.3871 | 3615.0793 | 3339.3853 | 3139.8432 | 3087.2417 | 3142.0283 | 3113.7547 | 3090.7816 | 3117.2288 | 3027.6669 | 2987.6022 | 2803.4698 | 2672.4363 | 2718.4422 | 2764.7686 | 2735.8131 | 2741.4822 | 2843.8132 | 2921.915 | 2883.8992 | 2789.6916 | 2727.4792 | 2614.4276 | 2645.7075 | 2691.6504 | 2755.8995 | 2697.3205 | 2662.2643 | 2684.183 | 2645.6078 | 2676.7503 | 2665.376 | 2642.1307 | 2675.594 | 2672.45 | 2654.0928 | 2894.837 | 2937.4778 | 3006.3105 | 3034.8226 | 3108.4955 | 3254.1196 | 3334.0498 | 3396.7001 | 3500.2169 | 3581.3982 | 3623.5397 | 3729.5765
-PRC Actual (Calculated) determined using 0.98 RDF as in Real-Time.
-PRC calculated using a maximum 1% discount; effectively replacing any 0.98 RDF with a 0.99 RDF.
-PRC (No RDF) eliminates any discount from the HSL in the PRC equations for each individual unit.

## Slide 9: Low PRC Intervals (<3,00MW)
Chart: Count of 5-min Intervals Where PRC < 3,000MW
| 14:00 | 14:05 | 14:10 | 14:15 | 14:20 | 14:25 | 14:30 | 14:35 | 14:40 | 14:45 | 14:50 | 14:55 | 15:00 | 15:05 | 15:10 | 15:15 | 15:20 | 15:25 | 15:30 | 15:35 | 15:40 | 15:45 | 15:50 | 15:55 | 16:00 | 16:05 | 16:10 | 16:15 | 16:20 | 16:25 | 16:30 | 16:35 | 16:40 | 16:45 | 16:50 | 16:55 | 17:00 | 17:05 | 17:10 | 17:15 | 17:20 | 17:25 | 17:30 | 17:35 | 17:40 | 17:45 | 17:50 | 17:55 | 18:00
count | 1 | 1 | 1 | 1 | 2 | 2 | 3 | 3 | 3 | 4 | 3 | 3 | 6 | 6 | 6 | 8 | 7 | 8 | 9 | 7 | 7 | 11 | 11 | 9 | 12 | 11 | 13 | 15 | 14 | 14 | 15 | 14 | 11 | 10 | 13 | 13 | 7 | 3 | 4 | 2 | 1 | 2 | 2 | 1 | 0 | 0 | 0 | 0 | 0
299 sampled intervals where PRC < 3,000 MW between HE15 and HE18.

## Slide 10: Lowest PRC Intervals (<3,00MW) with RDF Increase
RDF Increase Impact on PRC Intervals < 3,000 MW |  | 
 | PRC (1% RDF) MW | PRC (2% RDF) MW
Average |  | 
All (HE15 - HE18) | 159 | 256
HE15 - HE16 | 157 | 260
HE17 - HE18 | 158 | 234
98th Percentile |  | 
All (HE15 - HE18) | 204 | 345
HE15 - HE16 | 202 | 335
HE17 - HE18 | 205 | 355
95th Percentile |  | 
All (HE15 - HE18) | 197 | 324
HE15 - HE16 | 194 | 324
HE17 - HE18 | 197 | 325

## Slide 11: ERCOT Temp –Weighted Weather zone temp – 4 Hour Block

## Slide 12: ERCOT’s Recommendation
  ERCOT recommends procuring a additional 200 MW of RRS during HE 15 through HE 18 (4 hour block) when there is higher likelihood of RDF being less than 1 across all the weather zones for all hours within a block. (This assumes up to 200 MW of RRS adjustment for 1% RDF)
  This increases RRS procurement for HE 15 through HE 18 in July, and August of 2016

## Slide 13: Current Vs Proposed RRS

## Slide 14: Current Vs Proposed RRS

## Slide 15: Questions and Recommendations

## Slide 16: ERCOT Temperature – Weighted Average Temp of Weather zone

## Slide 17: ERCOT Temperature – Weighted Average Temp of Weather zone