| PGRR Number | 042 | PGRR Title | Regional Transmission Plan Model Reserve Requirement and Load-Generation Imbalance Methodology |
| --- | --- | --- | --- |

| Date | April 8, 2016 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Jeff Billo |
| E-mail Address | jbillo@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6334 |
| Cell Number |  |
| Market Segment | Not applicable. |

Comments

Since filing comments on Planning Guide Revision Request (PGRR) 042 in July 2015, ERCOT has been considering the effect those comments would have on the planning process as well as other comments submitted by stakeholders.  Based on those considerations ERCOT is offering additional comments in an effort to bring PGRR042 to completion.  These comments are intended to address the following issues:

- As discussed at the Planning Working Group (PLWG) meeting February 17, 2016, when a planning case has an imbalance between generation and demand there are fundamentally two adjustments that can be made to resolve the imbalance so that the case can be solved. One adjustment would be to reduce Load.  The other adjustment would be to add/increase generation.  With these comments the Planning Guide would leave open the possibility of using Load scaling but would require ERCOT to perform a sensitivity analysis involving the addition of generation with Standard Generation Interconnection Agreements (SGIAs) but not meeting Planning Guide Section 6.9 requirements for large (Tier 1) projects.  In this manner large projects would be evaluated using both techniques: (1) reducing Load, i.e. Load scaling; (2) adding generation.

- Transmission planners need to maintain discretion and flexibility in setting up the base cases used in the various studies they perform.  As was seen with the DC Tie modeling recommendations in the PLWG CDR-Planning Model White Paper, being too prescriptive with assumptions in rules can lead to unintended consequences and unnecessarily limit a planner.  However, in order to provide for the needed transparency around study assumptions ERCOT believes the Planning Guide should require ERCOT to give proper notice and an opportunity to comment to stakeholders (via the Regional Planning Group) regarding study assumptions for the Regional Transmission Plan and Tier 1 independent reviews.

With these changes ERCOT is hopeful that fruitful discussion at PLWG can bring this PGRR to completion.

Revised Cover Page Language

| Planning Guide Sections Requiring Revision | 3.1.1.2, Regional Transmission Plan 3.1.3, Project Evaluation 3.1.3.1, Definitions of Reliability-Driven and Economic-Driven Projects 3.1.4.1, Development of Regional Transmission Plan 3.1.4.1.1, Regional Transmission Plan Cases (new) 3.1.4.2, Use of Regional Transmission Plan |
| --- | --- |

Revised Proposed Guide Language

- 3.1.1.2	Regional Transmission Plan

(1)	The Regional Transmission Plan is developed annually by ERCOT, in coordination with the RPG and Transmission Service Providers (TSPs).  The Regional Transmission Plan addresses regional and ERCOT-wide reliability and economic transmission needs and the planned improvements to meet those needs for the upcoming six years starting with the SSWG base cases.  These planned improvements include projects previously approved by the ERCOT Board, projects previously reviewed by the RPG, new projects that will be refined at the appropriate time by TSPs in order to complete RPG review, and the local projects currently planned by TSPs.  Combined, these projects represent ERCOT’s plan which addresses the reliability and efficiency of the ERCOT System in order to meet North American Electric Reliability Corporation (NERC) Reliability Standards, the Protocols, Operating Guides and this Planning Guide.  Projects that are included in the Regional Transmission Plan are not considered to have been endorsed by ERCOT until they have undergone the appropriate level of RPG Project Review as outlined in Protocol Section 3.11.4, Regional Planning Group Project Review Process, if required.  The process used by ERCOT to develop the Regional Transmission Plan is outlined in Section 3.1.4, Regional Transmission Plan Development Process.

(2)	ERCOT shall post the Regional Transmission Plan to the Market Information System (MIS) Secure Area by December 31 of each year.

(3)	ERCOT shall include in the Regional Transmission Plan report a list of Transmission Facilities that are loaded above 95% of their applicable Ratings for the following conditions:

(a)	Normal system conditions; or

(b)	Following the contingency loss of a single generating unit, transmission circuit, transformer, or common tower outage.

- 3.1.3	Project Evaluation

(1)	ERCOT and the RPG shall evaluate proposed transmission projects using a variety of tools and techniques as needed to ensure that the system is able to meet applicable reliability criteria in a cost-effective manner.  For most proposed projects, several alternatives will be identified to meet the reliability criteria or other performance improvement objectives that the proposed project is designed to meet.  The project alternative with the expected lowest cost over the life of the project is generally recommended, subject to consideration of the expected long-term system needs in the area, and consideration of the relative operational impacts of the alternatives.

(2)	In some cases, one alternative may be to dispatch the system in such a way that all reliability requirements are met, even without the proposed transmission project or any transmission alternative, resulting in a less efficient dispatch than what would be required to meet the reliability requirements if the proposed project was in place.  Consideration of the merits of this alternative relative to the proposed transmission project is more complex.  To facilitate the discussion and consideration of these alternatives, ERCOT has adopted certain definitions and practices, described in paragraph (4) of Protocol Section 3.11.2, Planning Criteria, and Sections 3.1.3.1, Definitions of Reliability-Driven and Economic-Driven Projects, and 3.1.3.2, Reliability-Driven Project Evaluation below.

(3)	In conducting an independent review of any project, ERCOT may, in its discretion, make adjustments to the planning case to ensure that the case reaches a solution.  When conducting an independent review of any project classified as Tier 1 pursuant to Protocol Section 3.11.4, Regional Planning Group Project Review Process, ERCOT must provide reasonable advance notice to the RPG of any proposed adjustments and an opportunity for stakeholder comment on them.

(4) 	As part of its independent review of any project classified as Tier 1 pursuant to Protocol Section 3.11.4, ERCOT shall perform a sensitivity analysis to evaluate the effect on a recommended transmission project of proposed Generation Resources in or near the study area that have signed Standard Generation Interconnection Agreements (SGIAs) but were not included in the study cases because they did not meet all of the requirements for inclusion in the cases pursuant to Planning Guide Section 6.9, Addition of Proposed Generation Resources to the Planning Models.  ERCOT shall not consider the results of this sensitivity analysis in determining project need in its independent review of the project.

- 3.1.3.1	Definitions of Reliability-Driven and Economic-Driven Projects

(1)	Proposed transmission projects are categorized for evaluation purposes into two types:

(a)	Reliability-driven projects; and

(b)	Economic-driven projects.

(2)	The differentiation between these two types of projects is based on whether a simultaneously-feasible, security-constrained generating unit commitment dispatch is expected to be available for all hours of the planning horizon that can resolve the system reliability issue that the proposed project is intended to resolve.  If it is not possible to simulate a dispatch of the Generation Resources such that all reliability criteria are met without the project, and the addition of the project allows the reliability criteria to be met, then the project is classified as a reliability-driven project.  If it is possible to simulate a dispatch of the Generation Resources in such a way that all reliability criteria are met without the project, but the project may allow the reliability criteria to be met at a lower total cost, then the project is classified as an economic-driven project.  When performing a simulation of the generating unit commitment and dispatch, only contingencies and limits that would be considered in the operations horizon shall be simulated.

- 3.1.4.1	Development of Regional Transmission Plan

(1)	The planning process begins with computer modeling studies of the generation and Transmission Facilities and substation Loads under normal conditions in the ERCOT System.  Contingency conditions along with changes in Load and generation that might be expected to occur in operation of the ERCOT Transmission Grid are also modeled.  To maintain adequate service and minimize interruptions during Outages, model simulations are used to identify adverse results based upon the planning criteria and to examine the effectiveness of various problem-solving alternatives.

(2)	The effectiveness of each alternative will be evaluated under a variety of possible operating environments because Loads and operating conditions cannot be predicted with certainty.  As a result, repeated simulations under different conditions are often required.  In addition, options considered for future installation may affect other alternatives so that several different combinations must be evaluated, thereby multiplying the number of simulations required.

(3)	Once feasible alternatives have been identified, the process is continued with a comparison of those alternatives.  To determine the most favorable, the short-range and long-range benefits of each alternative must be considered including operating flexibility and compatibility with future plans.

- 3.1.4.1.1	Regional Transmission Plan Cases

(1)	The starting base cases for the Regional Transmission Plan development are created by removing all Tier 1, 2 and 3 projects that have not received RPG acceptance or, if applicable, ERCOT endorsement  RPG Pfrom the most recent SSWG base cases.

(2)	ERCOT shall set all non-seasonal Mothballed Generation Resources to out of service in the Regional Transmission Plan reliability base cases. ERCOT shall add proposed Generation Resources that have met the criteria for inclusion in Section 6.9, Addition of Proposed Generation Resources to the Regional Transmission Plan base cases.

(3)	ERCOT shall update the Regional Transmission Plan reliability and economic base cases to reflect any updates to the amount of Switchable Generation Resource capacity available to the ERCOT Region.

(4)	ERCOT may, in its discretion, make other adjustments to any Regional Transmission Plan base case to ensure that the case reaches a solution.  ERCOT must provide reasonable advance notice to the RPG of any proposed adjustments and an opportunity for stakeholder comment on them.

- 3.1.4.2	Use of Regional Transmission Plan

(1)	If a project submitted for RPG review is included in the Regional Transmission Plan, and no changes are identified which would affect the need for the proposed project through the 21-day comment period described in Section 3.1.5, Regional Planning Group Comment Process, then the Regional Transmission Plan may serve as the ERCOT Independent Review of the proposed project, if required.

(2)	Tier 1, 2, and 3 projects that are included in the Regional Transmission Plan should be submitted for RPG Project Review at an appropriate lead time.  Generally, this lead time should be sufficient to allow the review to be completed before the TSP reaches the decision point at which it must initiate the engineering and procurement in order to meet the required in-service date, but not farther in advance than is necessary.  In general, these lead times will be three to four months for Tier 3 projects and six to seven months for Tier 1 and 2 projects.

(3)	Tier 1, 2 and 3 projects that are included in the Regional Transmission Plan but do not reach this decision point before the development of the next year’s Regional Transmission Plan begins will be removed from the case used to develop the Regional Transmission Plan and will be re-evaluated as a part of the development of this subsequent Regional Transmission Plan.