| SCR Number | 788 | SCR Title | Addition of Integral ACE Feedback to GTBD Calculation |
| --- | --- | --- | --- |
| Date of Decision |  | April 14, 2016 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | Upon system implementation |  |
| Priority and Rank Assigned |  | Priority – 2016; Rank – 1640 |  |
| Supporting Protocol or Guide Section(s) (If applicable) |  | 6.5.7.3, Security Constrained Economic Dispatch |  |
| Other Document Reference/Source |  | None |  |
| System Change Description |  | This System Change Request (SCR) updates the formula used by the Resource Limit Calculator to calculate the Generation To Be Dispatched (GTBD) value. The update will include the addition of Area Control Error (ACE) Integral times a configurable factor that captures the long-term Dispatch trend to help minimize GTBD oscillations from one Security-Constrained Economic Dispatch (SCED) interval to the next. The analysis further shows that having an Integral ACE feedback would reduce the amount of manual Time Error corrections performed. Integral ACE is calculated from Raw ACE by integrating the raw ACE value over a configurable amount of time (X seconds) and adding it to the previous 4 second Integral ACE, as shown below: Integral ACE (current 4 sec) = Integral ACE(last 4 sec) + [(Raw ACE(Current 4 sec)*(Current Time – Last AGC run time))/X] In general, Integral ACE provides a good indication of which direction ACE has been trending. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | This SCR will reduce the amount of Regulation Service deployed. |  |
| PRS Decision |  | On 3/10/16, PRS voted to recommend approval of SCR788 as submitted. There was one abstention from the Consumer Market Segment. All Market Segments were present for the vote. On 4/14/16, PRS unanimously voted to endorse and forward to TAC the 3/10/16 PRS Report and the Impact Analysis for SCR788 with a recommended priority of 2016 and a rank of 1640. All Market Segments were present for the vote. |  |
| Summary of PRS Discussion |  | On 3/10/16, there was no discussion. On 4/14/16, participants requested as much notice as possible prior to the implementation of this change to allow them adequate time to update their systems. |  |

| Sponsor |  |
| --- | --- |
| Name | Mike Noth on behalf of the Performance, Disturbance, Compliance Working Group (PDCWG) |
| E-mail Address | mike.noth@lcra.org |
| Company | Lower Colorado River Authority (LCRA) |
| Phone Number | 512-578-2326 |
| Cell Number | 512-751-0308 |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Cory Phillips |
| E-Mail Address | cory.phillips@ercot.com |
| Phone Number | 512-248-6464 |

Business Case for Proposed System Change

Issue:

ERCOT’s current GTBD calculation does not have a longer-term Resources performance and dispatch accuracy feedback.  Besides helping lower the Regulation bias, this feedback is also expected to reduce the manual Time Error corrections.

Resolution:

Following modifications are needed:

- Add the K5 configurable factor together with the Integral ACE calculated in the Energy Management System (EMS).

- The Maximum Integral ACE Feedback, Maximum Regulation Deployed Feedback and K5 factor should all be tunable parameters.

Generation To Be Dispatched = Total Gen + K1*10*System Load Frequency Bias + K2*[(net non-conforming Load) – (net filtered non-conforming Load)] + K3*5*PLRR + K4*Regulation Deployed + K5*ACE Integral

|ACE Integral| ≤ Max Integral ACE Feedback

|Regulation Deployed| ≤ Max Regulation Deployed Feedback

- Ability to integrate the Raw ACE over X seconds for use in the ACE Integral equation, where the variable X can be configured.