## Slide 1
UFLS Survey Explanation
April 22, 2016

## Slide 2: Background
ERCOT issued the UFLS Survey Notice on 4/1/2016
This year ERCOT is requesting station level detail
Some questions have been raised and this presentation is to help clarify expectations

## Slide 3: Reminder of Op Guide Requirement
2.6 Requirements for Under-Frequency and Over-Frequency Relaying
2.6.1 Automatic Firm Load Shedding
At least 25% of the ERCOT System Load that is not equipped with high-set under-frequency relays shall be equipped at all times with provisions for automatic under-frequency load shedding. The under-frequency relays shall be set to provide Load relief as follows:
(2) With the assistance of applicable Transmission Service Providers (TSPs), ERCOT will, prior to the peak each year, survey each Distribution Service Provider’s (DSP’s) compliance with the automatic Load shedding steps above, and report its findings to the Technical Advisory Committee (TAC). For minimum compliance, DSPs are obligated to meet the prescribed percent values at all times. It is not permitted to use rounding to meet the minimum. ERCOT will direct a review of the automatic firm Load shedding program whenever warranted by conditions. At a minimum, this review will follow the Reliability and Operations Subcommittee (ROS) directed dynamic simulations of automatic firm Load shedding conducted at five-year intervals beginning in the Summer of 2001.
(3) Additional under-frequency relays may be installed on Transmission Facilities with the approval of ERCOT provided the relays are set at 58.0 cycles or below, are not directional, and have at least 2.0 seconds time delay. A DSP may by mutual agreement arrange to have all or part of its automatic Load shedding requirement performed by another entity. ERCOT will be notified and provided with the details of any such arrangement prior to implementation.

## Slide 4: Question #1
Do I need to show compliance for 5%10%10% at each DSP
  Yes, but….
  Many DSP have TO Designation or Agency agreements in place
  In that type of arrangement for a scenario where 8 DSPs roll up to a single TO, then the 5/10/10 is tracked at the TO level.

## Slide 5: Question #2
Is the 5%, 10%, 10% a cumulative response to meet a 25% value?
  No, the requirements are independent for each frequency level and should be set to respond accordingly.
  For 100MW area load
    At least 5% should be armed to trip at 59.3Hz (circuits of 5MW or more)
    An additional 10% should be armed to trip at 58.9 Hz (circuits of additional 10MW or more)
    An additional 10% should be armed to trip at 58.5 Hz (circuits of additional 10MW or more)
    Not allowed to count extra/excess MW from another category
      Invalid example 8 + 9 + 8 = 25 but does not meet individual requirement for each level

## Slide 6: Question #3
How do we address a Load Resource in the survey?
  In an area where there is currently 100MW of Load, inclusive of 15MW of Load Resource(s)
    The 5/10/10 survey response is still based on the 100 MW of area load
    Since the 15MW is a paid service that triggers at 59.7Hz, it is not part of the UFLS 5/10/10
    In the survey, there is no requirement for identifying Load Resource(s) impacted circuits
    In an actual event, the QSE is responsible for deploying the Load Resource at 59.7Hz and the DSP is responsible for the 5/10/10 UFLS requirement.
  Language may be unclear, but for the survey ERCOT considers the total area load as being the current load served, inclusive of Load Resources consuming power
  “At least 25% of the ERCOT System Load that is not equipped with high-set under-frequency relays shall be equipped at all times with provisions for automatic under-frequency load shedding.”

## Slide 7: Reminder of Survey Deadline
LONG DESCRIPTION: In accordance with Nodal Operating Guides Section 2.6.1, Automatic Firm Load Shedding, ERCOT requests that Transmission and/or Distribution Service Providers (TDSPs) complete the attached Under-Frequency Load Shedding (UFLS) survey. Distribution Service Providers (DSPs) must either complete the survey or ensure that their data is included in a survey completed by their Transmission Services Provider (TSP).
The survey must be completed for a test hour of May 12, 2016 at 11:00 A.M Central Prevailing Time (CPT). Each ERCOT Transmission Service Provider is required to make arrangements to secure the measured load for the above test hour.
ACTION REQUIRED: ERCOT appreciates your cooperation and asks that the attached survey be submitted no later than June 12, 2016 via e-mail to Compliance@ercot.com