| MGRR Number | 024 | MGRR Title | Add line length requirement to AC Line Segment |
| --- | --- | --- | --- |
| Date |  | 04/19/2016 |  |
| Submitter’s Information |  |  |  |
| Name |  | Chris Ngai |  |
| E-mail Address |  | cngai@ercot.com |  |
| Company |  | ERCOT |  |
| Phone Number |  | 512-248-3941 |  |
| Cell Number |  |  |  |
| Market Segment |  |  |  |

Comments

Clarification of conductor ratings for OSR owners not owning the physical AC Line Segment.

| Overall NMMS User Benefit | Reduce ambiguity of conductor rating entries for owners not owning the physical AC Line Segment. |
| --- | --- |
| Overall NMMS User Impact |  |
| ERCOT Impact |  |

Revised Proposed Modeling Guidelines Language

### Modeling Approach for Ratings AnalogLimit

The ERCOT data dictionary utilizes the AnalogLimits to specify the limit values for the Analog measurement.  AnalogLimits are modeled under the AnalogLimitSet. The attribute limittype is utilized to classify the type of the AnalogLimit being modeled. The commonly utilized types are fifteen minute rating, two hour rating, normal rating and conductor rating. In the ERCOT CIM model every AnalogLimitSet can have a maximum of four distinctly typed AnalogLimits as its children. In the figure, four AnalogLimits, namely 15MN, CONDUCTOR, EMGY and NRML are modeled as under of the AnalogLimitSet, ALS.  For CONDUCTOR rating, if owner of OSR is not the owner of AC Line Segment, 9999 may be entered into attribute Value.

#### Attributes

The attributes for AnalogLimit are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| Value | The value to supervise against. Should be Null for SCADA AnalogLimit. | Double Float | None | Null |
| Deadband | Amount, expressed as a percentage of the range between upper and lower threshold, used in the limit comparison to eliminate extraneous alarms generated when an Analog value oscillates around a limit. When either threshold is null, the percentage is that of the non-null limit. | Double Float | None | 5 |
| LimitType | Type of limit. | Enumeration | None | Normal Rating |
| LowerThreshhold | The value below which the Analog is considered in violation of the limit. When the Upper Threshold is null, only the Lower Threshold is checked for violation. | Float | None | -24 |
| UpperThreshhold | The value above which the Analog is considered in violation of the limit. When the low limit is null, only the high limit is checked for violation. This value must be greater than the Lower Threshold. | Float | None | 24 |
| ForbiddenRegion | T = The Analog is in violation if it is smaller than the Upper Threshold and larger than the Lower Threshold. | Boolean | False | False |
| IgnoreLimitChecking | T = The limit should be ignored when checking the Analog for limit violations. | Boolean | False | False |
| UsePercentage | T = The value displayed in the deadband field (below) is the percentage deadband. Otherwise, the value displayed is the numeric deadband. | Boolean | False | False |
| Zonal Attribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 123 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |

#### Linkage

No required links