| MGRR Number | 025 | MGRR Title | Add line length requirement to AC Line Segment |
| --- | --- | --- | --- |
| Date |  | 04/19/2016 |  |
| Submitter’s Information |  |  |  |
| Name |  | Chris Ngai |  |
| E-mail Address |  | cngai@ercot.com |  |
| Company |  | ERCOT |  |
| Phone Number |  | 512-248-3941 |  |
| Cell Number |  |  |  |
| Market Segment |  |  |  |

Comments

Add line length as required attribute in AC Line Segment.

| Overall NMMS User Benefit | More accurate line model in IMM because of enhanced line data validation using line length. |
| --- | --- |
| Overall NMMS User Impact | Add line length as required field; however, most of the AC Line Segments have line length not equal to zero in IMM. |
| ERCOT Impact | More accurate line model in IMM because of enhanced line data validation using line length. |

Revised Proposed Modeling Guidelines Language

- Modeling ACLineSegment

  - Modeling Approach

The ACLineSegment class represents an AC transmission line that connects two different Substations.  An ACLineSegment cannot be contained within a single Substation.  Additionally, an ACLineSegment must be underneath a Line instance and must have two Terminals.  ERCOT shall develop the naming convention with the assistance of the TSP and the approval of TAC.

ACLinesegment cannot go between different voltage levels.

Figure 1 - ACLineSegment

  - Attributes

Attributes for a ACLineSegment are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| name | Name of the instance of this class | String |  | CB_1 |
| 15 minute rating Max Shadow Price | 15 minute rating Max Shadow price | Double Float |  |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| b0ch | Zero sequence shunt (charging) susceptance, uniformly distributed, of the entire line section. | Double Float |  |  |
| bch | Positive sequence shunt (charging) susceptance, uniformly distributed, of the entire line section. | Double Float |  |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool |  |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool |  |  |
| Emergency Max Shadow Price | Emergency Max Shadow price | Double Float |  |  |
| g0ch | Zero sequence shunt (charging) conductance, uniformly distributed, of the entire line section. | Double Float |  |  |
| gch | Positive sequence shunt (charging) conductance, uniformly distributed, of the entire line section. | Double Float |  |  |
| Latitude | Latitude coordinates. | Float | None |  |
| length | Segment length for calculating line section capabilities (long length units). | Float |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| Max Shadow Price | Max shadow price | Double Float |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Long Int | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | String |  |  |
| PSS/E | Attribute will give Information Model Manager modelers control over the PSS/E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | String |  |  |
| r | Positive sequence series resistance of the entire line section. | Double Float |  |  |
| R0 | Zero sequence series resistance of the entire line section. | Double Float |  |  |
| Remove | The equipment is removed from the network. | Bool |  |  |
| Remove Enable | The equipment can be removed from the network in the EMS. | Bool |  |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool |  |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool |  |  |
| teid | Transmission Element ID | Integer | Auto-populated |  |
| x | Positive sequence series reactance of the entire line section. | Double Float |  |  |
| X0 | Zero sequence series reactance of the entire line section. | Double Float |  |  |

  - Linkage

The required links for ACLineSegment are defined in Table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| BaseVoltage | BaseVoltage to which this ACLineSegment belongs | Network/Base Voltage |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. Creator is the person who is submitting the entry through PTC, who is associated with the company that owns the equipment. Ownership and Operatorship point to a company whereas a creator points to a userid. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |