## Slide 1: LINE 69H REBUILD AND CONVERSION PROJECT
ERCOT Regional Planning Group
April 21,2016

## Slide 2: TNMP SERVICE AREA

## Slide 3: PRESENT WEST TEXAS NORTH(WTN) AREA

## Slide 4: PREVIOUS TNMP RPG SUBMITTALS FOR WTN AREA
REBUILD LINE 69D(WINK – PECOS) TO 138KV STANDARDS (OPERATE AT 69KV)
IN-SERVICE
REBUILD LINE 69E(WINK – PECOS) TO 138KV STANDARDS (OPERATE AT 69KV)
IN-SERVIVE
PIG CREEK 138KV TIE TO AEP
BP2017

## Slide 5: WTN AREA BP2017 ONE-LINE DIAGRAM

## Slide 6: 2016-2022 LOAD FORECAST FOR WTN AREA
Total Coincident Peak Load Forecasts Not Including Pending Agreements |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  |  |  | Year |  |  |  |  |  |  |  |  |  |  | 
 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 |  |  |  |  |  |  |  | 
 |  |  |  | MW |  |  |  |  |  |  |  |  |  |  | 
 | 181 | 208 | 223 | 237 | 251 | 252 | 254 |  |  |  |  |  |  |  | 
Total Coincident Peak Load Forecasts Including Pending Agreements |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  |  |  | Year |  |  |  |  |  |  |  |  |  |  | 
 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 |  |  |  |  |  |  |  | 
 |  |  |  | MW |  |  |  |  |  |  |  |  |  |  | 
 | 254 | 302 | 318 | 336 | 351 | 353 | 355 |  |  |  |  |  |  |  | 
 |  |  |  | Year |  |  |  |  |  |  |  |  |  |  | 
NET MW | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 |  |  |  |  |  |  |  | 
INCREASE | 73 | 94 | 95 | 99 | 100 | 101 | 101 |  |  |  |  |  |  |  | 

## Slide 7: WTN SYSTEM PERFORMANCE THERMAL VIOLATIONS
 |  |  |  | 2019
 |  | 2018 | 2022 | MIN
CONTINGENCY | VIOLATION |  |  | 
 |  | RATE C | RATE C | RATE C
WICKETT - PYOTE 69V CKT. | IH-20 - COLLIE FIELD TAP 69KV CKT.(Line 69H) |  |  | 
IH-20 - COLLIE FIELD TAP 69KV CKT. | WICKETT - PYOTE 69V CKT.(Line 69H) | X | X | 
 | PYOTE - WORSHAM 69KV CKT.(Line 69H) | X | X | 
 | WORSHAM - QUITO DRAW 69V CKT.(Line 69H) |  | X | 
BARILLA TAP - FLAT TOP 138V CKT. | TNMP WINK - ONCOR WINK 138KV CKT. |  | X | 
 | WICKETT - PYOTE 69V CKT.(Line 69H) |  | X | 
 | IH-20 - PECOS 69V CKT. | X | X | 
FLAT TOP - AEP PIG CREEK 138V CKT. | TNMP WINK - ONCOR WINK 138KV CKT. |  | X | 
 | WICKETT - PYOTE 69V CKT.(Line 69H) | X | X | 
 | IH-20 - PECOS 69V CKT. | X | X | 

## Slide 8: WTN EXISTING SYSTEM PERFORMANCE VOLTAGE VIOLATIONS
 | 2018 |  | 2022 |  | 2019 | MIN
 | VOLTAGE | VOLTAGE | VOLTAGE | VOLTAGE | VOLTAGE | VOLTAGE
CONTINGENCY | DROP | DEVIATION | DROP | DEVIATION | DROP | DEVIATION
BIRDS OF PREY - COLLIE TAP 69KV CKT. |  |  | X |  |  | 
IH-20 - COLLIE FIELD TAP 69KV CKT. | X | X | X | X | X | X
IH-20 138V AUTOTRANSFORMER | X | X | X | X | X | 
IH-20 - BARILLA TAP 138KV CKT. | X | X | X | X | X | 
BARILLA TAP - FLAT TOP 138V CKT. |  | X | X | X |  | 
TNMP WINK - ONCOR WINK 138KV CKT. |  |  | X |  |  | 
FLAT TOP - AEP PIG CREEK 138V CKT. | X | X | X | X |  | X
IH-20 - FLAT TOP 138KV CKT. | X | X | X | X | X | 

## Slide 9: PREFERRED SOLUTION DETAILS
Rebuild Line 69H from IH-20 – Wickett to 138kv standards utilizing Cumberland 1926 ACSR conductor(408 MVA) ~ 39 miles
Convert existing substations(3) along Line 69H to 138kV standards
Connect to IH-20 138kV substation
Build Wickett 138kV ring bus substation
Install Wickett 138/69kV autotransformer
Build Wickett – ONCOR Wolf 138kV transmission line utilizing 1926 ACSR conductor(408 MVA) ~ 6 miles

## Slide 10: PREFERRED SOLUTION BP2018 ONE-LINE DIAGRAM

## Slide 11: PREFERRED SOLUTION COST SUMMARY
Rebuild Pyote 69kV Tap Substation to 138kV Standards | $3,600,000
Rebuild Worsham 69kV Tap Substation to 138kV Standards | $3,600,000
Rebuild Collie 69kV Tap Substation to 138kV Standards | $1,700,000
Install New Wickett 138kV Ring Substation With Three Breaker Positions And 138/69kV Autotransformer | $9,350,000
Install Single Breaker Position at IH-20 138kV Substation | $1,700,000
Install Single Breaker Position at ONCOR Wolf 138kV Substation(ONCOR Estimate) | $552,160
Rebuild IH-20 - Wickett 69kv Transmission Line with 1926 ACSR Conductor (~ 39 Miles) | $24,648,583
Build Wickett - Wolf 138kV Transmission Line with 1926 ACSR Conductor(~6.0 Miles) | $5,485,000
Total Cost = | $50,635,743

## Slide 12: ALTERNATIVE 1 DETAILS
Rebuild Line 69H from IH-20 – Wickett to 138kv standards utilizing Cumberland 1926 ACSR conductor(204 MVA) ~ 39 miles but remain energized at 69kV
Convert existing substations(3) along Line 69H to 138kV standards
Install 20 MVAR of capacitance support on Line 69H

## Slide 13: ALTERNATIVE 1 BP2018 ONE-LINE DIAGRAM

## Slide 14: ALTERNATIVE 1 COST SUMMARY
Rebuild Pyote 69kV Tap Substation to 138kV Standards | $3,600,000
Rebuild Worsham 69kV Tap Substation to 138kV Standards | $3,600,000
Rebuild Collie 69kV Tap Substation to 138kV Standards | $1,700,000
Rebuild IH-20 - Wickett 69kv Transmission Line with 1926 ACSR Conductor (~ 39 Miles) | $24,648,583
Install 20 MVAR Capacitor Bank at Collie 69kV Tap Substation | $3,000,000
Total Cost = | $36,548,583

## Slide 15: ALTERNATIVE 2 DETAILS
Create 138kV tie connection to ONCOR Yucca Drive - Sand Lake – Culberson 138kV transmission line
ISD ~ 2016
Build 138kV Ring Substation at tie location
Build new 69kV Ring Substation at tie location
Install 138/69kV autotransformer at tie location
Rebuild Line 69H from new 138kV Ring Substation - IH20 to 138kv standards utilizing Cumberland 1926 ACSR conductor(408 MVA) ~ 37 miles
Convert existing substations(3) along Line 69H to 138kV standards

## Slide 16: ALTERNATIVE 2 BP2018 ONE-LINE DIAGRAM

## Slide 17: ALTERNATIVE 2 COST SUMMARY
Rebuild Pyote 69kV Tap Substation to 138kV Standards | $3,600,000
Rebuild Worsham 69kV Tap Substation to 138kV Standards | $3,600,000
Rebuild Collie 69kV Tap Substation to 138kV Standards | $1,700,000
Install New 138kV Ring Substation With Six Breaker Positions(ONCOR Estimate) | $6,461,769
Install Two Breaker Positions at New 69kV Ring Substation | $2,993,778
Install New 138/69kV Autotransformer (ONCOR Estimate) | $4,940,700
Install Single Breaker Position at IH-20 138kV Substation | $1,700,000
Rebuild IH-20 - New 138kV Ring Substation Transmission Line with 1926 ACSR Conductor (~ 37 Miles) | $23,384,553
Total Cost = | $48,380,800

## Slide 18: PROJECT COMPARISON
 |  |  | Capacity | 69 kV Phase | Inconsistent | 
Configuration | Cost | Cost | for Future | Out Plan | with Adjacent | R.O.W.
 |  | Uncertainty | Load | Consistency | TSP Plans for | Required
 |  |  | Growth |  | the Area | 
Preferred | $50,635,743 | Minimal | Best | Best | No | Yes
Solution |  |  |  |  |  | 
Alternative 1 | $36,548,583 | Minimal | Poor | Poor | No | No
Alternative 2 | $48,380,800 | Considerable | Best | Good | Yes | No

## Slide 19
QUESTIONS?