| NOGRR Number | 155 | NOGRR Title | Voltage Ride-Through Requirements Clarification |
| --- | --- | --- | --- |

| Date | April 21, 2016 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Anthony Alford |
| E-mail Address | anthony.alford@centerpointenergy.com |
| Company | CenterPoint Energy |
| Phone Number | 713-207-2265 |
| Cell Number |  |
| Market Segment | Investor Owned Utility (IOU) |

Comments

CenterPoint Energy appreciates the opportunity to provide comments on this topic.  The first paragraph of Section 2.9 refers to Section 2.6, which strictly covers frequency requirements.  This language does not appear to be pertinent to the Voltage Ride-Through (VRT) requirments of this section, and CenterPoint Energy suggests that it be struck with the newly proprosed language taking its place.

In addition, the term “except to aid in voltage recovery” is vague.  Is this in a steady state or transient time frame?  Does this allow for manual adjustment of the real power or is it by automatic control only?  Does this apply to high as well as low voltage conditions?  If the language is left as proposed, a Generation Resource could take the position that reducing its real power output with the sole intent of meeting the (VRT) requirements is in fact “aiding in voltage recovery.”  This interpretation would essentially nullify the purpose of this NOGRR. CenterPoint Energy recommends that these conditions be clearly defined to prevent confusion in the future.

Revised Proposed Guide Language

- 2.9	Voltage Ride-Through Requirements for Generation Resources

(1)

Following a fault, all Generation Resources shall remain On-Line and connected to the transmission system and shall maintain real power, except to aid in voltage recovery.

(2)	Generation Resources must be designed and generation voltage relays must be set to remain connected to the transmission system during the following operating conditions:

(a)	Generator terminal voltages are within 5% of the rated design voltage and volts per hertz are less than 105% of generator rated design voltage and frequency;

(b)	Generator terminal voltage deviations exceed 5% but are within 10% of the rated design voltage and persist for less than ten seconds;

(c)	Generator volts per hertz conditions are less than 116% of generator rated design voltage and frequency and last for less than 1.5 seconds;

(d)	A transmission system fault (three-phase, single-phase or phase-to-phase), but not a generator bus fault, is cleared by the protection scheme coordinated between the Generation Entity and the Transmission Service Provider (TSP) on any line connected to the generator’s transmission interconnect bus, provided such lines are not connected to induction generators described in paragraph (9) of Protocol Section 3.15, Voltage Support; and

(e)	In the case of a generator bus fault or a primary transmission system relay failure, the generator protective relaying may clear the generator independent of the operation of any transmission protective relaying.

(3)	Generating Resources required to provide Voltage Support Service (VSS) shall have and maintain the following capability:

(a)	Over-excitation limiters shall be provided and coordinated with the thermal capability of the generator field winding and protective relays in order to permit short-term reactive capability that allows at least 80% of the unit design standard (ANSI C50.13-1989), as follows:

Time (seconds)		10	30	60	120

Field Voltage %		208	146	125	112

After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.

(b)	Under-excitation limiters shall be provided and coordinated with loss-of-field protection to eliminate unnecessary generating unit disconnection as a result of operator error or equipment malfunction.

(4)	Generation Resources shall have protective relaying necessary to protect its equipment from abnormal conditions as well as to be consistent with protective relaying criteria described in Section 6.2.6.3.4, Generator Protection and Relay Requirements.

(5)	The Voltage Ride-Through (VRT) requirements do not apply to faults that occur between the generator terminals and the transmission voltage side of the Generator Step-Up (GSU) transformer, or when clearing the fault effectively disconnects the Generation Resources from the ERCOT System.