## Slide 1
ERCOT – LP&L Study Status Update
Regional Planning Group
April 21, 2016
Ben Richardson

## Slide 2: Cost Estimate Comparison with Upgrades (Preliminary Results)
Case | Upgrade | Capital Cost Estimate | Relative Annual Capital ¦ Production Cost ($Million) | % of Relative Capital
LP&L Option 1 | McKenzie-North 115 kV & CO-OP-McKenzie 69 kV | $311,818,800 | 0 ¦ 0 | 
LP&L Option 4 |  | $344,443,600 | +$32.6 ¦ -$0.4 | -1.2%
LP&L Option 4ow | McKenzie-North 115 kV & CO-OP-McKenzie 69 kV | $364,081,400 | +$52.3 ¦ -$10.3 | -19.7%
LP&L Option 4ow_dbckt_Grass | McKenzie-North 115 kV, Ogallala-Grassland 345 kV Double Ckt | $408,682,900 | +$96.9 ¦ -$14.5 | -15.0%
LP&L Option 8A |  | $426,107,200 | +$114.3 ¦ -$10.5 | -9.2%
LP&L Option 8A_dbckt_Grass | Ogallala-Grassland 345 kV Double Ckt | $470,708,700 | +$158.9 ¦ -$14.1 | -8.9%
LP&L Option 8B |  | $338,096,600 | +$26.3 ¦ -$3.6 | -13.6%
LP&L Option 11 |  | $492,368,200 | +$180.5 ¦ -$3.7 | -2.0%
LP&L Option 11 | McKenzie-North 115 kV | $492,368,200 | +$180.5 ¦ -$4.7 | -2.6%
Note: Increased capital expenditure meets economic criteria per ERCOT Protocols 3.11.2(5)

## Slide 3: Cost Estimate Comparison with Upgrades (Preliminary Results)
Case | Upgrade | Capital Cost Estimate | Relative Annual Capital ¦ Production Cost ($Million) | % of Relative Capital
LP&L Option 12 |  | $397,751,918 | +$85.9 ¦ +$1.1 | +1.3%
LP&L Option 12 | Holly-Wadsworth 115 kV | $397,751,918 | +$85.9 ¦ -$0.3 | -0.3%
LP&L Option 12c |  | $391,751,918 | +$79.9 ¦ +$0.8 | +1.0%
LP&L Option 20 |  | $466,552,338 | +$154.7 ¦ -$0.8 | -0.5%
SHY Option 1-2a |  | $383,800,200 | +$72.0 ¦ -$0.7 | -1.0%
SHY Option 1-2b |  | $365,076,200 | +$53.3 ¦ -$0.3 | -0.6%

## Slide 4: Next Steps/Timeline
Finalize Assessment of Short-listed Options
Explore Option variations in order to optimize
Complete Dynamic Stability Analysis
  Lubbock
  Panhandle Export
Perform SSR Assessment
Final Report (May 26)

## Slide 5
?

## Slide 6: Appendix
Capital Cost Estimate Assumptions
Panhandle Interface Definitions and WSCR Ratings

## Slide 7: Capital Cost Estimate Assumptions
Item | Cost Estimate | Unit | Source
345 kV Substation (Ring bus 6 line terminals) | $15,940,000.00 | 1 Substation | 2012 ERCOT Study
Land Acquisition for New 345/115 kV Substation | $500,000.00 | 1 Substation | Lubbock Power & Light
345 kV Substation Expansion | $700k to $4 Million | 1 - 345 kV Line Terminal | ERCOT TSPs
345 kV Double Line on Double Ckt Structure | $1,840,000.00 | $/Mile | Sharyland
345 kV Single Line on Double Ckt Structure | $1,660,000.00 | $/Mile | White River to Abernathy 345 kV Line
345 kV Add 2nd Line to Double Ckt Structure | $350,000.00 | $/Mile | Sharyland
345/115 kV 350 MVA Transformer | $6,000,000.00 | 1 Unit | TPIT 345/138 kV 600 MVA Auto Transformer
115 kV Substation (Ring bus 6 line terminals) | $9,050,000.00 | 1 Substation | 2012 ERCOT Study (138 kV Substation)
115 kV Line | $1,600,000.00 | $/Mile | Lubbock Power & Light

## Slide 8: Base Case

## Slide 9: Option 1

## Slide 10: Option 4

## Slide 11: Option 4ow

## Slide 12: Option 4ow_DB

## Slide 13: Option 4ow_DB_Grass

## Slide 14: Option 8A

## Slide 15: Option 8A_DB

## Slide 16: Option 8A_DB_Grass

## Slide 17: Option 8B

## Slide 18: Option 11

## Slide 19: Option 12

## Slide 20: Option 12c

## Slide 21: Option 20

## Slide 22: Opt. 1-2a
White River
Abernathy
North instead of Airport Park
McDonald instead of Quincy
To Vealmoor
Oliver instead of Southeast
Notes: According to Ben:
1. Connected to North rather than Airport Park
2. Connected to McDonald rather than Quincy
3. 1-2a is from Vealmoor just as Sharyland proposed but 1-2b is from Long Draw instead of Vealmoor since Long Draw is closer.

## Slide 23: Opt. 1-2b
White River
Abernathy
North instead of Airport Park
McDonald instead of Quincy
To Long Draw
Oliver instead of Southeast
Notes: According to Ben:
1. Connected to North rather than Airport Park
2. Connected to McDonald rather than Quincy
3. 1-2a is from Vealmoor just as Sharyland proposed but 1-2b is from Long Draw instead of Vealmoor since Long Draw is closer.

## Slide 24: Panhandle Transfer Limit with WSCR=1.5
LP&L Interconnection Impacts on WSCR
WSCR Panhandle Transfer Limit Summary