## README
ERCOT Drought Risk Analysis
This spreadsheet-based calculator is designed to help ERCOT evaluate risk of drought affecting generation supplies
The methodologies contained herein are developed for this specific purpose, which is to provide early warning of possible outages or derating of generation units.
Guidance & Instructions
This spreadsheet is intended to allow users to understand the methodology behind ERCOT's drought risk analysis. The spreadsheets are for demo purposes only and are not intended to reflect conditions at any specific reservor or generating unit. The spreadsheets included in this workbook provide example calculations for a drainage-fed and off-channel reservoir. Separate methodologies are required for the two types of reservoirs due to their different modes of operation and information available. Additional explanation of the methodology behind the spreadsheet is available in the attached file (see icon at right).
The following color conventions are used throughout the model:
Cells shown in this color may be used by the user to input updated information and select from different options.
Cells shown in this color contain data input information that are set by the user when initially developing the reservoir prediction.
Cells shown in this color contain calculations based on historical reservoir data and future reservoir storage predictions. These cells should not be modified.
Cells shown in this color contain model assumptions and other internal calculations. These cells should not be modified.
Yellow boxes contain user tips and other exlanatory information.
1
Click on the icon at right for a detailed description of the water supply prediction methodology used in this tool.
Please read before using the model:
Prediction of drought risk is an inexact science with current knowledge and understanding. Communications should be begun with at risk generators as soon as possible to determine if there are mitigating circumstances which could alter the inputs for the prediction.
User tips...
Electric Reliability Council of Texas

## Drainage-Fed Reservoir
[5 empty] | Historical Data |  |  |  |  | Reservoir Storage Predictions |  |  | All values are in acre-feet | [6 empty] | Percentile lookup for probability fit: | Calculation of Drought Fit | [23 empty] | Lake Bathymetry
| Risk | Average | Worst | Drought Fit | Year | Month | Elevation (ft) | Storage (Acre-ft) | Change (Acre-ft) |  | Reservoir Characteristics |  | Predicted Reservoir Storage |  |  |  | Is Prediction At Risk Level? |  |  |  | Lookup table for exceedence probability calculations | [7 empty] | Historical Monthly Changes in Storage | [15 empty] | Elevation (ft) | Volume (acre-ft)
| Months to Empty | 45 | 8 | 29 | 1999-12-01 | 12 | 45.1 | 77212.7501 |  | Date | Full Storage | At-Risk Storage | Average | Worst | Drought fit | Probability Fit | Average | Worst | Drought Fit | 1 | Month (#) | Month | 0.1 | 0.25 | 0.5 | 0.75 | 0.95 |  | Month/Year | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 0.01 | 0
| Months to At Risk | 45 | 6 | 20 | 2000-01-01 | 1 | 45.3 | 78120.9814 | 908.2313 | 2015-12-01 | 100000 | 20000 | 100000 | 100000 | 100000 | 100000 | No | No | No |  | 1 | JAN | -4732.6714 | -2365.4574 | 4643.3512 | 8188.8499 | 11902.7098 |  | 1 | 908.2313 | 9306.4596 | 4643.3512 | -5209.9383 | 7843.3363 | -1432.0444 | 5037.872 | 14550.214 | -9287.9467 | 2211.3566 | -3298.8703 | 10768.0651 | 8534.3635 | 5717.7267 | -4016.7712 | 0.1 | 0
[5 empty] | 2000-02-01 | 2 | 47.7 | 89156.8379 | 11035.8565 | 2016-01-01 | 100000 | 20000 | 99522.345 | 99522.345 | 99522.345 | 99522.345 | No | No | No |  | 2 | FEB | -4833.5623 | 483.5896 | 3189.4844 | 8100.6893 | 14981.1959 |  | 2 | 11035.8565 | 18865.109 | 9445.1826 | 1885.961 | 3269.1599 | -1426.3213 | 13316.6617 | -7105.0562 | -918.7817 | -8659.8487 | 4721.3845 | 1903.0059 | 3189.4844 | 6756.1959 | 3119.364 | 0.2 | 0
| Generators at Risk | MW | Cap Fctr | MWh (2015) | 2000-03-01 | 3 | 50.1 | 95100 | 5943.1621 | 2016-02-01 | 100000 | 20000 | 97141.6343 | 97141.6343 | 97141.6343 | 97141.6343 | No | No | No |  | 3 | MAR | -3380.0388 | -8.7215 | 4674.0022 | 9437.0832 | 15471.0376 |  | 3 | 5943.1621 | 6635.5877 | -1000 | 1420.9714 | 4674.0022 | 2858.3657 | 15295.8794 | 4721.3845 | 15879.7402 | 12238.5787 | -474.6939 | -7555.2653 | 457.2509 | -4966.7314 | 12736.5383 | 0.3 | 0
| Generator 2 | 600 | 66.5% | 3495000 | 2000-04-01 | 4 | 50.4 | 100000 | 4900 | 2016-03-01 | 100000 | 20000 | 101732.619 | 89586.3691 | 97141.6343 | 93761.5955 | No | No | No |  | 4 | APR | -3438.0512 | -216.3681 | 1000 | 4287.4017 | 11602.345 |  | 4 | 4900 | 0 | 1000 | 2858.3657 | -432.7361 | -5223.3005 | 10516.3283 | 951.6274 | 476.6846 | 10501.3885 | 2858.3657 | -5115.8057 | 3674.8034 | 14136.384 | -921.4193 | 0.4 | 0
[5 empty] | 2000-05-01 | 5 | 49.3 | 96667.2639 | -3332.7361 | 2016-04-01 | 100000 | 20000 | 104411.3314 | 84363.0686 | 97141.6343 | 90323.5443 | No | No | No |  | 5 | MAY | -6900.8858 | -4645.0309 | -952.971 | 6818.9758 | 12680.321 |  | 5 | -3332.7361 | -7105.0562 | -1908.3308 | -7574.0022 | 3332.7361 | 0 | -6594.6302 | -1426.3213 | -952.971 | 11900 | 0 | 10768.0651 | -5957.3256 | 10305.2155 | 14501.07 | 0.5 | 0
[5 empty] | 2000-06-01 | 6 | 47.9 | 90088.4344 | -6578.8295 | 2016-05-01 | 100000 | 20000 | 105475.0456 | 76789.0664 | 94093.7792 | 83422.6585 | No | No | No |  | 6 | JUN | -6128.5956 | -4008.8957 | -455.0861 | 2383.3483 | 5072.2007 |  | 6 | -6578.8295 | -2340.1264 | 1908.3308 | 7574.0022 | 0 | -1881.7557 | -2794.4909 | 2858.3657 | -6134.3685 | 4000 | -5223.3005 | -6119.9363 | -455.0861 | 2858.3657 | 1432.0444 | 0.6 | 0.024883
[5 empty] | 2000-07-01 | 7 | 47.1 | 86373.5692 | -3714.8651 | 2016-06-01 | 100000 | 20000 | 104748.5933 | 70210.2369 | 91390.1612 | 77294.0629 | No | No | No |  | 7 | JUL | -11772.7929 | -5930.0164 | -4194.0629 | -3253.3219 | 1566.9901 |  | 7 | -3714.8651 | -5105.0314 | -3332.7361 | -2858.3657 | -6165.2981 | -4203.2945 | -4160.3215 | 0 | -4194.0629 | -11772.7929 | 5223.3005 | -15167.7615 | -3173.9076 | -11772.7929 | -5694.7347 | 0.7 | 0.024883
[5 empty] | 2000-08-01 | 8 | 46.1 | 81771.2252 | -4602.344 | 2016-07-01 | 100000 | 20000 | 99675.749 | 55042.4754 | 85813.3672 | 65521.27 | No | No | No |  | 8 | AUG | -14107.9048 | -11745.1005 | -8563.2378 | -5919.5183 | 1562.9815 |  | 8 | -4602.344 | -7328.8046 | -7857.2639 | -13041.6343 | 5209.9383 | -9660.6699 | -11966.8856 | 0 | -8563.2378 | -5127.2071 | -10900 | -11523.3154 | -6711.8294 | -15527.1723 | -14818.7519 | 0.8 | 0.049766
[5 empty] | 2000-09-01 | 9 | 40.2 | 56120.5584 | -25650.6669 | 2016-08-01 | 100000 | 20000 | 91514.4705 | 39515.3031 | 74414.7148 | 51413.3652 | No | No | No |  | 9 | SEPT | -8293.0278 | -7551.6697 | -3360.214 | -499.1664 | 8286.3342 |  | 9 | -25650.6669 | 909.998 | -3360.214 | -7793.4159 | -2850.8261 | -7674.1316 | -8626.1023 | -1908.3308 | -3346.0635 | 8857.3007 | 8041.6343 | -7429.2077 | 2220.4141 | -6204.9617 | -5437.668 | 0.9 | 0.074649
[5 empty] | 2000-10-01 | 10 | 40.8 | 58487.4589 | 2366.9006 | 2016-09-01 | 100000 | 20000 | 87497.6544 | 13864.6362 | 67230.3563 | 43120.3374 | No | Yes | No |  | 10 | OCT | -9923.7484 | -5124.2585 | 0 | 2545.648 | 9117.662 |  | 10 | 2366.9006 | -455.0861 | 923.7832 | 2724.3953 | -7036.9762 | -5256.8478 | -850.6271 | -4991.6692 | -12806.0117 | 8042.6993 | 0 | 3210.7097 | 893.5503 | 11625.9082 | -11848.2632 | 1 | 0.099532
[5 empty] | 2000-11-01 | 11 | 41.7 | 62200.5823 | 3713.1233 | 2016-10-01 | 100000 | 20000 | 86600.4854 | 1058.6245 | 63066.8956 | 33196.589 | No | Yes | No |  | 11 | NOV | -5169.991 | -3120.0109 | -893.5503 | 3112.1355 | 12391.3556 |  | 11 | 3713.1233 | -1363.1432 | 0 | 5496.5413 | 9887.8023 | -5987.877 | 18232.98 | -3943.1621 | -424.6541 | -3332.7361 | -6119.9363 | 2511.1476 | -893.5503 | -1361.5507 | -2907.2858 | 1.1 | 0.1493
[5 empty] | 2000-12-01 | 12 | 42.4 | 65192.8436 | 2992.2614 | 2016-11-01 | 100000 | 20000 | 87500.9986 | -5061.3118 | 60468.4383 | 28026.598 | No | Yes | No |  | 12 | DEC | -6284.6123 | -4129.1928 | 955.3598 | 4889.3948 | 9890.4225 |  | 12 | 2992.2614 | 8698.716 | 12671.071 | -3214.0191 | 955.3598 | -6662.5361 | 4593.5354 | 3738.1059 | 5185.2543 | -473.4498 | -4648.1288 | 6509.1321 | -5717.7267 | -3610.2568 | -7700.4081 | 1.2 | 0.19906
| Reservoir Details |  |  |  | 2001-01-01 | 1 | 44.5 | 74499.3033 | 9306.4596 | 2016-12-01 | 100000 | 20000 | 88388.7927 | -12761.7199 | 56937.4291 | 21741.9857 | No | Yes | No | [25 empty] | 1.3 | 0.24883
| Full (Conservation) | 100000 | Acre-feet |  | 2001-02-01 | 2 | 48.6 | 93364.4123 | 18865.109 | 2017-01-01 | 100000 | 20000 | 91473.8197 | -22049.6666 | 55973.4398 | 17009.3142 | No | Yes | No |  | Monthly Changes in Storage - Statistics |  |  |  |  | Reservoir storage: | 100000 | Dr. fit % of Storage | [16 empty] | 1.4 | 0.32348
| At-Risk Level | 20000 | Acre-feet |  | 2001-03-01 | 3 | 51.2 | 100000 | 6635.5877 | 2017-02-01 | 100000 | 20000 | 95433.6435 | -30709.5153 | 55973.4398 | 12175.752 | No | Yes | No |  | Month (#) | Month | Max | Average | Min | 30th Percentile | Drought Fit | [17 empty] | 1.5 | 0.39813
[5 empty] | 2001-04-01 | 4 | 50.4 | 100000 | 0 | 2017-03-01 | 100000 | 20000 | 100024.6282 | -38264.7805 | 55973.4398 | 8795.7131 | No | Yes | No |  | 1 | JAN | 14550.214 | 3085.027 | -9287.9467 | -963.9893 | -963.9893 | 0.964% | [16 empty] | 1.6 | 0.47278
| At-Risk Level |  | Reasons |  | 2001-05-01 | 5 | 48.5 | 92894.9438 | -7105.0562 | 2017-04-01 | 100000 | 20000 | 102703.3406 | -43488.081 | 55973.4398 | 5357.662 | No | Yes | No |  | 2 | FEB | 18865.109 | 3959.8238 | -8659.8487 | 1889.37 | 0 | 0% | [16 empty] | 1.7 | 0.57231
| 20% | Set at default level of 20% for drainage-fed reservoirs |  |  | 2001-06-01 | 6 | 48 | 90554.8174 | -2340.1264 | 2017-05-01 | 100000 | 20000 | 103767.0548 | -51062.0832 | 52925.5848 | -1543.2238 | No | Yes | No |  | 3 | MAR | 15879.7402 | 4590.9847 | -7555.2653 | 649.995 | 0 | 0% | [16 empty] | 1.8 | 0.67184
[5 empty] | 2001-07-01 | 7 | 46.9 | 85449.786 | -5105.0314 | 2017-06-01 | 100000 | 20000 | 103040.6025 | -57640.9127 | 50221.9668 | -7671.8194 | No | Yes | No |  | 4 | APR | 14136.384 | 2678.7124 | -5223.3005 | 95.3369 | 0 | 0% | [16 empty] | 1.9 | 0.77137
[5 empty] | 2001-08-01 | 8 | 45.3 | 78120.9814 | -7328.8046 | 2017-07-01 | 100000 | 20000 | 97967.7582 | -72808.6742 | 44645.1727 | -19444.6123 | No | Yes | No |  | 5 | MAY | 14501.07 | 1063.7142 | -7574.0022 | -3047.8551 | -3047.8551 | 3.048% | [16 empty] | 2 | 0.87091
| Historical Storage Change Probability |  |  |  | 2001-09-01 | 9 | 45.5 | 79030.9794 | 909.998 | 2017-08-01 | 100000 | 20000 | 89806.4797 | -88335.8465 | 33246.5204 | -33552.5172 | No | Yes | No |  | 6 | JUN | 7574.0022 | -726.4523 | -6578.8295 | -2703.618 | -2703.618 | 2.704% | [16 empty] | 2.1 | 1.0202
| Extreme Drought | 10% |  |  | 2001-10-01 | 10 | 45.4 | 78575.8933 | -455.0861 | 2017-09-01 | 100000 | 20000 | 85789.6636 | -113986.5134 | 26062.1618 | -41845.5449 | No | Yes | No |  | 7 | JUL | 5223.3005 | -5072.8443 | -15167.7615 | -5576.7941 | -5576.7941 | 5.577% | [16 empty] | 2.2 | 1.269
|  | 25% |  |  | 2001-11-01 | 11 | 45.1 | 77212.7501 | -1363.1432 | 2017-10-01 | 100000 | 20000 | 84892.4946 | -126792.5251 | 21898.7011 | -51769.2933 | No | Yes | No |  | 8 | AUG | 5209.9383 | -8161.2785 | -15527.1723 | -11398.6523 | -11398.6523 | 11.4% | [16 empty] | 2.3 | 1.7169
|  | 50% |  |  | 2001-12-01 | 12 | 47 | 85911.4661 | 8698.716 | 2017-11-01 | 100000 | 20000 | 85793.0079 | -132912.4614 | 19300.2439 | -56939.2844 | No | Yes | Yes |  | 9 | SEPT | 8857.3007 | -4016.8161 | -25650.6669 | -7184.3585 | -7184.3585 | 7.184% | [16 empty] | 2.4 | 2.4137
|  | 75% |  |  | 2002-01-01 | 1 | 48 | 90554.8174 | 4643.3512 | 2017-12-01 | 100000 | 20000 | 86680.8019 | -140612.8695 | 15769.2346 | -63223.8967 | No | Yes | Yes |  | 10 | OCT | 11625.9082 | -897.169 | -12806.0117 | -4163.4607 | -4163.4607 | 4.163% | [16 empty] | 2.5 | 3.2846
| Very Wet | 95% |  |  | 2002-02-01 | 2 | 50.5 | 100000 | 9445.1826 | 2018-01-01 | 100000 | 20000 | 89765.8289 | -149900.8162 | 14805.2453 | -67956.5681 | No | Yes | Yes |  | 11 | NOV | 18232.98 | 900.5133 | -6119.9363 | -2598.4573 | -2598.4573 | 2.598% | [16 empty] | 2.6 | 4.3048
[5 empty] | 2002-03-01 | 3 | 50.1 | 99000 | -1000 | 2018-02-01 | 100000 | 20000 | 93725.6528 | -158560.6649 | 14805.2453 | -72790.1304 | No | Yes | Yes |  | 12 | DEC | 12671.071 | 887.794 | -7700.4081 | -3531.0093 | -3531.0093 | 3.531% | [16 empty] | 2.7 | 5.4992
[5 empty] | 2002-04-01 | 4 | 50.1 | 100000 | 1000 | 2018-03-01 | 100000 | 20000 | 98316.6375 | -166115.9301 | 14805.2453 | -76170.1692 | No | Yes | Yes |  | For drought fit, values in blue cells are set at 30th percentile; values in green cells modified as described below. | [23 empty] | 2.8 | 6.818
[5 empty] | 2002-05-01 | 5 | 49.6 | 98091.6692 | -1908.3308 | 2018-04-01 | 100000 | 20000 | 100995.3499 | -171339.2306 | 14805.2453 | -79608.2204 | No | Yes | Yes | [25 empty] | 2.9 | 8.2861
[5 empty] | 2002-06-01 | 6 | 50.1 | 100000 | 1908.3308 | 2018-05-01 | 100000 | 20000 | 102059.0641 | -178913.2328 | 11757.3903 | -86509.1062 | No | Yes | Yes |  | Explanation of Drought Fit |  |  | Months Affected: | [20 empty] | 3 | 9.9035
[5 empty] | 2002-07-01 | 7 | 49.3 | 96667.2639 | -3332.7361 | 2018-06-01 | 100000 | 20000 | 101332.6117 | -185492.0623 | 9053.7723 | -92637.7018 | No | Yes | Yes |  | Reason for Change: |  |  |  | Modified Value Based On: | [19 empty] | 3.1 | 11.6702
[5 empty] | 2002-08-01 | 8 | 46.7 | 88810 | -7857.2639 | 2018-07-01 | 100000 | 20000 | 96259.7674 | -200659.8238 | 3476.9782 | -104410.4947 | No | Yes | Yes |  | Value is > 0 |  |  | Feb-Apr | Assumed to be zero | [19 empty] | 3.2 | 13.5613
[5 empty] | 2002-09-01 | 9 | 46.9 | 85449.786 | -3360.214 | 2018-08-01 | 100000 | 20000 | 88098.4889 | -216186.9961 | -7921.6741 | -118518.3995 | No | Yes | Yes | [25 empty] | 3.3 | 15.6266
[5 empty] | 2002-10-01 | 10 | 47.1 | 86373.5692 | 923.7832 | 2018-09-01 | 100000 | 20000 | 84081.6728 | -241837.663 | -15106.0326 | -126811.4273 | No | Yes | Yes | [25 empty] | 3.4 | 17.8411
[5 empty] | 2002-11-01 | 11 | 47.1 | 86373.5692 | 0 | 2018-10-01 | 100000 | 20000 | 83184.5038 | -254643.6747 | -19269.4934 | -136735.1757 | No | Yes | Yes | [25 empty] | 3.5 | 20.2299
[5 empty] | 2002-12-01 | 12 | 49.8 | 99044.6402 | 12671.071 | 2018-11-01 | 100000 | 20000 | 84085.0171 | -260763.611 | -21867.9506 | -141905.1667 | No | Yes | Yes | [25 empty] | 3.6 | 22.768
[5 empty] | 2003-01-01 | 1 | 48.7 | 93834.7019 | -5209.9383 | 2018-12-01 | 100000 | 20000 | 84972.8111 | -268464.0191 | -25398.9599 | -148189.779 | No | Yes | Yes | [25 empty] | 3.7 | 25.5051
[5 empty] | 2003-02-01 | 2 | 49.1 | 95720.6629 | 1885.961 | 2019-01-01 | 100000 | 20000 | 88057.8382 | -277751.9658 | -26362.9491 | -152922.4505 | No | Yes | Yes | [25 empty] | 3.8 | 28.4164
[5 empty] | 2003-03-01 | 3 | 49.4 | 97141.6343 | 1420.9714 | 2019-02-01 | 100000 | 20000 | 92017.662 | -286411.8145 | -26362.9491 | -157756.0127 | No | Yes | Yes | [25 empty] | 3.9 | 31.5019
[5 empty] | 2003-04-01 | 4 | 50 | 100000 | 2858.3657 | 2019-03-01 | 100000 | 20000 | 96608.6467 | -293967.0797 | -26362.9491 | -161136.0516 | No | Yes | Yes | [25 empty] | 4 | 34.7865
[5 empty] | 2003-05-01 | 5 | 48.4 | 92425.9978 | -7574.0022 | 2019-04-01 | 100000 | 20000 | 99287.3591 | -299190.3802 | -26362.9491 | -164574.1027 | No | Yes | Yes | [25 empty] | 4.1 | 38.2452
[5 empty] | 2003-06-01 | 6 | 50.8 | 100000 | 7574.0022 | 2019-05-01 | 100000 | 20000 | 100351.0733 | -306764.3824 | -29410.8042 | -171474.9886 | No | Yes | Yes | [25 empty] | 4.2 | 41.8782
[5 empty] | 2003-07-01 | 7 | 49.4 | 97141.6343 | -2858.3657 | 2019-06-01 | 100000 | 20000 | 99624.6209 | -313343.2119 | -32114.4222 | -177603.5842 | No | Yes | Yes | [25 empty] | 4.3 | 45.6853
[5 empty] | 2003-08-01 | 8 | 45 | 84100 | -13041.6343 | 2019-07-01 | 100000 | 20000 | 94551.7766 | -328510.9734 | -37691.2163 | -189376.377 | No | Yes | Yes | [25 empty] | 4.4 | 49.6915
[5 empty] | 2003-09-01 | 9 | 44.9 | 76306.5841 | -7793.4159 | 2019-08-01 | 100000 | 20000 | 86390.4981 | -344038.1457 | -49089.8686 | -203484.2819 | No | Yes | Yes | [25 empty] | 4.5 | 53.8967
[5 empty] | 2003-10-01 | 10 | 45.5 | 79030.9794 | 2724.3953 | 2019-09-01 | 100000 | 20000 | 82373.682 | -369688.8126 | -56274.2271 | -211777.3096 | No | Yes | Yes | [25 empty] | 4.6 | 58.3259
[5 empty] | 2003-11-01 | 11 | 46.7 | 84527.5207 | 5496.5413 | 2019-10-01 | 100000 | 20000 | 81476.5131 | -382494.8243 | -60437.6879 | -221701.058 | No | Yes | Yes | [25 empty] | 4.7 | 62.9541
[5 empty] | 2003-12-01 | 12 | 46 | 81313.5015 | -3214.0191 | 2019-11-01 | 100000 | 20000 | 82377.0263 | -388614.7606 | -63036.1451 | -226871.0491 | No | Yes | Yes | [25 empty] | 4.8 | 67.8312
[5 empty] | 2004-01-01 | 1 | 47.7 | 89156.8379 | 7843.3363 | [35 empty] | 4.9 | 72.982
[5 empty] | 2004-02-01 | 2 | 48.4 | 92425.9978 | 3269.1599 | [35 empty] | 5 | 78.4314
[5 empty] | 2004-03-01 | 3 | 50.5 | 97100 | 4674.0022 | [35 empty] | 5.1 | 84.1545
[5 empty] | 2004-04-01 | 4 | 49.3 | 96667.2639 | -432.7361 | [35 empty] | 5.2 | 90.2011
Notes: |  |  |  |  | 2004-05-01 | 5 | 50.1 | 100000 | 3332.7361 | [35 empty] | 5.3 | 96.5462
[5 empty] | 2004-06-01 | 6 | 50 | 100000 | 0 | [35 empty] | 5.4 | 103.1651
[5 empty] | 2004-07-01 | 7 | 48.7 | 93834.7019 | -6165.2981 | [35 empty] | 5.5 | 110.0577
[5 empty] | 2004-08-01 | 8 | 49.8 | 99044.6402 | 5209.9383 | [35 empty] | 5.6 | 117.2738
[5 empty] | 2004-09-01 | 9 | 49.2 | 96193.8141 | -2850.8261 | [35 empty] | 5.7 | 124.7885
[5 empty] | 2004-10-01 | 10 | 47.7 | 89156.8379 | -7036.9762 | [35 empty] | 5.8 | 132.6018
[5 empty] | 2004-11-01 | 11 | 49.8 | 99044.6402 | 9887.8023 | [35 empty] | 5.9 | 140.7385
[5 empty] | 2004-12-01 | 12 | 50.1 | 100000 | 955.3598 | [35 empty] | 6 | 149.1988
[5 empty] | 2005-01-01 | 1 | 49.7 | 98567.9556 | -1432.0444 | [35 empty] | 6.1 | 158.0322
[5 empty] | 2005-02-01 | 2 | 49.4 | 97141.6343 | -1426.3213 | [35 empty] | 6.2 | 167.3385
[5 empty] | 2005-03-01 | 3 | 50.4 | 100000 | 2858.3657 | [35 empty] | 6.3 | 177.0927
[5 empty] | 2005-04-01 | 4 | 48.9 | 94776.6995 | -5223.3005 | [35 empty] | 6.4 | 187.2698
[5 empty] | 2005-05-01 | 5 | 48.9 | 94776.6995 | 0 | [35 empty] | 6.5 | 197.87
[5 empty] | 2005-06-01 | 6 | 48.5 | 92894.9438 | -1881.7557 | [35 empty] | 6.6 | 208.8932
[5 empty] | 2005-07-01 | 7 | 47.6 | 88691.6492 | -4203.2945 | [35 empty] | 6.7 | 220.3394
[5 empty] | 2005-08-01 | 8 | 45.5 | 79030.9794 | -9660.6699 | [35 empty] | 6.8 | 232.1589
[5 empty] | 2005-09-01 | 9 | 43.8 | 71356.8478 | -7674.1316 | [35 empty] | 6.9 | 244.4262
[5 empty] | 2005-10-01 | 10 | 41 | 66100 | -5256.8478 | [35 empty] | 7 | 257.0917
[5 empty] | 2005-11-01 | 11 | 41.2 | 60112.123 | -5987.877 | [35 empty] | 7.1 | 270.205
[5 empty] | 2005-12-01 | 12 | 39.5 | 53449.5869 | -6662.5361 | [35 empty] | 7.2 | 283.7165
[5 empty] | 2006-01-01 | 1 | 40.8 | 58487.4589 | 5037.872 | [35 empty] | 7.3 | 297.7008
[5 empty] | 2006-02-01 | 2 | 43.9 | 71804.1206 | 13316.6617 | [35 empty] | 7.4 | 312.133
[5 empty] | 2006-03-01 | 3 | 48.1 | 87100 | 15295.8794 | [35 empty] | 7.5 | 327.0628
[5 empty] | 2006-04-01 | 4 | 49.5 | 97616.3283 | 10516.3283 | [35 empty] | 7.6 | 342.4903
[5 empty] | 2006-05-01 | 5 | 48.1 | 91021.698 | -6594.6302 | [35 empty] | 7.7 | 358.4154
[5 empty] | 2006-06-01 | 6 | 47.5 | 88227.2071 | -2794.4909 | [35 empty] | 7.8 | 374.8631
[5 empty] | 2006-07-01 | 7 | 46.6 | 84066.8856 | -4160.3215 | [35 empty] | 7.9 | 391.8583
[5 empty] | 2006-08-01 | 8 | 41.3 | 72100 | -11966.8856 | [35 empty] | 8 | 409.3759
[5 empty] | 2006-09-01 | 9 | 42 | 63473.8977 | -8626.1023 | [35 empty] | 8.1 | 427.3664
[5 empty] | 2006-10-01 | 10 | 41.8 | 62623.2706 | -850.6271 | [35 empty] | 8.2 | 445.8545
[5 empty] | 2006-11-01 | 11 | 45.9 | 80856.2506 | 18232.98 | [35 empty] | 8.3 | 464.7905
[5 empty] | 2006-12-01 | 12 | 46.9 | 85449.786 | 4593.5354 | [35 empty] | 8.4 | 484.2241
[5 empty] | 2007-01-01 | 1 | 50.8 | 100000 | 14550.214 | [35 empty] | 8.5 | 504.2301
[5 empty] | 2007-02-01 | 2 | 48.5 | 92894.9438 | -7105.0562 | [35 empty] | 8.6 | 524.8333
[5 empty] | 2007-03-01 | 3 | 49.5 | 97616.3283 | 4721.3845 | [35 empty] | 8.7 | 546.0336
[5 empty] | 2007-04-01 | 4 | 49.7 | 98567.9556 | 951.6274 | [35 empty] | 8.8 | 567.881
[5 empty] | 2007-05-01 | 5 | 49.4 | 97141.6343 | -1426.3213 | [35 empty] | 8.9 | 590.3504
[5 empty] | 2007-06-01 | 6 | 51.4 | 100000 | 2858.3657 | [35 empty] | 9 | 613.5662
[5 empty] | 2007-07-01 | 7 | 51.5 | 100000 | 0 | [35 empty] | 9.1 | 637.5286
[5 empty] | 2007-08-01 | 8 | 50 | 100000 | 0 | [35 empty] | 9.2 | 662.3121
[5 empty] | 2007-09-01 | 9 | 49.6 | 98091.6692 | -1908.3308 | [35 empty] | 9.3 | 687.8421
[5 empty] | 2007-10-01 | 10 | 47.8 | 93100 | -4991.6692 | [35 empty] | 9.4 | 714.1186
[5 empty] | 2007-11-01 | 11 | 47.7 | 89156.8379 | -3943.1621 | [35 empty] | 9.5 | 741.0172
[5 empty] | 2007-12-01 | 12 | 48.5 | 92894.9438 | 3738.1059 | [35 empty] | 9.6 | 768.513
[5 empty] | 2008-01-01 | 1 | 46.5 | 83606.9971 | -9287.9467 | [35 empty] | 9.7 | 796.606
[5 empty] | 2008-02-01 | 2 | 46.3 | 82688.2154 | -918.7817 | [35 empty] | 9.8 | 825.2463
[5 empty] | 2008-03-01 | 3 | 49.7 | 98567.9556 | 15879.7402 | [35 empty] | 9.9 | 854.4342
[5 empty] | 2008-04-01 | 4 | 49.8 | 99044.6402 | 476.6846 | [35 empty] | 10 | 884.1694
[5 empty] | 2008-05-01 | 5 | 49.6 | 98091.6692 | -952.971 | [35 empty] | 10.1 | 914.4023
[5 empty] | 2008-06-01 | 6 | 48.3 | 91957.3007 | -6134.3685 | [35 empty] | 10.2 | 945.2324
[5 empty] | 2008-07-01 | 7 | 47.4 | 87763.2378 | -4194.0629 | [35 empty] | 10.3 | 976.6099
[5 empty] | 2008-08-01 | 8 | 44.7 | 79200 | -8563.2378 | [35 empty] | 10.4 | 1008.6095
[5 empty] | 2008-09-01 | 9 | 44.8 | 75853.9365 | -3346.0635 | [35 empty] | 10.5 | 1041.281
[5 empty] | 2008-10-01 | 10 | 41.9 | 63047.9248 | -12806.0117 | [35 empty] | 10.6 | 1074.6491
[5 empty] | 2008-11-01 | 11 | 41.8 | 62623.2706 | -424.6541 | [35 empty] | 10.7 | 1108.6643
[5 empty] | 2008-12-01 | 12 | 43 | 67808.5249 | 5185.2543 | [35 empty] | 10.8 | 1143.3264
[5 empty] | 2009-01-01 | 1 | 43.5 | 70019.8816 | 2211.3566 | [35 empty] | 10.9 | 1178.6354
[5 empty] | 2009-02-01 | 2 | 41.5 | 61360.0328 | -8659.8487 | [35 empty] | 11 | 1214.6163
[5 empty] | 2009-03-01 | 3 | 44.3 | 73598.6115 | 12238.5787 | [35 empty] | 11.1 | 1251.2939
[5 empty] | 2009-04-01 | 4 | 47.7 | 84100 | 10501.3885 | [35 empty] | 11.2 | 1288.6185
[5 empty] | 2009-05-01 | 5 | 50.5 | 96000 | 11900 | [35 empty] | 11.3 | 1326.5651
[5 empty] | 2009-06-01 | 6 | 50.4 | 100000 | 4000 | [35 empty] | 11.4 | 1365.1836
[5 empty] | 2009-07-01 | 7 | 47.5 | 88227.2071 | -11772.7929 | [35 empty] | 11.5 | 1404.4491
[5 empty] | 2009-08-01 | 8 | 46 | 83100 | -5127.2071 | [35 empty] | 11.6 | 1444.4362
[5 empty] | 2009-09-01 | 9 | 48.3 | 91957.3007 | 8857.3007 | [35 empty] | 11.7 | 1485.1199
[5 empty] | 2009-10-01 | 10 | 50.2 | 100000 | 8042.6993 | [35 empty] | 11.8 | 1526.4756
[5 empty] | 2009-11-01 | 11 | 49.3 | 96667.2639 | -3332.7361 | [35 empty] | 11.9 | 1568.5528
[5 empty] | 2009-12-01 | 12 | 49.2 | 96193.8141 | -473.4498 | [35 empty] | 12 | 1611.4014
[5 empty] | 2010-01-01 | 1 | 48.5 | 92894.9438 | -3298.8703 | [35 empty] | 12.1 | 1654.9965
[5 empty] | 2010-02-01 | 2 | 49.5 | 97616.3283 | 4721.3845 | [35 empty] | 12.2 | 1699.363
[5 empty] | 2010-03-01 | 3 | 49.4 | 97141.6343 | -474.6939 | [35 empty] | 12.3 | 1744.4262
[5 empty] | 2010-04-01 | 4 | 50.3 | 100000 | 2858.3657 | [35 empty] | 12.4 | 1790.2857
[5 empty] | 2010-05-01 | 5 | 50 | 100000 | 0 | [35 empty] | 12.5 | 1836.9165
[5 empty] | 2010-06-01 | 6 | 48.9 | 94776.6995 | -5223.3005 | [35 empty] | 12.6 | 1884.2689
[5 empty] | 2010-07-01 | 7 | 50.3 | 100000 | 5223.3005 | [35 empty] | 12.7 | 1932.3181
[5 empty] | 2010-08-01 | 8 | 46.6 | 89100 | -10900 | [35 empty] | 12.8 | 1981.0391
[5 empty] | 2010-09-01 | 9 | 49.4 | 97141.6343 | 8041.6343 | [35 empty] | 12.9 | 2030.4817
[5 empty] | 2010-10-01 | 10 | 49.4 | 97141.6343 | 0 | [35 empty] | 13 | 2080.6211
[5 empty] | 2010-11-01 | 11 | 48.1 | 91021.698 | -6119.9363 | [35 empty] | 13.1 | 2131.4572
[5 empty] | 2010-12-01 | 12 | 47.1 | 86373.5692 | -4648.1288 | [35 empty] | 13.2 | 2183.0148
[5 empty] | 2011-01-01 | 1 | 49.4 | 97141.6343 | 10768.0651 | [35 empty] | 13.3 | 2235.2195
[5 empty] | 2011-02-01 | 2 | 49.8 | 99044.6402 | 1903.0059 | [35 empty] | 13.4 | 2288.1457
[5 empty] | 2011-03-01 | 3 | 48.2 | 91489.3749 | -7555.2653 | [35 empty] | 13.5 | 2341.694
[5 empty] | 2011-04-01 | 4 | 47.1 | 86373.5692 | -5115.8057 | [35 empty] | 13.6 | 2395.8893
[5 empty] | 2011-05-01 | 5 | 49.4 | 97141.6343 | 10768.0651 | [35 empty] | 13.7 | 2450.7813
[5 empty] | 2011-06-01 | 6 | 48.1 | 91021.698 | -6119.9363 | [35 empty] | 13.8 | 2506.2954
[5 empty] | 2011-07-01 | 7 | 44.8 | 75853.9365 | -15167.7615 | [35 empty] | 13.9 | 2562.4813
[5 empty] | 2011-08-01 | 8 | 42.2 | 64330.6211 | -11523.3154 | [35 empty] | 14 | 2619.3142
[5 empty] | 2011-09-01 | 9 | 40.4 | 56901.4134 | -7429.2077 | [35 empty] | 14.1 | 2676.819
[5 empty] | 2011-10-01 | 10 | 41.2 | 60112.123 | 3210.7097 | [35 empty] | 14.2 | 2734.9955
[5 empty] | 2011-11-01 | 11 | 41.8 | 62623.2706 | 2511.1476 | [35 empty] | 14.3 | 2793.8191
[5 empty] | 2011-12-01 | 12 | 43.3 | 69132.4027 | 6509.1321 | [35 empty] | 14.4 | 2853.3891
[5 empty] | 2012-01-01 | 1 | 45.2 | 77666.7662 | 8534.3635 | [35 empty] | 14.5 | 2913.7056
[5 empty] | 2012-02-01 | 2 | 45.9 | 80856.2506 | 3189.4844 | [35 empty] | 14.6 | 2974.8184
[5 empty] | 2012-03-01 | 3 | 46 | 81313.5015 | 457.2509 | [35 empty] | 14.7 | 3036.7274
[5 empty] | 2012-04-01 | 4 | 46.8 | 84988.305 | 3674.8034 | [35 empty] | 14.8 | 3099.358
[5 empty] | 2012-05-01 | 5 | 45.5 | 79030.9794 | -5957.3256 | [35 empty] | 14.9 | 3162.7849
[5 empty] | 2012-06-01 | 6 | 45.4 | 78575.8933 | -455.0861 | [35 empty] | 15 | 3226.9334
[5 empty] | 2012-07-01 | 7 | 44.7 | 75401.9857 | -3173.9076 | [35 empty] | 15.1 | 3291.9528
[5 empty] | 2012-08-01 | 8 | 43.2 | 68690.1563 | -6711.8294 | [35 empty] | 15.2 | 3357.9924
[5 empty] | 2012-09-01 | 9 | 43.7 | 70910.5703 | 2220.4141 | [35 empty] | 15.3 | 3424.8532
[5 empty] | 2012-10-01 | 10 | 43.9 | 71804.1206 | 893.5503 | [35 empty] | 15.4 | 3492.6097
[5 empty] | 2012-11-01 | 11 | 43.7 | 70910.5703 | -893.5503 | [35 empty] | 15.5 | 3561.1625
[5 empty] | 2012-12-01 | 12 | 42.4 | 65192.8436 | -5717.7267 | [35 empty] | 15.6 | 3630.5365
[5 empty] | 2013-01-01 | 1 | 43.7 | 70910.5703 | 5717.7267 | [35 empty] | 15.7 | 3700.7813
[5 empty] | 2013-02-01 | 2 | 45.2 | 77666.7662 | 6756.1959 | [35 empty] | 15.8 | 3771.7478
[5 empty] | 2013-03-01 | 3 | 44.1 | 72700.0348 | -4966.7314 | [35 empty] | 15.9 | 3843.5105
[5 empty] | 2013-04-01 | 4 | 47.2 | 86836.4188 | 14136.384 | [35 empty] | 16 | 3915.9699
[5 empty] | 2013-05-01 | 5 | 49.4 | 97141.6343 | 10305.2155 | [35 empty] | 16.1 | 3989.1261
[5 empty] | 2013-06-01 | 6 | 50 | 100000 | 2858.3657 | [35 empty] | 16.2 | 4063.0785
[5 empty] | 2013-07-01 | 7 | 47.5 | 88227.2071 | -11772.7929 | [35 empty] | 16.3 | 4137.6779
[5 empty] | 2013-08-01 | 8 | 44.1 | 72700.0348 | -15527.1723 | [35 empty] | 16.4 | 4213.0238
[5 empty] | 2013-09-01 | 9 | 42.7 | 66495.0732 | -6204.9617 | [35 empty] | 16.5 | 4289.0166
[5 empty] | 2013-10-01 | 10 | 45.3 | 78120.9814 | 11625.9082 | [35 empty] | 16.6 | 4365.6813
[5 empty] | 2013-11-01 | 11 | 45 | 76759.4307 | -1361.5507 | [35 empty] | 16.7 | 4443.0427
[5 empty] | 2013-12-01 | 12 | 44.2 | 73149.1739 | -3610.2568 | [35 empty] | 16.8 | 4521.0511
[5 empty] | 2014-01-01 | 1 | 43.3 | 69132.4027 | -4016.7712 | [35 empty] | 16.9 | 4599.781
[5 empty] | 2014-02-01 | 2 | 44 | 72251.7667 | 3119.364 | [35 empty] | 17 | 4679.1828
[5 empty] | 2014-03-01 | 3 | 46.8 | 84988.305 | 12736.5383 | [35 empty] | 17.1 | 4759.2814
[5 empty] | 2014-04-01 | 4 | 46.6 | 84066.8856 | -921.4193 | [35 empty] | 17.2 | 4840.1264
[5 empty] | 2014-05-01 | 5 | 49.7 | 98567.9556 | 14501.07 | [35 empty] | 17.3 | 4921.6184
[5 empty] | 2014-06-01 | 6 | 50.5 | 100000 | 1432.0444 | [35 empty] | 17.4 | 5003.9564
[5 empty] | 2014-07-01 | 7 | 48.8 | 94305.2653 | -5694.7347 | [35 empty] | 17.5 | 5086.9663
[5 empty] | 2014-08-01 | 8 | 45.6 | 79486.5134 | -14818.7519 | [35 empty] | 17.6 | 5170.7226
[5 empty] | 2014-09-01 | 9 | 44.4 | 74048.8454 | -5437.668 | [35 empty] | 17.7 | 5255.325
[5 empty] | 2014-10-01 | 10 | 41.7 | 62200.5823 | -11848.2632 | [35 empty] | 17.8 | 5340.7236
[5 empty] | 2014-11-01 | 11 | 41 | 59293.2965 | -2907.2858 | [35 empty] | 17.9 | 5427.0678
[5 empty] | 2014-12-01 | 12 | 39 | 51592.8884 | -7700.4081 | [35 empty] | 18 | 5514.2331
[5 empty] | 2015-01-01 | 1 | 43 | 67808.5249 | 16215.6365 | [35 empty] | 18.1 | 5602.344
[5 empty] | 2015-02-01 | 2 | 45.3 | 78120.9814 | 10312.4565 | [35 empty] | 18.2 | 5691.4502
[5 empty] | 2015-03-01 | 3 | 45.5 | 79030.9794 | 909.998 | [35 empty] | 18.3 | 5781.4273
[5 empty] | 2015-04-01 | 4 | 47 | 85911.4661 | 6880.4867 | [35 empty] | 18.4 | 5872.4246
[5 empty] | 2015-05-01 | 5 | 49.2 | 96193.8141 | 10282.348 | [35 empty] | 18.5 | 5964.2928
[5 empty] | 2015-06-01 | 6 | 53.4 | 100000 | 3806.1859 | [35 empty] | 18.6 | 6057.1315
[5 empty] | 2015-07-01 | 7 | 50.2 | 100000 | 0 | [35 empty] | 18.7 | 6150.9903
[5 empty] | 2015-08-01 | 8 | 48.9 | 94776.6995 | -5223.3005 | [35 empty] | 18.8 | 6245.7699
[5 empty] | 2015-09-01 | 9 | 45.7 | 79942.7441 | -14833.9554 | [35 empty] | 18.9 | 6341.6194
[5 empty] | 2015-10-01 | 10 | 45.1 | 77212.7501 | -2729.994 | [35 empty] | 19 | 6438.3647
[5 empty] | 2015-11-01 | 11 | 52 | 100000 | 22787.2499 | [35 empty] | 19.1 | 6536.18
[5 empty] | 2015-12-01 | 12 | 53.4 | 100000 | 0 | [35 empty] | 19.2 | 6635.2145
[5 empty] | 2016-01-01 | 1 | 49.9 | 99522.345 | -477.655 | [35 empty] | 19.3 | 6735.3936
[5 empty] | 2016-02-01 | 2 | 49.4 | 97141.6343 | -2380.7107 | [35 empty] | 19.4 | 6836.8916
[5 empty] | 2016-03-01 | 3 |  | #N/A | #N/A | [35 empty] | 19.5 | 6939.6088
[5 empty] | 2016-04-01 | 4 |  | #N/A | #N/A | [35 empty] | 19.6 | 7043.62
[5 empty] | 2016-05-01 | 5 |  | #N/A | #N/A | [35 empty] | 19.7 | 7148.9499
[5 empty] | 2016-06-01 | 6 |  | #N/A | #N/A | [35 empty] | 19.8 | 7255.4992
[5 empty] | 2016-07-01 | 7 |  | #N/A | #N/A | [35 empty] | 19.9 | 7363.3921
[5 empty] | 2016-08-01 | 8 |  | #N/A | #N/A | [35 empty] | 20 | 7472.5291
[5 empty] | 2016-09-01 | 9 |  | #N/A | #N/A | [35 empty] | 20.1 | 7583.1094
[5 empty] | 2016-10-01 | 10 |  | #N/A | #N/A | [35 empty] | 20.2 | 7695.1826
[5 empty] | 2016-11-01 | 11 |  | #N/A | #N/A | [35 empty] | 20.3 | 7808.724
[5 empty] | 2016-12-01 | 12 |  | #N/A | #N/A | [35 empty] | 20.4 | 7923.8828
[45 empty] | 20.5 | 8040.6589
[45 empty] | 20.6 | 8159.2515
[45 empty] | 20.7 | 8279.9343
[45 empty] | 20.8 | 8402.5829
[45 empty] | 20.9 | 8527.2718
[45 empty] | 21 | 8653.7026
[45 empty] | 21.1 | 8781.7757
[45 empty] | 21.2 | 8911.5905
[45 empty] | 21.3 | 9042.8237
[45 empty] | 21.4 | 9175.5499
[45 empty] | 21.5 | 9309.6944
[45 empty] | 21.6 | 9445.2573
[45 empty] | 21.7 | 9582.1887
[45 empty] | 21.8 | 9720.3394
[45 empty] | 21.9 | 9859.8835
[45 empty] | 22 | 10000.6967
[45 empty] | 22.1 | 10142.7789
[45 empty] | 22.2 | 10286.1551
[45 empty] | 22.3 | 10430.7256
[45 empty] | 22.4 | 10576.6896
[45 empty] | 22.5 | 10723.8479
[45 empty] | 22.6 | 10872.3251
[45 empty] | 22.7 | 11022.2206
[45 empty] | 22.8 | 11173.3851
[45 empty] | 22.9 | 11325.968
[45 empty] | 23 | 11479.7701
[45 empty] | 23.1 | 11634.7915
[45 empty] | 23.2 | 11791.1317
[45 empty] | 23.3 | 11948.6414
[45 empty] | 23.4 | 12107.5197
[45 empty] | 23.5 | 12267.667
[45 empty] | 23.6 | 12429.2077
[45 empty] | 23.7 | 12592.3161
[45 empty] | 23.8 | 12756.6687
[45 empty] | 23.9 | 12922.3898
[45 empty] | 24 | 13089.2306
[45 empty] | 24.1 | 13257.1663
[45 empty] | 24.2 | 13426.1969
[45 empty] | 24.3 | 13596.1232
[45 empty] | 24.4 | 13767.0947
[45 empty] | 24.5 | 13938.8872
[45 empty] | 24.6 | 14111.6005
[45 empty] | 24.7 | 14285.3837
[45 empty] | 24.8 | 14460.0378
[45 empty] | 24.9 | 14635.8615
[45 empty] | 25 | 14812.8048
[45 empty] | 25.1 | 14991.0421
[45 empty] | 25.2 | 15170.6231
[45 empty] | 25.3 | 15351.274
[45 empty] | 25.4 | 15533.2189
[45 empty] | 25.5 | 15716.1839
[45 empty] | 25.6 | 15900.3434
[45 empty] | 25.7 | 16085.7221
[45 empty] | 25.8 | 16272.121
[45 empty] | 25.9 | 16459.789
[45 empty] | 26 | 16648.502
[45 empty] | 26.1 | 16838.3099
[45 empty] | 26.2 | 17029.3122
[45 empty] | 26.3 | 17221.2352
[45 empty] | 26.4 | 17414.3277
[45 empty] | 26.5 | 17608.3159
[45 empty] | 26.6 | 17803.2995
[45 empty] | 26.7 | 17999.4775
[45 empty] | 26.8 | 18196.5761
[45 empty] | 26.9 | 18394.8691
[45 empty] | 27 | 18594.1077
[45 empty] | 27.1 | 18794.4162
[45 empty] | 27.2 | 18995.9192
[45 empty] | 27.3 | 19198.3677
[45 empty] | 27.4 | 19402.0106
[45 empty] | 27.5 | 19606.5741
[45 empty] | 27.6 | 19812.1827
[45 empty] | 27.7 | 20019.0106
[45 empty] | 27.8 | 20226.7592
[45 empty] | 27.9 | 20435.5778
[45 empty] | 28 | 20645.2424
[45 empty] | 28.1 | 20855.9769
[45 empty] | 28.2 | 21067.8561
[45 empty] | 28.3 | 21280.6062
[45 empty] | 28.4 | 21494.476
[45 empty] | 28.5 | 21709.1918
[45 empty] | 28.6 | 21924.8532
[45 empty] | 28.7 | 22141.6343
[45 empty] | 28.8 | 22359.2615
[45 empty] | 28.9 | 22578.0332
[45 empty] | 29 | 22797.6759
[45 empty] | 29.1 | 23018.3388
[45 empty] | 29.2 | 23240.1961
[45 empty] | 29.3 | 23462.974
[45 empty] | 29.4 | 23686.9215
[45 empty] | 29.5 | 23911.7896
[45 empty] | 29.6 | 24137.7277
[45 empty] | 29.7 | 24364.885
[45 empty] | 29.8 | 24592.9631
[45 empty] | 29.9 | 24822.2106
[45 empty] | 30 | 25052.4535
[45 empty] | 30.1 | 25284.04
[45 empty] | 30.2 | 25516.9951
[45 empty] | 30.3 | 25750.9953
[45 empty] | 30.4 | 25986.3143
[45 empty] | 30.5 | 26222.6784
[45 empty] | 30.6 | 26460.1871
[45 empty] | 30.7 | 26698.9897
[45 empty] | 30.8 | 26938.8375
[45 empty] | 30.9 | 27180.0786
[45 empty] | 31 | 27422.4147
[45 empty] | 31.1 | 27666.0446
[45 empty] | 31.2 | 27911.1177
[45 empty] | 31.3 | 28157.2609
[45 empty] | 31.4 | 28404.7726
[45 empty] | 31.5 | 28653.3294
[45 empty] | 31.6 | 28903.1054
[45 empty] | 31.7 | 29154.2998
[45 empty] | 31.8 | 29406.5641
[45 empty] | 31.9 | 29660.3215
[45 empty] | 32 | 29915.5469
[45 empty] | 32.1 | 30172.3151
[45 empty] | 32.2 | 30430.8251
[45 empty] | 32.3 | 30690.8032
[45 empty] | 32.4 | 30952.5978
[45 empty] | 32.5 | 31215.8605
[45 empty] | 32.6 | 31480.7903
[45 empty] | 32.7 | 31747.4619
[45 empty] | 32.8 | 32015.6017
[45 empty] | 32.9 | 32285.5579
[45 empty] | 33 | 32556.9573
[45 empty] | 33.1 | 32829.8746
[45 empty] | 33.2 | 33104.5337
[45 empty] | 33.3 | 33380.6858
[45 empty] | 33.4 | 33658.7539
[45 empty] | 33.5 | 33938.3398
[45 empty] | 33.6 | 34219.4934
[45 empty] | 33.7 | 34502.339
[45 empty] | 33.8 | 34786.4786
[45 empty] | 33.9 | 35072.2106
[45 empty] | 34 | 35359.0873
[45 empty] | 34.1 | 35647.3077
[45 empty] | 34.2 | 35936.9712
[45 empty] | 34.3 | 36227.7297
[45 empty] | 34.4 | 36519.9811
[45 empty] | 34.5 | 36813.3274
[45 empty] | 34.6 | 37108.0422
[45 empty] | 34.7 | 37404.2998
[45 empty] | 34.8 | 37701.8015
[45 empty] | 34.9 | 38000.8211
[45 empty] | 35 | 38300.9107
[45 empty] | 35.1 | 38602.2445
[45 empty] | 35.2 | 38905.0463
[45 empty] | 35.3 | 39208.943
[45 empty] | 35.4 | 39514.3326
[45 empty] | 35.5 | 39820.8669
[45 empty] | 35.6 | 40128.7698
[45 empty] | 35.7 | 40438.2403
[45 empty] | 35.8 | 40749.0047
[45 empty] | 35.9 | 41061.4114
[45 empty] | 36 | 41375.0871
[45 empty] | 36.1 | 41690.2807
[45 empty] | 36.2 | 42007.2161
[45 empty] | 36.3 | 42325.5698
[45 empty] | 36.4 | 42645.74
[45 empty] | 36.5 | 42967.3286
[45 empty] | 36.6 | 43290.5096
[45 empty] | 36.7 | 43615.6066
[45 empty] | 36.8 | 43942.2713
[45 empty] | 36.9 | 44270.852
[45 empty] | 37 | 44601.0003
[45 empty] | 37.1 | 44932.9899
[45 empty] | 37.2 | 45266.9454
[45 empty] | 37.3 | 45602.4435
[45 empty] | 37.4 | 45939.9323
[45 empty] | 37.5 | 46279.1132
[45 empty] | 37.6 | 46620.1354
[45 empty] | 37.7 | 46963.2726
[45 empty] | 37.8 | 47308.1268
[45 empty] | 37.9 | 47655.096
[45 empty] | 38 | 48003.7822
[45 empty] | 38.1 | 48354.4093
[45 empty] | 38.2 | 48707.1016
[45 empty] | 38.3 | 49061.4611
[45 empty] | 38.4 | 49417.9357
[45 empty] | 38.5 | 49776.0526
[45 empty] | 38.6 | 50135.9859
[45 empty] | 38.7 | 50497.8352
[45 empty] | 38.8 | 50861.1526
[45 empty] | 38.9 | 51226.3362
[45 empty] | 39 | 51592.8884
[45 empty] | 39.1 | 51960.9834
[45 empty] | 39.2 | 52330.845
[45 empty] | 39.3 | 52702.1001
[45 empty] | 39.4 | 53075.1468
[45 empty] | 39.5 | 53449.5869
[45 empty] | 39.6 | 53825.6196
[45 empty] | 39.7 | 54203.5433
[45 empty] | 39.8 | 54582.9601
[45 empty] | 39.9 | 54964.6163
[45 empty] | 40 | 55347.9397
[45 empty] | 40.1 | 55733.1791
[45 empty] | 40.2 | 56120.5584
[45 empty] | 40.3 | 56509.8039
[45 empty] | 40.4 | 56901.4134
[45 empty] | 40.5 | 57294.8144
[45 empty] | 40.6 | 57690.206
[45 empty] | 40.7 | 58087.9118
[45 empty] | 40.8 | 58487.4589
[45 empty] | 40.9 | 58889.3948
[45 empty] | 41 | 59293.2965
[45 empty] | 41.1 | 59699.5621
[45 empty] | 41.2 | 60112.123
[45 empty] | 41.3 | 60526.2516
[45 empty] | 41.4 | 60942.3957
[45 empty] | 41.5 | 61360.0328
[45 empty] | 41.6 | 61779.3371
[45 empty] | 41.7 | 62200.5823
[45 empty] | 41.8 | 62623.2706
[45 empty] | 41.9 | 63047.9248
[45 empty] | 42 | 63473.8977
[45 empty] | 42.1 | 63901.3885
[45 empty] | 42.2 | 64330.6211
[45 empty] | 42.3 | 64760.9734
[45 empty] | 42.4 | 65192.8436
[45 empty] | 42.5 | 65625.6594
[45 empty] | 42.6 | 66059.5949
[45 empty] | 42.7 | 66495.0732
[45 empty] | 42.8 | 66931.6214
[45 empty] | 42.9 | 67369.6128
[45 empty] | 43 | 67808.5249
[45 empty] | 43.1 | 68248.6563
[45 empty] | 43.2 | 68690.1563
[45 empty] | 43.3 | 69132.4027
[45 empty] | 43.4 | 69575.8435
[45 empty] | 43.5 | 70019.8816
[45 empty] | 43.6 | 70464.7158
[45 empty] | 43.7 | 70910.5703
[45 empty] | 43.8 | 71356.8478
[45 empty] | 43.9 | 71804.1206
[45 empty] | 44 | 72251.7667
[45 empty] | 44.1 | 72700.0348
[45 empty] | 44.2 | 73149.1739
[45 empty] | 44.3 | 73598.6115
[45 empty] | 44.4 | 74048.8454
[45 empty] | 44.5 | 74499.3033
[45 empty] | 44.6 | 74950.2837
[45 empty] | 44.7 | 75401.9857
[45 empty] | 44.8 | 75853.9365
[45 empty] | 44.9 | 76306.5841
[45 empty] | 45 | 76759.4307
[45 empty] | 45.1 | 77212.7501
[45 empty] | 45.2 | 77666.7662
[45 empty] | 45.3 | 78120.9814
[45 empty] | 45.4 | 78575.8933
[45 empty] | 45.5 | 79030.9794
[45 empty] | 45.6 | 79486.5134
[45 empty] | 45.7 | 79942.7441
[45 empty] | 45.8 | 80399.149
[45 empty] | 45.9 | 80856.2506
[45 empty] | 46 | 81313.5015
[45 empty] | 46.1 | 81771.2252
[45 empty] | 46.2 | 82229.6457
[45 empty] | 46.3 | 82688.2154
[45 empty] | 46.4 | 83147.5316
[45 empty] | 46.5 | 83606.9971
[45 empty] | 46.6 | 84066.8856
[45 empty] | 46.7 | 84527.5207
[45 empty] | 46.8 | 84988.305
[45 empty] | 46.9 | 85449.786
[45 empty] | 47 | 85911.4661
[45 empty] | 47.1 | 86373.5692
[45 empty] | 47.2 | 86836.4188
[45 empty] | 47.3 | 87299.4675
[45 empty] | 47.4 | 87763.2378
[45 empty] | 47.5 | 88227.2071
[45 empty] | 47.6 | 88691.6492
[45 empty] | 47.7 | 89156.8379
[45 empty] | 47.8 | 89622.2504
[45 empty] | 47.9 | 90088.4344
[45 empty] | 48 | 90554.8174
[45 empty] | 48.1 | 91021.698
[45 empty] | 48.2 | 91489.3749
[45 empty] | 48.3 | 91957.3007
[45 empty] | 48.4 | 92425.9978
[45 empty] | 48.5 | 92894.9438
[45 empty] | 48.6 | 93364.4123
[45 empty] | 48.7 | 93834.7019
[45 empty] | 48.8 | 94305.2653
[45 empty] | 48.9 | 94776.6995
[45 empty] | 49 | 95248.3826
[45 empty] | 49.1 | 95720.6629
[45 empty] | 49.2 | 96193.8141
[45 empty] | 49.3 | 96667.2639
[45 empty] | 49.4 | 97141.6343
[45 empty] | 49.5 | 97616.3283
[45 empty] | 49.6 | 98091.6692
[45 empty] | 49.7 | 98567.9556
[45 empty] | 49.8 | 99044.6402
[45 empty] | 49.9 | 99522.345
[45 empty] | 50 | 100000
Formulas:
Reservoir Storage Predictions = DATE(YEAR([Reservoir Storage Predictions, row below]),MONTH([Reservoir Storage Predictions, row below])-1,DAY([Reservoir Storage Predictions, row below]))
Reservoir Storage Predictions = DATE(YEAR([Reservoir Storage Predictions, row above]),MONTH([Reservoir Storage Predictions, row above])+1,DAY([Reservoir Storage Predictions, row above]))
Historical Data = DATE(YEAR([Historical Data, row above]),MONTH([Historical Data, row above])+1,DAY([Historical Data, row above]))
Access the reservoir elevation from the appropriate source. Record the level (in feet) for the first of the month and input it into the relevant box in column Y
Lookup table for storage volume. This table should not be altered except if there is a change in the bathymetry of the lake.
This table calculates statistics based on historical monthly changes in storage for the reservoir.
The drought fit (column AX) is based on the 30th percentile, with modifications as necessary (e.g., to remove anomolies or values > 0) described in the table below.
Column AY and the chart at right provide a basic check on the reasonableness of the drought fit.
The information in the average, min, and drought fit columns are the basis for future predictions in the table at left.
Group Box 15
Choose the probability required using the relevant radio button. (low = dry, high = wet)
This is the primary output of the prediction spreadsheet, indicating the number of months before the reservoir becomes at risk. The green dot indicates the reservoir is not expected to become at risk for at least the next 18 months.
This table predicts future storage based on the most recent storage records (rows 5-7), and the profiles of montly changes estimated in the "Calculation of Drought Fit" table at right.
This table calculates percentiles based on the historical monthly changes in storage for the reservoir. These percentiles are used to calculate the "Probability Fit" based on user selections in cells R26:R30.

## Off-Channel Reservoir
[5 empty] | Estimated Storage |  |  |  |  | Reservoir Storage Predictions |  |  |  | All values are in acre-feet | Calculation of Drought Fit | [11 empty] | Lake Bathymetry
| Risk | Drought Fit |  |  | Year | Month | Elevation (ft) | Storage (Acre-ft) | Change (Acre-ft) |  | Reservoir Characteristics |  | Drought Fit Forecast |  |  |  | Evaporation Location |  | I 35 Corr. |  | Most Recent Elevation: | 69.5 |  |  |  |  | Depth (ft) | Elevation (ft) | Volume (acre-ft) | Elevation (ft)
| Months to Empty | 25 |  |  | 2014-01-01 | 1 | 69.5 | 13650 |  | Date | Full Storage | At-Risk Storage | Storage | At Risk? |  |  | Pan Evaporation Assumptions |  |  | Storage Loss from Evaporation |  | Storage Loss from Consumption |  | Drought Fit | Evaporation Location Lookup |  | 20 | 70 | 14000 | 70
| Months to At Risk | 12 |  |  | 2014-02-01 | 2 | 69.5 | 13650 | 0 | 2015-12-01 | 14000 | 7000 | 13650 | No | Month (#) | Month | East TX | I 35 Corr. | West TX | Elevation (ft) | Storage (acre-ft) | Storage (acre-ft) | Elevation (ft) | Change (acre-ft) | East TX | 1 |  | 50 | 0 | 50
[5 empty] | 2014-03-01 | 3 | 69.5 | 13650 | 0 | 2016-01-01 | 14000 | 7000 | 13650 | No | 1 | JAN | 0.21667 | 0.25 | 0.35 | 69.25 | 13440 | 13407.7399 | 69.1 |  | I 35 Corr. | 2 |  | 50.1 | 70 | 50.1
| Generators at Risk | MW | Cap Fctr | MWh (2015) | 2014-04-01 | 4 | 69.5 | 13650 | 0 | 2016-02-01 | 14000 | 7000 | 13650 | No | 2 | FEB | 0.26667 | 0.33333 | 0.41667 | 68.7667 | 13090 | 13057.7399 | 68.6 | -350 | West TX | 3 |  | 50.2 | 140 | 50.2
| Generator 2 | 300 | 10% | 262800 | 2014-05-01 | 5 | 69.5 | 13650 | 0 | 2016-03-01 | 14000 | 7000 | 13160 | No | 3 | MAR | 0.4 | 0.51667 | 0.63333 | 68.0833 | 12600 | 12567.7399 | 67.9 | -490 | Location to use | 2 |  | 50.3 | 210 | 50.3
[5 empty] | 2014-06-01 | 6 | 69.5 | 13650 | 0 | 2016-04-01 | 14000 | 7000 | 12600 | No | 4 | APR | 0.5 | 0.61667 | 0.78333 | 67.2833 | 12040 | 12007.7399 | 67.1 | -560 |  |  |  | 50.4 | 280 | 50.4
[5 empty] | 2014-07-01 | 7 | 69.5 | 13650 | 0 | 2016-05-01 | 14000 | 7000 | 11970 | No | 5 | MAY | 0.59167 | 0.7 | 0.85 | 66.4 | 11410 | 11377.7399 | 66.2 | -630 |  |  |  | 50.5 | 350 | 50.5
[5 empty] | 2014-08-01 | 8 | 69.5 | 13650 | 0 | 2016-06-01 | 14000 | 7000 | 11270 | No | 6 | JUN | 0.63333 | 0.85 | 0.96667 | 65.35 | 10710 | 10677.7399 | 65.2 | -700 |  |  |  | 50.6 | 420 | 50.6
[5 empty] | 2014-09-01 | 9 | 69.5 | 13650 | 0 | 2016-07-01 | 14000 | 7000 | 10430 | No | 7 | JUL | 0.66667 | 1 | 1.0583 | 64.2 | 9870 | 9837.7399 | 64 | -840 |  |  |  | 50.7 | 490 | 50.7
| Monthly Consump | Acre-feet | gal/MWh | MWh (2015) | 2014-10-01 | 10 | 69.5 | 13650 | 0 | 2016-08-01 | 14000 | 7000 | 9660 | No | 8 | AUG | 0.64167 | 0.93333 | 0.98333 | 63.0667 | 9100 | 9067.7399 | 62.9 | -770 |  |  |  | 50.8 | 560 | 50.8
| Gas Steam-Non-reheat | 32.2601 | 480 | 21900 | 2014-11-01 | 11 | 69.5 | 13650 | 0 | 2016-09-01 | 14000 | 7000 | 9100 | No | 9 | SEPT | 0.5 | 0.69167 | 0.75 | 62.2083 | 8540 | 8507.7399 | 62.1 | -560 |  |  |  | 50.9 | 630 | 50.9
|  |  |  | 0 | 2014-12-01 | 12 | 69.5 | 13650 | 0 | 2016-10-01 | 14000 | 7000 | 8610 | No | 10 | OCT | 0.4 | 0.525 | 0.58333 | 61.575 | 8050 | 8017.7399 | 61.4 | -490 |  |  |  | 51 | 700 | 51
|  |  |  | 0 | 2015-01-01 | 1 | 69.5 | 13650 | 0 | 2016-11-01 | 14000 | 7000 | 8260 | No | 11 | NOV | 0.26667 | 0.34167 | 0.41667 | 61.0583 | 7700 | 7667.7399 | 60.9 | -350 |  |  |  | 51.1 | 770 | 51.1
|  |  |  | 0 | 2015-02-01 | 2 | 69.5 | 13650 | 0 | 2016-12-01 | 14000 | 7000 | 7980 | No | 12 | DEC | 0.23333 | 0.25833 | 0.33333 | 60.6417 | 7420 | 7387.7399 | 60.5 | -280 |  |  |  | 51.2 | 840 | 51.2
[5 empty] | 2015-03-01 | 3 | 69.5 | 13650 | 0 | 2017-01-01 | 14000 | 7000 | 7700 | No | 1 | JAN | 0.21667 | 0.25 | 0.35 | 60.25 | 7140 | 7107.7399 | 60.1 | -280 |  |  |  | 51.3 | 910 | 51.3
| Reservoir Details |  |  |  | 2015-04-01 | 4 | 69.5 | 13650 | 0 | 2017-02-01 | 14000 | 7000 | 7350 | No | 2 | FEB | 0.26667 | 0.33333 | 0.41667 | 59.7667 | 6790 | 6757.7399 | 59.6 | -350 |  |  |  | 51.4 | 980 | 51.4
| Full (Conservation) | 14000 | Acre-feet |  | 2015-05-01 | 5 | 69.5 | 13650 | 0 | 2017-03-01 | 14000 | 7000 | 6860 | Yes | [13 empty] | 51.5 | 1050 | 51.5
| At-Risk Level | 7000 | Acre-feet |  | 2015-06-01 | 6 | 69.5 | 13650 | 0 | 2017-04-01 | 14000 | 7000 | 6300 | Yes | [13 empty] | 51.6 | 1120 | 51.6
[5 empty] | 2015-07-01 | 7 | 69.5 | 13650 | 0 | 2017-05-01 | 14000 | 7000 | 5670 | Yes | [13 empty] | 51.7 | 1190 | 51.7
| At-Risk Level |  | Reasons |  | 2015-08-01 | 8 | 69.5 | 13650 | 0 | 2017-06-01 | 14000 | 7000 | 4970 | Yes | [13 empty] | 51.8 | 1260 | 51.8
| 50% | Set at default level of 50% for off channel reservoirs |  |  | 2015-09-01 | 9 | 69.5 | 13650 | 0 | 2017-07-01 | 14000 | 7000 | 4130 | Yes | [13 empty] | 51.9 | 1330 | 51.9
[5 empty] | 2015-10-01 | 10 | 69.5 | 13650 | 0 | 2017-08-01 | 14000 | 7000 | 3360 | Yes | [13 empty] | 52 | 1400 | 52
[5 empty] | 2015-11-01 | 11 | 69.5 | 13650 | 0 | 2017-09-01 | 14000 | 7000 | 2800 | Yes | [13 empty] | 52.1 | 1470 | 52.1
[5 empty] | 2015-12-01 | 12 | 69.5 | 13650 | 0 | 2017-10-01 | 14000 | 7000 | 2310 | Yes | [13 empty] | 52.2 | 1540 | 52.2
[5 empty] | 2016-01-01 | 1 | 69.5 | 13650 | 0 | 2017-11-01 | 14000 | 7000 | 1960 | Yes | [13 empty] | 52.3 | 1610 | 52.3
[5 empty] | 2016-02-01 | 2 | 69.5 | 13650 | 0 | 2017-12-01 | 14000 | 7000 | 1680 | Yes | [13 empty] | 52.4 | 1680 | 52.4
[5 empty] | 2016-03-01 | 3 |  | #N/A | #N/A | 2018-01-01 | 14000 | 7000 | 1400 | Yes | [13 empty] | 52.5 | 1750 | 52.5
[5 empty] | 2016-04-01 | 4 |  | #N/A | #N/A | 2018-02-01 | 14000 | 7000 | 1050 | Yes | [13 empty] | 52.6 | 1820 | 52.6
[5 empty] | 2016-05-01 | 5 |  | #N/A | #N/A | 2018-03-01 | 14000 | 7000 | 560 | Yes | [13 empty] | 52.7 | 1890 | 52.7
[5 empty] | 2016-06-01 | 6 |  | #N/A | #N/A | 2018-04-01 | 14000 | 7000 | 0 | Yes | [13 empty] | 52.8 | 1960 | 52.8
[5 empty] | 2016-07-01 | 7 |  | #N/A | #N/A | 2018-05-01 | 14000 | 7000 | -630 | Yes | [13 empty] | 52.9 | 2030 | 52.9
[5 empty] | 2016-08-01 | 8 |  | #N/A | #N/A | 2018-06-01 | 14000 | 7000 | -1330 | Yes | [13 empty] | 53 | 2100 | 53
[5 empty] | 2016-09-01 | 9 |  | #N/A | #N/A | 2018-07-01 | 14000 | 7000 | -2170 | Yes | [13 empty] | 53.1 | 2170 | 53.1
[5 empty] | 2016-10-01 | 10 |  | #N/A | #N/A | 2018-08-01 | 14000 | 7000 | -2940 | Yes | [13 empty] | 53.2 | 2240 | 53.2
[5 empty] | 2016-11-01 | 11 |  | #N/A | #N/A | 2018-09-01 | 14000 | 7000 | -3500 | Yes | [13 empty] | 53.3 | 2310 | 53.3
[5 empty] | 2016-12-01 | 12 |  | #N/A | #N/A | 2018-10-01 | 14000 | 7000 | -3990 | Yes | [13 empty] | 53.4 | 2380 | 53.4
[10 empty] | 2018-11-01 | 14000 | 7000 | -4340 | Yes | [13 empty] | 53.5 | 2450 | 53.5
[10 empty] | 2018-12-01 | 14000 | 7000 | -4620 | Yes | [13 empty] | 53.6 | 2520 | 53.6
[10 empty] | 2019-01-01 | 14000 | 7000 | -4900 | Yes | [13 empty] | 53.7 | 2590 | 53.7
[10 empty] | 2019-02-01 | 14000 | 7000 | -5250 | Yes | [13 empty] | 53.8 | 2660 | 53.8
[10 empty] | 2019-03-01 | 14000 | 7000 | -5740 | Yes | [13 empty] | 53.9 | 2730 | 53.9
[10 empty] | 2019-04-01 | 14000 | 7000 | -6300 | Yes | [13 empty] | 54 | 2800 | 54
[10 empty] | 2019-05-01 | 14000 | 7000 | -6930 | Yes | [13 empty] | 54.1 | 2870 | 54.1
[10 empty] | 2019-06-01 | 14000 | 7000 | -7630 | Yes | [13 empty] | 54.2 | 2940 | 54.2
[10 empty] | 2019-07-01 | 14000 | 7000 | -8470 | Yes | [13 empty] | 54.3 | 3010 | 54.3
[10 empty] | 2019-08-01 | 14000 | 7000 | -9240 | Yes | [13 empty] | 54.4 | 3080 | 54.4
[10 empty] | 2019-09-01 | 14000 | 7000 | -9800 | Yes | [13 empty] | 54.5 | 3150 | 54.5
[10 empty] | 2019-10-01 | 14000 | 7000 | -10290 | Yes | [13 empty] | 54.6 | 3220 | 54.6
[10 empty] | 2019-11-01 | 14000 | 7000 | -10640 | Yes | [13 empty] | 54.7 | 3290 | 54.7
[28 empty] | 54.8 | 3360 | 54.8
[28 empty] | 54.9 | 3430 | 54.9
[28 empty] | 55 | 3500 | 55
Notes: | [27 empty] | 55.1 | 3570 | 55.1
[28 empty] | 55.2 | 3640 | 55.2
[28 empty] | 55.3 | 3710 | 55.3
[28 empty] | 55.4 | 3780 | 55.4
[28 empty] | 55.5 | 3850 | 55.5
[28 empty] | 55.6 | 3920 | 55.6
[28 empty] | 55.7 | 3990 | 55.7
[28 empty] | 55.8 | 4060 | 55.8
[28 empty] | 55.9 | 4130 | 55.9
[28 empty] | 56 | 4200 | 56
[28 empty] | 56.1 | 4270 | 56.1
[28 empty] | 56.2 | 4340 | 56.2
[28 empty] | 56.3 | 4410 | 56.3
[28 empty] | 56.4 | 4480 | 56.4
[28 empty] | 56.5 | 4550 | 56.5
[28 empty] | 56.6 | 4620 | 56.6
[28 empty] | 56.7 | 4690 | 56.7
[28 empty] | 56.8 | 4760 | 56.8
[28 empty] | 56.9 | 4830 | 56.9
[28 empty] | 57 | 4900 | 57
[28 empty] | 57.1 | 4970 | 57.1
[28 empty] | 57.2 | 5040 | 57.2
[28 empty] | 57.3 | 5110 | 57.3
[28 empty] | 57.4 | 5180 | 57.4
[28 empty] | 57.5 | 5250 | 57.5
[28 empty] | 57.6 | 5320 | 57.6
[28 empty] | 57.7 | 5390 | 57.7
[28 empty] | 57.8 | 5460 | 57.8
[28 empty] | 57.9 | 5530 | 57.9
[28 empty] | 58 | 5600 | 58
[28 empty] | 58.1 | 5670 | 58.1
[28 empty] | 58.2 | 5740 | 58.2
[28 empty] | 58.3 | 5810 | 58.3
[28 empty] | 58.4 | 5880 | 58.4
[28 empty] | 58.5 | 5950 | 58.5
[28 empty] | 58.6 | 6020 | 58.6
[28 empty] | 58.7 | 6090 | 58.7
[28 empty] | 58.8 | 6160 | 58.8
[28 empty] | 58.9 | 6230 | 58.9
[28 empty] | 59 | 6300 | 59
[28 empty] | 59.1 | 6370 | 59.1
[28 empty] | 59.2 | 6440 | 59.2
[28 empty] | 59.3 | 6510 | 59.3
[28 empty] | 59.4 | 6580 | 59.4
[28 empty] | 59.5 | 6650 | 59.5
[28 empty] | 59.6 | 6720 | 59.6
[28 empty] | 59.7 | 6790 | 59.7
[28 empty] | 59.8 | 6860 | 59.8
[28 empty] | 59.9 | 6930 | 59.9
[28 empty] | 60 | 7000 | 60
[28 empty] | 60.1 | 7070 | 60.1
[28 empty] | 60.2 | 7140 | 60.2
[28 empty] | 60.3 | 7210 | 60.3
[28 empty] | 60.4 | 7280 | 60.4
[28 empty] | 60.5 | 7350 | 60.5
[28 empty] | 60.6 | 7420 | 60.6
[28 empty] | 60.7 | 7490 | 60.7
[28 empty] | 60.8 | 7560 | 60.8
[28 empty] | 60.9 | 7630 | 60.9
[28 empty] | 61 | 7700 | 61
[28 empty] | 61.1 | 7770 | 61.1
[28 empty] | 61.2 | 7840 | 61.2
[28 empty] | 61.3 | 7910 | 61.3
[28 empty] | 61.4 | 7980 | 61.4
[28 empty] | 61.5 | 8050 | 61.5
[28 empty] | 61.6 | 8120 | 61.6
[28 empty] | 61.7 | 8190 | 61.7
[28 empty] | 61.8 | 8260 | 61.8
[28 empty] | 61.9 | 8330 | 61.9
[28 empty] | 62 | 8400 | 62
[28 empty] | 62.1 | 8470 | 62.1
[28 empty] | 62.2 | 8540 | 62.2
[28 empty] | 62.3 | 8610 | 62.3
[28 empty] | 62.4 | 8680 | 62.4
[28 empty] | 62.5 | 8750 | 62.5
[28 empty] | 62.6 | 8820 | 62.6
[28 empty] | 62.7 | 8890 | 62.7
[28 empty] | 62.8 | 8960 | 62.8
[28 empty] | 62.9 | 9030 | 62.9
[28 empty] | 63 | 9100 | 63
[28 empty] | 63.1 | 9170 | 63.1
[28 empty] | 63.2 | 9240 | 63.2
[28 empty] | 63.3 | 9310 | 63.3
[28 empty] | 63.4 | 9380 | 63.4
[28 empty] | 63.5 | 9450 | 63.5
[28 empty] | 63.6 | 9520 | 63.6
[28 empty] | 63.7 | 9590 | 63.7
[28 empty] | 63.8 | 9660 | 63.8
[28 empty] | 63.9 | 9730 | 63.9
[28 empty] | 64 | 9800 | 64
[28 empty] | 64.1 | 9870 | 64.1
[28 empty] | 64.2 | 9940 | 64.2
[28 empty] | 64.3 | 10010 | 64.3
[28 empty] | 64.4 | 10080 | 64.4
[28 empty] | 64.5 | 10150 | 64.5
[28 empty] | 64.6 | 10220 | 64.6
[28 empty] | 64.7 | 10290 | 64.7
[28 empty] | 64.8 | 10360 | 64.8
[28 empty] | 64.9 | 10430 | 64.9
[28 empty] | 65 | 10500 | 65
[28 empty] | 65.1 | 10570 | 65.1
[28 empty] | 65.2 | 10640 | 65.2
[28 empty] | 65.3 | 10710 | 65.3
[28 empty] | 65.4 | 10780 | 65.4
[28 empty] | 65.5 | 10850 | 65.5
[28 empty] | 65.6 | 10920 | 65.6
[28 empty] | 65.7 | 10990 | 65.7
[28 empty] | 65.8 | 11060 | 65.8
[28 empty] | 65.9 | 11130 | 65.9
[28 empty] | 66 | 11200 | 66
[28 empty] | 66.1 | 11270 | 66.1
[28 empty] | 66.2 | 11340 | 66.2
[28 empty] | 66.3 | 11410 | 66.3
[28 empty] | 66.4 | 11480 | 66.4
[28 empty] | 66.5 | 11550 | 66.5
[28 empty] | 66.6 | 11620 | 66.6
[28 empty] | 66.7 | 11690 | 66.7
[28 empty] | 66.8 | 11760 | 66.8
[28 empty] | 66.9 | 11830 | 66.9
[28 empty] | 67 | 11900 | 67
[28 empty] | 67.1 | 11970 | 67.1
[28 empty] | 67.2 | 12040 | 67.2
[28 empty] | 67.3 | 12110 | 67.3
[28 empty] | 67.4 | 12180 | 67.4
[28 empty] | 67.5 | 12250 | 67.5
[28 empty] | 67.6 | 12320 | 67.6
[28 empty] | 67.7 | 12390 | 67.7
[28 empty] | 67.8 | 12460 | 67.8
[28 empty] | 67.9 | 12530 | 67.9
[28 empty] | 68 | 12600 | 68
[28 empty] | 68.1 | 12670 | 68.1
[28 empty] | 68.2 | 12740 | 68.2
[28 empty] | 68.3 | 12810 | 68.3
[28 empty] | 68.4 | 12880 | 68.4
[28 empty] | 68.5 | 12950 | 68.5
[28 empty] | 68.6 | 13020 | 68.6
[28 empty] | 68.7 | 13090 | 68.7
[28 empty] | 68.8 | 13160 | 68.8
[28 empty] | 68.9 | 13230 | 68.9
[28 empty] | 69 | 13300 | 69
[28 empty] | 69.1 | 13370 | 69.1
[28 empty] | 69.2 | 13440 | 69.2
[28 empty] | 69.3 | 13510 | 69.3
[28 empty] | 69.4 | 13580 | 69.4
[28 empty] | 69.5 | 13650 | 69.5
[28 empty] | 69.6 | 13720 | 69.6
[28 empty] | 69.7 | 13790 | 69.7
[28 empty] | 69.8 | 13860 | 69.8
[28 empty] | 69.9 | 13930 | 69.9
[28 empty] | 70 | 14000 | 70
[28 empty] | 70.1 | 14070 | 70.1
[28 empty] | 70.2 | 14140 | 70.2
[28 empty] | 70.3 | 14210 | 70.3
[28 empty] | 70.4 | 14280 | 70.4
[28 empty] | 70.5 | 14350 | 70.5
[28 empty] | 70.6 | 14420 | 70.6
[28 empty] | 70.7 | 14490 | 70.7
[28 empty] | 70.8 | 14560 | 70.8
[28 empty] | 70.9 | 14630 | 70.9
[28 empty] | 71 | 14700 | 71
[28 empty] | 71.1 | 14770 | 71.1
[28 empty] | 71.2 | 14840 | 71.2
[28 empty] | 71.3 | 14910 | 71.3
[28 empty] | 71.4 | 14980 | 71.4
[28 empty] | 71.5 | 15050 | 71.5
[28 empty] | 71.6 | 15120 | 71.6
[28 empty] | 71.7 | 15190 | 71.7
[28 empty] | 71.8 | 15260 | 71.8
[28 empty] | 71.9 | 15330 | 71.9
[28 empty] | 72 | 15400 | 72
[28 empty] | 72.1 | 15470 | 72.1
[28 empty] | 72.2 | 15540 | 72.2
[28 empty] | 72.3 | 15610 | 72.3
[28 empty] | 72.4 | 15680 | 72.4
[28 empty] | 72.5 | 15750 | 72.5
[28 empty] | 72.6 | 15820 | 72.6
[28 empty] | 72.7 | 15890 | 72.7
[28 empty] | 72.8 | 15960 | 72.8
[28 empty] | 72.9 | 16030 | 72.9
[28 empty] | 73 | 16100 | 73
[28 empty] | 73.1 | 16170 | 73.1
[28 empty] | 73.2 | 16240 | 73.2
[28 empty] | 73.3 | 16310 | 73.3
[28 empty] | 73.4 | 16380 | 73.4
[28 empty] | 73.5 | 16450 | 73.5
[28 empty] | 73.6 | 16520 | 73.6
[28 empty] | 73.7 | 16590 | 73.7
[28 empty] | 73.8 | 16660 | 73.8
[28 empty] | 73.9 | 16730 | 73.9
[28 empty] | 74 | 16800 | 74
[28 empty] | 74.1 | 16870 | 74.1
[28 empty] | 74.2 | 16940 | 74.2
[28 empty] | 74.3 | 17010 | 74.3
[28 empty] | 74.4 | 17080 | 74.4
[28 empty] | 74.5 | 17150 | 74.5
[28 empty] | 74.6 | 17220 | 74.6
[28 empty] | 74.7 | 17290 | 74.7
[28 empty] | 74.8 | 17360 | 74.8
[28 empty] | 74.9 | 17430 | 74.9
[28 empty] | 75 | 17500 | 75
[28 empty] | 75.1 | 17570 | 75.1
[28 empty] | 75.2 | 17640 | 75.2
[28 empty] | 75.3 | 17710 | 75.3
[28 empty] | 75.4 | 17780 | 75.4
[28 empty] | 75.5 | 17850 | 75.5
[28 empty] | 75.6 | 17920 | 75.6
[28 empty] | 75.7 | 17990 | 75.7
[28 empty] | 75.8 | 18060 | 75.8
[28 empty] | 75.9 | 18130 | 75.9
[28 empty] | 76 | 18200 | 76
[28 empty] | 76.1 | 18270 | 76.1
[28 empty] | 76.2 | 18340 | 76.2
[28 empty] | 76.3 | 18410 | 76.3
[28 empty] | 76.4 | 18480 | 76.4
[28 empty] | 76.5 | 18550 | 76.5
[28 empty] | 76.6 | 18620 | 76.6
[28 empty] | 76.7 | 18690 | 76.7
[28 empty] | 76.8 | 18760 | 76.8
[28 empty] | 76.9 | 18830 | 76.9
[28 empty] | 77 | 18900 | 77
[28 empty] | 77.1 | 18970 | 77.1
[28 empty] | 77.2 | 19040 | 77.2
[28 empty] | 77.3 | 19110 | 77.3
[28 empty] | 77.4 | 19180 | 77.4
[28 empty] | 77.5 | 19250 | 77.5
[28 empty] | 77.6 | 19320 | 77.6
[28 empty] | 77.7 | 19390 | 77.7
[28 empty] | 77.8 | 19460 | 77.8
[28 empty] | 77.9 | 19530 | 77.9
[28 empty] | 78 | 19600 | 78
[28 empty] | 78.1 | 19670 | 78.1
[28 empty] | 78.2 | 19740 | 78.2
[28 empty] | 78.3 | 19810 | 78.3
[28 empty] | 78.4 | 19880 | 78.4
[28 empty] | 78.5 | 19950 | 78.5
[28 empty] | 78.6 | 20020 | 78.6
[28 empty] | 78.7 | 20090 | 78.7
[28 empty] | 78.8 | 20160 | 78.8
[28 empty] | 78.9 | 20230 | 78.9
[28 empty] | 79 | 20300 | 79
[28 empty] | 79.1 | 20370 | 79.1
[28 empty] | 79.2 | 20440 | 79.2
[28 empty] | 79.3 | 20510 | 79.3
[28 empty] | 79.4 | 20580 | 79.4
[28 empty] | 79.5 | 20650 | 79.5
[28 empty] | 79.6 | 20720 | 79.6
[28 empty] | 79.7 | 20790 | 79.7
[28 empty] | 79.8 | 20860 | 79.8
[28 empty] | 79.9 | 20930 | 79.9
[28 empty] | 80 | 21000 | 80
[28 empty] | 80.1 | 21070 | 80.1
[28 empty] | 80.2 | 21140 | 80.2
[28 empty] | 80.3 | 21210 | 80.3
[28 empty] | 80.4 | 21280 | 80.4
[28 empty] | 80.5 | 21350 | 80.5
[28 empty] | 80.6 | 21420 | 80.6
[28 empty] | 80.7 | 21490 | 80.7
[28 empty] | 80.8 | 21560 | 80.8
[28 empty] | 80.9 | 21630 | 80.9
[28 empty] | 81 | 21700 | 81
[28 empty] | 81.1 | 21770 | 81.1
[28 empty] | 81.2 | 21840 | 81.2
[28 empty] | 81.3 | 21910 | 81.3
[28 empty] | 81.4 | 21980 | 81.4
[28 empty] | 81.5 | 22050 | 81.5
[28 empty] | 81.6 | 22120 | 81.6
[28 empty] | 81.7 | 22190 | 81.7
[28 empty] | 81.8 | 22260 | 81.8
[28 empty] | 81.9 | 22330 | 81.9
[28 empty] | 82 | 22400 | 82
[28 empty] | 82.1 | 22470 | 82.1
[28 empty] | 82.2 | 22540 | 82.2
[28 empty] | 82.3 | 22610 | 82.3
[28 empty] | 82.4 | 22680 | 82.4
[28 empty] | 82.5 | 22750 | 82.5
[28 empty] | 82.6 | 22820 | 82.6
[28 empty] | 82.7 | 22890 | 82.7
[28 empty] | 82.8 | 22960 | 82.8
[28 empty] | 82.9 | 23030 | 82.9
[28 empty] | 83 | 23100 | 83
[28 empty] | 83.1 | 23170 | 83.1
[28 empty] | 83.2 | 23240 | 83.2
[28 empty] | 83.3 | 23310 | 83.3
[28 empty] | 83.4 | 23380 | 83.4
[28 empty] | 83.5 | 23450 | 83.5
[28 empty] | 83.6 | 23520 | 83.6
[28 empty] | 83.7 | 23590 | 83.7
[28 empty] | 83.8 | 23660 | 83.8
[28 empty] | 83.9 | 23730 | 83.9
[28 empty] | 84 | 23800 | 84
[28 empty] | 84.1 | 23870 | 84.1
[28 empty] | 84.2 | 23940 | 84.2
[28 empty] | 84.3 | 24010 | 84.3
[28 empty] | 84.4 | 24080 | 84.4
[28 empty] | 84.5 | 24150 | 84.5
[28 empty] | 84.6 | 24220 | 84.6
[28 empty] | 84.7 | 24290 | 84.7
[28 empty] | 84.8 | 24360 | 84.8
[28 empty] | 84.9 | 24430 | 84.9
[28 empty] | 85 | 24500 | 85
[28 empty] | 85.1 | 24570 | 85.1
[28 empty] | 85.2 | 24640 | 85.2
[28 empty] | 85.3 | 24710 | 85.3
[28 empty] | 85.4 | 24780 | 85.4
[28 empty] | 85.5 | 24850 | 85.5
[28 empty] | 85.6 | 24920 | 85.6
[28 empty] | 85.7 | 24990 | 85.7
[28 empty] | 85.8 | 25060 | 85.8
[28 empty] | 85.9 | 25130 | 85.9
[28 empty] | 86 | 25200 | 86
[28 empty] | 86.1 | 25270 | 86.1
[28 empty] | 86.2 | 25340 | 86.2
[28 empty] | 86.3 | 25410 | 86.3
[28 empty] | 86.4 | 25480 | 86.4
[28 empty] | 86.5 | 25550 | 86.5
[28 empty] | 86.6 | 25620 | 86.6
[28 empty] | 86.7 | 25690 | 86.7
[28 empty] | 86.8 | 25760 | 86.8
[28 empty] | 86.9 | 25830 | 86.9
[28 empty] | 87 | 25900 | 87
[28 empty] | 87.1 | 25970 | 87.1
[28 empty] | 87.2 | 26040 | 87.2
[28 empty] | 87.3 | 26110 | 87.3
[28 empty] | 87.4 | 26180 | 87.4
[28 empty] | 87.5 | 26250 | 87.5
[28 empty] | 87.6 | 26320 | 87.6
[28 empty] | 87.7 | 26390 | 87.7
[28 empty] | 87.8 | 26460 | 87.8
[28 empty] | 87.9 | 26530 | 87.9
[28 empty] | 88 | 26600 | 88
[28 empty] | 88.1 | 26670 | 88.1
[28 empty] | 88.2 | 26740 | 88.2
[28 empty] | 88.3 | 26810 | 88.3
[28 empty] | 88.4 | 26880 | 88.4
[28 empty] | 88.5 | 26950 | 88.5
[28 empty] | 88.6 | 27020 | 88.6
[28 empty] | 88.7 | 27090 | 88.7
[28 empty] | 88.8 | 27160 | 88.8
[28 empty] | 88.9 | 27230 | 88.9
[28 empty] | 89 | 27300 | 89
[28 empty] | 89.1 | 27370 | 89.1
[28 empty] | 89.2 | 27440 | 89.2
[28 empty] | 89.3 | 27510 | 89.3
[28 empty] | 89.4 | 27580 | 89.4
[28 empty] | 89.5 | 27650 | 89.5
[28 empty] | 89.6 | 27720 | 89.6
[28 empty] | 89.7 | 27790 | 89.7
[28 empty] | 89.8 | 27860 | 89.8
[28 empty] | 89.9 | 27930 | 89.9
[28 empty] | 90 | 28000 | 90
[28 empty] | 90.1 | 28070 | 90.1
[28 empty] | 90.2 | 28140 | 90.2
[28 empty] | 90.3 | 28210 | 90.3
[28 empty] | 90.4 | 28280 | 90.4
[28 empty] | 90.5 | 28350 | 90.5
[28 empty] | 90.6 | 28420 | 90.6
[28 empty] | 90.7 | 28490 | 90.7
[28 empty] | 90.8 | 28560 | 90.8
[28 empty] | 90.9 | 28630 | 90.9
[28 empty] | 91 | 28700 | 91
[28 empty] | 91.1 | 28770 | 91.1
[28 empty] | 91.2 | 28840 | 91.2
[28 empty] | 91.3 | 28910 | 91.3
[28 empty] | 91.4 | 28980 | 91.4
[28 empty] | 91.5 | 29050 | 91.5
[28 empty] | 91.6 | 29120 | 91.6
[28 empty] | 91.7 | 29190 | 91.7
[28 empty] | 91.8 | 29260 | 91.8
[28 empty] | 91.9 | 29330 | 91.9
[28 empty] | 92 | 29400 | 92
[28 empty] | 92.1 | 29470 | 92.1
[28 empty] | 92.2 | 29540 | 92.2
[28 empty] | 92.3 | 29610 | 92.3
[28 empty] | 92.4 | 29680 | 92.4
[28 empty] | 92.5 | 29750 | 92.5
[28 empty] | 92.6 | 29820 | 92.6
[28 empty] | 92.7 | 29890 | 92.7
[28 empty] | 92.8 | 29960 | 92.8
[28 empty] | 92.9 | 30030 | 92.9
[28 empty] | 93 | 30100 | 93
[28 empty] | 93.1 | 30170 | 93.1
[28 empty] | 93.2 | 30240 | 93.2
[28 empty] | 93.3 | 30310 | 93.3
[28 empty] | 93.4 | 30380 | 93.4
[28 empty] | 93.5 | 30450 | 93.5
[28 empty] | 93.6 | 30520 | 93.6
[28 empty] | 93.7 | 30590 | 93.7
[28 empty] | 93.8 | 30660 | 93.8
[28 empty] | 93.9 | 30730 | 93.9
[28 empty] | 94 | 30800 | 94
[28 empty] | 94.1 | 30870 | 94.1
[28 empty] | 94.2 | 30940 | 94.2
[28 empty] | 94.3 | 31010 | 94.3
[28 empty] | 94.4 | 31080 | 94.4
[28 empty] | 94.5 | 31150 | 94.5
[28 empty] | 94.6 | 31220 | 94.6
[28 empty] | 94.7 | 31290 | 94.7
[28 empty] | 94.8 | 31360 | 94.8
[28 empty] | 94.9 | 31430 | 94.9
[28 empty] | 95 | 31500 | 95
[28 empty] | 95.1 | 31570 | 95.1
[28 empty] | 95.2 | 31640 | 95.2
[28 empty] | 95.3 | 31710 | 95.3
[28 empty] | 95.4 | 31780 | 95.4
[28 empty] | 95.5 | 31850 | 95.5
[28 empty] | 95.6 | 31920 | 95.6
[28 empty] | 95.7 | 31990 | 95.7
[28 empty] | 95.8 | 32060 | 95.8
[28 empty] | 95.9 | 32130 | 95.9
[28 empty] | 96 | 32200 | 96
[28 empty] | 96.1 | 32270 | 96.1
[28 empty] | 96.2 | 32340 | 96.2
[28 empty] | 96.3 | 32410 | 96.3
[28 empty] | 96.4 | 32480 | 96.4
[28 empty] | 96.5 | 32550 | 96.5
[28 empty] | 96.6 | 32620 | 96.6
[28 empty] | 96.7 | 32690 | 96.7
[28 empty] | 96.8 | 32760 | 96.8
[28 empty] | 96.9 | 32830 | 96.9
[28 empty] | 97 | 32900 | 97
[28 empty] | 97.1 | 32970 | 97.1
[28 empty] | 97.2 | 33040 | 97.2
[28 empty] | 97.3 | 33110 | 97.3
[28 empty] | 97.4 | 33180 | 97.4
[28 empty] | 97.5 | 33250 | 97.5
[28 empty] | 97.6 | 33320 | 97.6
[28 empty] | 97.7 | 33390 | 97.7
[28 empty] | 97.8 | 33460 | 97.8
[28 empty] | 97.9 | 33530 | 97.9
[28 empty] | 98 | 33600 | 98
[28 empty] | 98.1 | 33670 | 98.1
[28 empty] | 98.2 | 33740 | 98.2
[28 empty] | 98.3 | 33810 | 98.3
[28 empty] | 98.4 | 33880 | 98.4
[28 empty] | 98.5 | 33950 | 98.5
[28 empty] | 98.6 | 34020 | 98.6
[28 empty] | 98.7 | 34090 | 98.7
[28 empty] | 98.8 | 34160 | 98.8
[28 empty] | 98.9 | 34230 | 98.9
[28 empty] | 99 | 34300 | 99
[28 empty] | 99.1 | 34370 | 99.1
[28 empty] | 99.2 | 34440 | 99.2
[28 empty] | 99.3 | 34510 | 99.3
[28 empty] | 99.4 | 34580 | 99.4
[28 empty] | 99.5 | 34650 | 99.5
[28 empty] | 99.6 | 34720 | 99.6
[28 empty] | 99.7 | 34790 | 99.7
[28 empty] | 99.8 | 34860 | 99.8
[28 empty] | 99.9 | 34930 | 99.9
[28 empty] | 100 | 35000 | 100
[28 empty] | 100.1 | 35070 | 100.1
[28 empty] | 100.2 | 35140 | 100.2
[28 empty] | 100.3 | 35210 | 100.3
[28 empty] | 100.4 | 35280 | 100.4
[28 empty] | 100.5 | 35350 | 100.5
[28 empty] | 100.6 | 35420 | 100.6
[28 empty] | 100.7 | 35490 | 100.7
[28 empty] | 100.8 | 35560 | 100.8
[28 empty] | 100.9 | 35630 | 100.9
[28 empty] | 101 | 35700 | 101
[28 empty] | 101.1 | 35770 | 101.1
[28 empty] | 101.2 | 35840 | 101.2
[28 empty] | 101.3 | 35910 | 101.3
[28 empty] | 101.4 | 35980 | 101.4
[28 empty] | 101.5 | 36050 | 101.5
[28 empty] | 101.6 | 36120 | 101.6
[28 empty] | 101.7 | 36190 | 101.7
[28 empty] | 101.8 | 36260 | 101.8
[28 empty] | 101.9 | 36330 | 101.9
[28 empty] | 102 | 36400 | 102
[28 empty] | 102.1 | 36470 | 102.1
[28 empty] | 102.2 | 36540 | 102.2
[28 empty] | 102.3 | 36610 | 102.3
[28 empty] | 102.4 | 36680 | 102.4
[28 empty] | 102.5 | 36750 | 102.5
[28 empty] | 102.6 | 36820 | 102.6
[28 empty] | 102.7 | 36890 | 102.7
[28 empty] | 102.8 | 36960 | 102.8
[28 empty] | 102.9 | 37030 | 102.9
[28 empty] | 103 | 37100 | 103
[28 empty] | 103.1 | 37170 | 103.1
[28 empty] | 103.2 | 37240 | 103.2
[28 empty] | 103.3 | 37310 | 103.3
[28 empty] | 103.4 | 37380 | 103.4
[28 empty] | 103.5 | 37450 | 103.5
[28 empty] | 103.6 | 37520 | 103.6
[28 empty] | 103.7 | 37590 | 103.7
[28 empty] | 103.8 | 37660 | 103.8
[28 empty] | 103.9 | 37730 | 103.9
[28 empty] | 104 | 37800 | 104
[28 empty] | 104.1 | 37870 | 104.1
[28 empty] | 104.2 | 37940 | 104.2
[28 empty] | 104.3 | 38010 | 104.3
[28 empty] | 104.4 | 38080 | 104.4
[28 empty] | 104.5 | 38150 | 104.5
[28 empty] | 104.6 | 38220 | 104.6
[28 empty] | 104.7 | 38290 | 104.7
[28 empty] | 104.8 | 38360 | 104.8
[28 empty] | 104.9 | 38430 | 104.9
[28 empty] | 105 | 38500 | 105
[28 empty] | 105.1 | 38570 | 105.1
[28 empty] | 105.2 | 38640 | 105.2
[28 empty] | 105.3 | 38710 | 105.3
[28 empty] | 105.4 | 38780 | 105.4
[28 empty] | 105.5 | 38850 | 105.5
[28 empty] | 105.6 | 38920 | 105.6
[28 empty] | 105.7 | 38990 | 105.7
[28 empty] | 105.8 | 39060 | 105.8
[28 empty] | 105.9 | 39130 | 105.9
[28 empty] | 106 | 39200 | 106
[28 empty] | 106.1 | 39270 | 106.1
[28 empty] | 106.2 | 39340 | 106.2
[28 empty] | 106.3 | 39410 | 106.3
[28 empty] | 106.4 | 39480 | 106.4
[28 empty] | 106.5 | 39550 | 106.5
[28 empty] | 106.6 | 39620 | 106.6
[28 empty] | 106.7 | 39690 | 106.7
[28 empty] | 106.8 | 39760 | 106.8
[28 empty] | 106.9 | 39830 | 106.9
[28 empty] | 107 | 39900 | 107
[28 empty] | 107.1 | 39970 | 107.1
[28 empty] | 107.2 | 40040 | 107.2
[28 empty] | 107.3 | 40110 | 107.3
[28 empty] | 107.4 | 40180 | 107.4
[28 empty] | 107.5 | 40250 | 107.5
[28 empty] | 107.6 | 40320 | 107.6
[28 empty] | 107.7 | 40390 | 107.7
[28 empty] | 107.8 | 40460 | 107.8
[28 empty] | 107.9 | 40530 | 107.9
[28 empty] | 108 | 40600 | 108
[28 empty] | 108.1 | 40670 | 108.1
[28 empty] | 108.2 | 40740 | 108.2
[28 empty] | 108.3 | 40810 | 108.3
[28 empty] | 108.4 | 40880 | 108.4
[28 empty] | 108.5 | 40950 | 108.5
[28 empty] | 108.6 | 41020 | 108.6
[28 empty] | 108.7 | 41090 | 108.7
[28 empty] | 108.8 | 41160 | 108.8
[28 empty] | 108.9 | 41230 | 108.9
[28 empty] | 109 | 41300 | 109
[28 empty] | 109.1 | 41370 | 109.1
[28 empty] | 109.2 | 41440 | 109.2
[28 empty] | 109.3 | 41510 | 109.3
[28 empty] | 109.4 | 41580 | 109.4
[28 empty] | 109.5 | 41650 | 109.5
Formulas:
Estimated Storage = DATE(YEAR([Estimated Storage, row above]),MONTH([Estimated Storage, row above])+1,DAY([Estimated Storage, row above]))
Reservoir Storage Predictions = DATE(YEAR([Reservoir Storage Predictions, row below]),MONTH([Reservoir Storage Predictions, row below])-1,DAY([Reservoir Storage Predictions, row below]))
Reservoir Storage Predictions = DATE(YEAR([Reservoir Storage Predictions, row above]),MONTH([Reservoir Storage Predictions, row above])+1,DAY([Reservoir Storage Predictions, row above]))
Group Box 15
For off channel reservoirs. with (normally) constant levels, this table uses a pan evaporation and consumption (gals/MWh) to calculate the level and storage reductions
For sites with no level information use the conservation level and total depth to create a storage profile.
Select the evaporation location to use in calculations based on the geographic location of the reservoir in the state.
Consumption assumptions are based on information entered in the table in cells Q13:T17.
The monthly
change in storage after accounting for evaporation and consumption is used to forecast future storage in the reservoir.
This table predicts future storage based on the estimated storage in the table at left, and the profiles of montly changes estimated in the "Calculation of Drought Fit" table (columns AI to AR).
Because monitoring data is unavailable, the model assumes the reservoir is kept at constant levels.
This is the primary output of the prediction spreadsheet, indicating the number of months before the reservoir becomes at risk. The yellow dot indicates, should secondary water sources fail, the reservoir could become at risk within 12 months.
Note on BE3: Black & Veatch: Second Elevation column for calculations