Planning Geomagnetic Disturbance Task Force

(PGDTF) Procedure Manual

March 29, 2016

| Date | Version | Description | Author(s) | Comments |
| --- | --- | --- | --- | --- |
| 03/29/2016 | Draft V 1 | First Draft of Section 4 | ERCOT |  |

# Revisions and Approval History

# 1 Introduction

# ERCOT Planning Geomagnetic Disturbance Task Force Scope

## The purpose of the Planning Geomagnetic Task Force (PGDTF) is to develop and maintain the Geomagnetic Induced Current (GIC) system model which will be used by ERCOT to calculate per phase GICs and Mvar losses for each modeled transformer.

# Activities of the PGDTF

# Administrative Procedures

## Membership

## PGTF membership consists of representatives from each Transmission Planner that is subject to TPL-007-1, ERCOT, and other interested Transmission and/or Distribution Service Providers (TDSPs), Qualified Scheduling Entities (QSEs) and Resource Entities.  Meetings of the PGTF shall be open to all interested parties.

## Duties of Chair and Vice-Chair

## The Chair and Vice-Chair positions shall be nominated by the PGTF for approval by ROS to a term     not to exceed 12 months, on a one year, rolling basis.  The Vice-Chair shall act as Chair in the absence of the Chair.

## Meetings

## The PGTF shall meet as often as necessary to perform their duties and functions.

## All PGTF meetings shall be called by the Chair and/or Vice-Chair and all such meeting notices shall be sent and posted to the ERCOT website at least one week prior to the meeting.

## The Chair shall preside at all meetings and is responsible for preparation of agendas for such meetings which will be posted to the ERCOT website in advance of the meeting.  In the absence of the Chair and the Vice-Chair, the group shall select another PGTF member to preside at the meeting.  The Chair, or the presiding member, shall be guided by input from the membership in the conduct of the meetings. Notes of PGTF meetings shall be recorded and distributed, along with other communications to all members of the PGTF.  Additionally, such information will be posted on the ERCOT website as authorized by the PGTF and author of document.

## Reports to ROS

## The Chair or Vice-Chair shall provide reports on the group’s activities to the ROS at its scheduled meetings or outside of the meetings if urgency dictates.

# 3 Definitions and Acronyms

# 4 Data Requirements for GIC System Model

## General

### Software – PSSE will be used by ERCOT to perform the items for which it is responsible.

### GIC System Models – General

- Substation Ground Grid and Neutral Connected GIC Blocking Data

- Series Capacitor

- Transformer Data Including Generator Step-Up

- Bus Fixed Shunt Data

- Transmission Line Models

### Modeling Refinements

- Non-Uniform Source Fields

- Non-Uniform Earth Structure

- Including Neighboring Systems

### Maintenance of GIC System Model  (IMM and RARF)

### GIC Data for Existing Equipment (IMM)

### GIC Data for Planned Equipment (may not need) ? No place in MOD for Transmission Co. owned equipment, Pre-RARF for RE owned equipment.

## GIC Data for Equipment Owned by Transmission-Distribution Service Providers (TDSP)

### GIC Data Requirements for Existing Equipment

### Updates to Existing GIC Data

## GIC Data for Equipment Owned by Resource Entities (RE)

### 4.3.1  GIC Data Requirements for Existing Equipment

### Updates to Existing GIC Data

### Missing or Problematic GIC Data

# Overview of PGDTF Activities

## Updating PGDTF Data and Cases

### Schedule for GIC Data Updates and GIC System Model

### PGDTF Data Updates

### PGDTF Data Screening

### PGDTF Cases Screening Criteria

## PGDTF Study Methodologies and Criteria

### Steady State Voltage Criteria

### Voltage Instability Identification in Stability Studies

### Cascading Identification in Stability Studies

### Uncontrolled Islanding Identification in Stability Studies

## Post Case Screening Activities

### Distribution of Screening Results and the GIC System Data File

### PGDTF Coordination with the Steady State & Dynamics Working Groups

### PGDTF Case Screening Assumptions List

## Other PGDTF Activities

### Data Recording Requirements

### Triggering Requirements

### Data Reporting Requirements

### Maintenance and Testing Requirements

### Event Simulation

### Procedure Manual Revision Guidelines

## On a periodic basis, PGDTF will review the Procedure Manual for needed updates.  Any      member of PGDTF can submit proposed changes.  The PGDTF will strive to develop consensus on the proposed changes.  If consensus cannot be achieved, alternative proposed changes will be developed with an explanation of the alternatives and will provided to the Reliability Operations Subcommittee (ROS) for its consideration.  A red-lined version and a final version will be provided to ROS for its review and approval.

# 4 Data Requirements for GIC System Model

## General

### Software

PSSE will be used by the ERCOT Planning Coordinator and Transmission Planners to build the GIC system models.  Models will not be created in any other format by ERCOT.  The PSSE version used will follow the version used by the Steady State Working Group.

### GIC System Models – General

For the 345 kV system, actual data should be used for the GIC system model unless the software specifies a certain value.  Typical data based upon actual data can be used if actual data is not available.

For the 138 kV system, actual data should be used for the GIC system model to the extent possible unless the software specifies a certain value.  Typical data based upon actual data can be used if actual data is not available.  Default data as specified by this Procedure Manual can be used if actual or typical data is not available.

For the 69 kV system, actual data should be used for the GIC system model if available unless the software specifies a certain value.  Typical data based upon actual data can be used if actual data is not available.  Default data as specified by this Procedure Manual can be used if actual or typical data is not available.

A SSWG base case updated to reflect known changes will be used as the starting base case for the GIC system model.

Substation Data

The format for the Substation record is:

I, NAME, UNIT, LATITUDE, LONGITUDE, RG

This Substation Data record will be provided by TP for all stations not in NMMS.  For stations in NMMS, TSP will update the appropriate field with these values and ERCOT will extract the needed data.

| I | Station Number – This value will be from the ERCOT database based on keeping the same station number for a given station name each time a case is built | ERCOT to provide station/bus mapping from NMMS. TSP model station/bus relationship in NMMS for their facilities ERCOT model station/bus relationship in NMMS for RE facilities |
| --- | --- | --- |
| NAME | Station | ERCOT to provide long or short name for substation from NMMS. TSP update names in NMMS. |
| UNIT | Unit for geophysical location will always equal 0 | Default to 0 |
| LATITUDE | Station Latitude | ERCOT will provide for existing stations from NMMS for TPs who request ERCOT to do so and for power plants. TPs will provide this data for their future stations via Substation Data record. |
| LONGITUDE | Station Longitude | ERCOT to provide for existing stations from NMMS for TPs who request ERCOT to do so and for power plants. TSP to provide for future stations via this Substation Data record |
| RG | Substation grounding DC resistance (in Ohms) from NMMS (new to NMMS) | ERCOT to provide for existing stations from NMMS TSP to provide via this Substation Data record for future stations. |
| EARTHMD (v34) | Name of the Earth Model | From USGS standard earth conductivity models which can be found on USGS’s website |

Bus Substation Data

This data set consists of two data -- BUSNUM and SUBNUM, where BUSNUM is the bus number for a bus that exists in power flow network data for an SSWG case, and SUBNUM is the substation number for a substation to which the bus with “BUSNUM” belongs to.

The format for Bus Substation Data is:

BUSNUM, SUBNUM

ERCOT will provide bus-substation mapping from NMMS and generate the Bus Substation Data.

Series Capacitors

Series capacitors are used in the bulk power system to re-direct power flow and improve system stability. Series capacitors present very high impedance to the flow of GIC. NERC recommends two modeling methods in their GIC application guide. One method is to model the series capacitor with a very large resistance (1 megohm), and another method is to remove the line connecting the series capacitor from the model completely.  In the ERCOT GIC system model, use the 1 megohm method.

Transformer Data Including Generator Step-Up

The format for the Transformer Data is:

I, J, K, CKT, WRI, WRJ, WRK, GICBDI, GICBDJ, GICBDK, VECGRP, CORE, KFACTOR, GRDWRI, GRDWRJ, GRDWRK, TMODEL

The transformer specified by buses "I, J, K, CKT" must exist in power flow data. Also the winding bus order must be same as in power flow data.

| I | The bus number of the bus to which Winding 1 is connected. It must be same Winding 1 bus for the same transformer power flow data. No default allowed. | This number comes from SSWG base case. |
| --- | --- | --- |
| J | The bus number of the bus to which Winding 2 is connected. It must be same Winding 2 bus for the same transformer power flow data. No default allowed. | This number comes from SSWG base case. |
| K | The bus number of the bus to which Winding 3 is connected. It must be same Winding 3 bus for the same transformer power flow data. No default allowed. | This number comes from SSWG base case. |
| CKT | One- or two-character non-blank alphanumeric circuit identifier | This comes from SSWG base case. |
| WRI | DC resistance of Winding 1 in ohms/phase. WRI = 0.0 by default. When WRI is not specified, power flow data resistance is used to determine WRI. | REs and TSPs provide this value through RARF and NMMS respectively. |
| WRJ | DC resistance of Winding 2 in ohms/phase. WRJ = 0.0 by default. When WRJ is not specified, power flow data resistance is used to determine WRJ. | REs and TSPs provide this value through RARF and NMMS respectively. |
| WRK | DC resistance of Winding 3 in ohms/phase. WRK = 0.0 by default. When WRK is not specified, power flow data resistance is used to determine WRK. | REs and TSPs provide this value through RARF and NMMS respectively. |
| GICBDI | GIC blocking device in neutral of Winding 1. = 0, no GIC blocking device present = 1, GIC blocking device present For an auto-transformers, if either GICBDI=1 or GICBDJ=1, that autotransformer is treated as it has GIC blocking device present. GICBDI = 0 by default. | REs and TSPs provide this value through RARF and NMMS respectively. |
| GICBDJ | GIC blocking device in neutral of Winding 2. = 0, no GIC blocking device present = 1, GIC blocking device present For an auto-transformers, if either GICBDI=1 or GICBDJ=1, that autotransformer is treated as it has GIC blocking device present. GICBDJ = 0 by default. | REs and TSPs provide this value through RARF and NMMS respectively. |
| GICBDK | GIC blocking device in neutral of Winding 3. = 0, no GIC blocking device present = 1, GIC blocking device present GICBDK = 0 for two winding transformers GICBDK = 0 by default. | REs and TSPs provide this value through RARF and NMMS respectively. |
| VECGRP | Alphanumeric identifier specifying vector group based on transformer winding connections and phase angles. VECGRP is 12 blanks by default. If vector group is specified in power flow data that data will be used and it is not needed to be specified here. As far as GIC calculations are concerned, winding grounding connection information is used; its clock angles are not used. • Specify VECGRP considering the winding order I, J, K defined on this record. • For auto transformers, bus with lower base bus voltage is treated as common winding bus. • For three winding auto transformers, windings on bus I and bus J form auto transformer. Winding connection designations First Symbol: for High Voltage: Always capital letters. D=Delta, Y=Wye, Z=Interconnected star, N=Neutral Second Symbol: for Low voltage: Always Small letters. d=Delta, y=wye, z=Interconnected star, n=Neutral. Third Symbol: Phase displacement expressed as the clock hour number (1,6,11) 0 =0° that the LV phasor is in phase with the HV phasor 1 =30° lagging (LV lags HV with 30°) because rotation is anti-clockwise. 11 = 330° lagging or 30° leading (LV leads HV with 30°) 5 = 150° lagging (LV lags HV with 150°) 6 = 180° lagging (LV lags HV with 180°) | REs and TSPs provide this data through RARF and NMMS respectively. |
| CORE | Number of cores in transformer core design. This information is used to calculate transformer reactive power loss from GIC flowing its winding. = -1 for three phase shell form = 0 for unknown core design = 1 for single core design = 3 for three phase 3-legged core form = 5 for three phase 5-legged core form CORE = 0 by default | REs and TSPs provide this value through RARF and NMMS respectively. |
| KFACTOR | A factor to calculate transformer reactive power loss from GIC flowing in its winding (MVAR/AMP). KFACTOR = 0.0 by default. Windings Highest Voltage KFACTOR Unknown core, <= 200 kV 0.6 Unknown core, > 200 kV and <= 400 kV 0.6 Unknown core, > 400 kV 1.1 | REs and TSPs provide this data through RARF and NMMS respectively. |
| GRDWRI | Winding 1 grounding DC resistance in ohms GRDWRI = 0.0 by default (no grounding resistance) | REs and TSPs provide this data through RARF and NMMS respectively. |
| GRDWRJ | Winding 2 grounding DC resistance in ohms GRDWRJ = 0.0 by default (no grounding resistance) | REs and TSPs provide this data through RARF and NMMS respectively. |
| GRDWRK | Winding 3 grounding DC resistance in ohms GRDWRK = 0.0 by default (no grounding resistance) | REs and TSPs provide this data through RARF and NMMS respectively. |
| TMODEL | Transformer Model in GIC DC Network = 0, two/three/auto transformer model as defined by its vector group = 1, Transformer as T model in DC network. TMODEL = 0 by default | REs and TSPs provide this data through RARF and NMMS respectively. |

Bus Fixed Shunt Data

The format for the Bus Fixed Shunt Data is

I, ID, R, RG

Only in-service bus fixed shunts are modeled in GIC DC network.

| I | Bus number of the bus to which fixed shunt is connected. It must be present in power flow network data. No default allowed. | This number comes from SSWG base case. |
| --- | --- | --- |
| ID | One- or two-character non-blank alphanumeric shunt identifier | This value comes from SSWG base case. |
| R | DC resistance in ohms/phase. It must be > 0. No default allowed. Fixed bus shunt records with R=0 will be ignored. | REs and TSPs provide this data through RARF and NMMS respectively. |
| RG | Grounding DC resistance in ohms. RG = 0.0 by default (no grounding resistance) | REs and TSPs provide this data through RARF and NMMS respectively. |

Transmission Line Models

The format for Branch Data (v34) is

I, J, CKT, RBRN, INDVP, INDVQ

| I | Branch from bus number. No default allowed. | This number comes from SSWG base case. |
| --- | --- | --- |
| J | Branch to bus number. No default allowed. | This number comes from SSWG base case. |
| CKT | One- or two-character non-blank alphanumeric branch circuit identifier | This value comes from SSWG base case. |
| RBRN | Branch DC resistance in ohms/phase. RBRN = 0.0 by default. When RBRN is not specified or RBRN=0.0, power flow data branch resistance is used as is. | REs and TSPs provide this data through RARF and NMMS respectively. |
| INDVP | Real part of total branch GMD induced electric field in volts. |  |
| INDVQ | Imaginary part of total branch GMD induced electric field in volts. |  |

Notes:

Total branch GMD induced electric field, INDUCEDV = INDVP + j INDVQ volts. Branch INDUCEDV is determined as below:

a. When INDUCEDV is not specified, GIC activity calculates this according to  GMD event specified.

b. When INDUCEDV is specified, it is used as GMD induced electric field on that branch.

c. When INDUCEDV is specified as INDVP = 0.0 and INDVQ = 0.0, then that branch

is treated as part of GIC DC network but does not have GMD induced voltage, like

"underground cable".

For uniform filed modeling INDUCEDV will be real value, but for non-uniform field modeling this will be complex value.

This voltage will have positive polarity at branch To Bus (J bus).

User Earth Model Data

User Earth Model Data Activity GIC models US and Canada Earth Models.  However, if any other Earth Model is required then use this data to define such an earth model.

A total of up to 50 user earth models are allowed.  Also, each earth model may have up to 25 layers. Use as many records needed to specify the data.  The thickness of the last layer is infinity.  This is specified as any value less than 0.0 (=-999.0 for example). The thickness value less than 0.0 is also used as end of earth model data.

The format for Earth Model Data (v34) is

NAME, BETAFTER, DESC,

RESISTIVITY1, THICKNESS1, RESISTIVITY2, THICKNESS2,…..,

RESISTIVITY24, THICKNESS24, RESISTIVITY25, THICKNESS25

| NAME | NAME may be up to 12 characters. This name should be different than the Standard US and Canada Earth Models. No default allowed. |  |
| --- | --- | --- |
| BETAFTER | Earth Model scaling factor used when calculating branch induced electric field for Benchmark GMD event. BETAFTR=1 by default |  |
| DESC | Description of the earth model. NAME maybe up to 72 characters. This is for information purpose only. DESC = “ by default |  |
| RESISTIVITY1 | Layer 1 Resistivity in ohm-m. No default allowed. |  |
| THICKNESS1 | Layer 1 Thickness in km. No default allowed. |  |
| RESISTIVITYn | Nth Layer Resistivity in ohm-m. No default allowed. Up to 25 layers are allowed. |  |
| THICKNESSn | Nth Layer Thickness in km. No default allowed. Up to 25 layers are allowed. |  |

The thickness of the last layer is infinity.  This is specified as any value less than 0 (= -999.0 for example).

### Modeling Refinements

### Maintenance of GIC System Model  (IMM and RARF)

The input data from REs is submitted to ERCOT through RARF documents which will follow ERCOT processes and be converted to NOMCR and stored and maintained in NMMS (IMM). The input data from TSPs is submitted to the ERCOT using PMCR  to be stored in the NMMS (IMM) and will be stored and maintained in IMM of ERCOT. Based on the appropriate SSWG case and the input data from REs and TSPs, ERCOT will develop a new GMD base GMD casescases which consists of the SSWG base case and GIC input file. ERCOT will deliver the new GMD base case to all TSPs through emails (PGDTF email list), and post the case in MIS of ERCOT (we can discuss if it is necessary). TSPs will review the GMD base case and may submit any modification (in PSSE *.idv file) to ERCOT if necessary. ERCOT is in charge of maintenance of GMD base cases and GIC input files, and will deliver the change files (*.idv) to all TSPs through email and MIS.

### GIC Data for Existing Equipment

For existing equipment that has been modeled in SSWG cases, TSPs and REs can submit or update the GIC parameters through IMM and RARF documents, respectively.

### GIC Data for Planned Equipment (may not need) ? No place in MOD for Transmission Co. owned equipment, Pre-RARF for RE owned equipment

For the planned equipment that has not been modeled in SSWG cases, REs can submit the GIC parameters through pre-RARF documents. However, TSPs may have to submit the GIC parameters through emails since no place in IMM (MOD) can accommodate the GIC parameters.

# Comments

Oncor added this section.

CNP has concerns with the procedure outlined for updating and maintaining the GIC data file. Rather than utilizing NMMS, a simpler approach would be for TSPs to submit/maintain their own GIC data files (similar to DWG’s procedure for maintaining dynamic data).  We could still utilize NMMS naming convention for substation names and numbering, as there is an input for this data in the planning cases in PSSE v34; however, for data that is not included in the planning cases, it does not make sense to submit this data to NMMS.  The purpose of NMMS seeding the planning data was to maintain consistency between the Planning and Operations models, but in this case Operations will not be performing any GIC studies, so no consistency needed.

To populate PSSE GIC Module with initial GIC data, Oncor proposes using Excel spreadsheet or text file process similar to DWG’s process until GIC model building process is more mature.

We would appreciate ERCOT to specify file type preferences for data submittal (.xls, .csv, .pdf…)

Does the TP or TO have the responsibility for supplying the data?  TDSP was also used.  We should be consistent in the term we use.

The GIC model should be similar to the SSWG model with each TP having its own bus range so stations are grouped by TP for ease in reviewing data.

Please, further elaborate on this parameter!

Is RG the substation’s Ground Grid Resistance (GGR)?

AEP believes that the Effective Ground Grid Resistance (EGGR) should be used. We define EGGR as the value that factors in not only the usual substation GGR, but also the contribution of parallel shield wires connected to that substation. Although that value might not be easy to obtain, we think it is the right way to proceed!

What is the source of data contained in the NMM database?

Specifically, how were the RG values for existing substations obtained?

Where is this data in NMMS?

This is automated if the option selected is: Create Excel template for GIC data file. However, the Bus Substation would be renumbered every time a new bus is modeled.  If the option: Create GIC data file from Excel template is selected then the Bus Substation numbers can be controlled.  This preferable from TPs’ perspective.

ERCOT should establish a process to specify which specific SSWG cases members should use for modeling and vulnerability assessment.

R4 of TPL-007 calls for two vulnerability studies conditions (system Off and On Peak load cases, both for “at least one year within the Near-Term Transmission Planning Horizon”).

Will the SSWG publish steady state base cases frequently enough, such as to allow requirement R4 to be met?

What is the intend of this paragraph? If it is here to solely remind us of the two recommended NERC modeling methods of series capacitors, it would be good to know whether ERCOT is okay with either methods.

For all other intend of this paragraph please let us know.

If CORE number is known, does Module select KFACTOR?

It will select a value from the Mvar Loss Scaling Factors dialog box.

- Would ERCOT be interested in knowing what method was used to model blocking devices?

If Yes, we, ERCOT members should have a mean to communicate it.

We worry about how to communicate the status of a branch that contains a blocking device.

How does GIC module of PSS/e handle branch data in GIC computations?

Does the branch data from the GIC module override the powerflow data?

If Yes, then we will model series cap with the “01 MΩ” method and use the branch data format to also communicate the status branches with series capacitor (01 MΩ resistance to signify OFF status).

If No, we need a mean (maybe a sixth field added to the Branch Data format) to indicate the status (ON/OFF) of each line.

What is the input if the USGS model is used?

The GIC base case is a future case, how will planned system changes be incorporated in the model?

Planners are providing this data, and they use PMCR instead of NOMCR.

We would appreciate also the sharing of the “.GIC files”.

Can we submit auxiliary files from PowerWord simulator 18 that AEP uses?

Providing case updates via .idv file will only work to correct GIC module data that is in the base cases.  For other data (DC transformer winding resistance, transformer core type, k factor, etc.), the GIC data file would need to be manually updated.

Per proposed PGRR046 ERCOT together with TSPs will develop the GIC base cases derived from the SSWG near-term base cases, therefore this statement is not relevant.

Is this being pursued by ERCOT?