## Slide 1
PDCWG Report to ROS
Chair: Percy Galliguez, Brazos Electric Power Cooperative, Inc.
Vice Chair: Stewart Rake, Luminant
ROS
May 5th, 2016

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-1 FMEs & IMFR
    No FME’s in the month of March
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 4/13/16
  Regulation & Frequency Control Reports
  GREDP Performance Analysis
  BAL-001-TRE-1 Mitigation Plan Requirements
    Section C 2.1 of Regional Standard
  Assessing Historical Frequency Response Demands & Assessing Reliability Issues, Ongoing Costs, and Concerns
    Mike Potishnak asked for volunteers within PDCWG to participate in a survey.
  Reviewed 2 (non-FME) ERCOT Frequency Disturbance
    3/15/2016 @ 1000
      Loss of 425 MW
      977 MW/0.1HZ Response
    3/22/2016 @ 0929
      Loss of 276 MW
      544 MW/0.1HZ Response
    4/9/2016 @ 0500
      Loss of 234 MW
      498 MW/0.1HZ Response

## Slide 4: Frequency Measurable Events Performance
April & May 2016

## Slide 5: Frequency Measurable Events
There were 3 FMEs during the month of April.
  4/17/2016 23:30:44
    Loss of 663 MW
    Interconnection Frequency Response: 872 MW/0.1 Hz
    6 of 41 Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    5 of 41 Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  4/23/2016 1:54:22
    Loss of 402 MW
    Interconnection Frequency Response: 687 MW/0.1 Hz
    7 of 44 Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    7 of 44 Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Frequency Measurable Events
  4/30/2016 1:16:20
    Loss of 432 MW
    Interconnection Frequency Response: 584 MW/0.1 Hz
    4 of 39 Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    3 of 39 Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
There has been 1 FME so far in May.
  5/1/2016 12:32:30
    Loss of 562 MW
    Interconnection Frequency Response: 906 MW/0.1 Hz
    5 of 48 Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    4 of 48 Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: Interconnection Minimum Frequency Response (IMFR) Performance

## Slide 8: Frequency Control Report
January 2016

## Slide 9: CPS1 Performance
CPS1 12 Month Rolling Average = 175.57%

## Slide 10: RMS1 Performance of ERCOT Frequency

## Slide 11: Frequency Profile Analysis

## Slide 12: Time Error Corrections
There was noTime Error Corrections (TEC) in April.

## Slide 13: Wind Generation Performance

## Slide 14: Wind Generation Performance

## Slide 15: Wind Generation Performance

## Slide 16
Questions?