## Slide 1: Generation Deliverability
ROS
May 5, 2016

## Slide 2: How we got here
Jan. 2014: ROS requested PLWG consider transmission planning as it relates to constrained generation, system-wide, and any impacts to reliability
June 2014: ERCOT hosted Generation Deliverability Workshop to discuss tool development
July 2014: ROS directs the PLWG to develop language to include criteria to address generation deliverability in peak Load conditions
First half of 2014: PLWG discusses constrained generation during several monthly meetings
Sept. 2014: PLWG discusses need to revise economic criteria to address generation deliverability
Nov. 2015: PLWG discusses potential need to change PUCT Rules to accommodate previously discussed criteria changes and lack of evidence of existing problem
Focus on economics
Scope narrowed to peak Load
Worth pursuing now?

## Slide 3: Two conceptual economic planning criteria additions
Consider reduced generation investment needs due to relieving transmission bottlenecks that constrain generation at peak [may need PUCT rules changes]
  In addition to the production cost savings of a project
  Need to develop a metric such as the Cost Of New Entry as the appropriate societal cost benefit
  May need to discount for plants closer to retirement
Consider probability-weighted production cost savings for different load profiles [could be implemented without PUCT rules changes]
  In the Brattle Group’s 2013 review of the ERCOT LTSA and economic planning processes they noted that “SPP’s Metrics Task Force recently suggested that SPP’s production simulations should be developed and tested for load profiles that represent 90/10 and 10/90 peak load conditions— rather than just for base case simulations (reflecting 50/50 peak load conditions)...”

## Slide 4: Is there an existing problem?
ERCOT developed tool to find generation deliverability problems in a powerflow case
Tool ran on EC, WFW, NNC, and SSC 2015 cases from the 2014 RTP
Tool identified 25 unique transmission constraints that could lead to generation deliverability problems
Of those 25 Unique Transmission constraints:
  15 did not have any real-time congestion in 2015
  10 had real-time congestion in 2015
The table on the next slide shows the constraints

## Slide 5: Congestion in 2015
Transmission identified as causing generation getaway constraint | 2015 Congestion Rank | 2015 Congestion Rent
DUPONT SWITCHING STATION TO DUPONT PP-1 (INGLESIDE) CKT 1 [138.00 - 138.00 kV] | NA | NA
DILLEY SWITCH AEP TO COTULLA SUB CKT 1 [ 69.00 - 69.00 kV] | 121 | $405,578.50
PALODURO SUB TO PEARSALL SWITCHING STATION CKT 1 [138.00 - 138.00 kV] | 489 | $186.80
PEARSALL SWITCHING STATION TO PRSALGSU CKT 1 [138.00 - 138.00 kV] | NA | NA
Transformer ALLEN SWITCH TO ALLENSTR CKT 1 [345.00 - 138.00 kV] | NA | NA
ELKTON TO ATHENS CKT 1 [138.00 - 138.00 kV] | NA | NA
ELKTON TO TYLER WEST CKT 1 [138.00 - 138.00 kV] | 95 | $547,907.59
STRYKER CREEK SES TO TROUP CKT 1 [138.00 - 138.00 kV] | 601 | 0
TROUP TO WALNUT GROVE CKT 1 [138.00 - 138.00 kV] | NA | NA
TYLER GRANDE TO WHITEHOUSE CKT 1 [138.00 - 138.00 kV] | NA | NA
WALNUT GROVE TO WHITEHOUSE CKT 1 [138.00 - 138.00 kV] | NA | NA
IRVING HUNTER FERRELL TAP 2 TO TRINITY RIVER AUTHORITY CKT 1 [138.00 - 138.00 kV] | NA | NA
MOUNTAIN CREEK SES TO TRINITY RIVER AUTHORITY CKT 1 [138.00 - 138.00 kV] | 364 | $9,695.47
MATHIS TO EDROY CKT 1 [ 69.00 - 69.00 kV] | 369 | $9,276.77
NUECES BAY TO LON HILL CKT 1 [138.00 - 138.00 kV] | NA | NA
HOLLY TO RODD FIELD CKT 1 [138.00 - 138.00 kV] | 137 | $328,853.57
WESTSIDE AEP TO CABANISS CKT 1 [138.00 - 138.00 kV] | NA | NA
BRINE TO LANGSTON CKT 86 [138.00 - 138.00 kV] | 165 | $230,392.92
BOSQUE SWITCH TO OLSEN SWITCHING STATION CKT 1 [138.00 - 138.00 kV] | 104 | $499,648.18
BARNEY DAVIS TO RODD FIELD CKT 1 [138.00 - 138.00 kV] | NA | NA
AIRLINE AEP TO CABANISS CKT 1 [138.00 - 138.00 kV] | 441 | $1,753.26
BARNEY DAVIS TO WOOLDRIDGE CKT 1 [138.00 - 138.00 kV] | NA | NA
MONTICELLO MINING TO MONTICELLO TAP CKT 1 [138.00 - 138.00 kV] | NA | NA
Transformer OLSEN SWITCHING STATION TO OLSEN SWITCHING STATION CKT 1 [ 69.00 - 138.00 kV] | NA | NA
MONTICELLO MINING TO MONTICELLO SES CKT 1 [138.00 - 138.00 kV] | NA | NA

## Slide 6: Conclusions after two years of work
Generation getaway issues could be more appropriately accounted for with a change in the economic planning criteria
However, this change will require Protocol, Planning Guide and likely PUCT rules changes
At this time there is not a significant generation getaway issue in ERCOT so it may not be worth pursuing
In the future this could change

## Slide 7: Options for ROS
Review generation resources that are limited by transmission (resulting from similar efforts ongoing with Panhandle CREZ)
PLWG Request to ROS:
  Consider this assignment complete.
  Clarify Scope Needing completion before returning issue to ROS.