| NPRR Number | 667 | NPRR Title | Ancillary Service Redesign |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Tabled |
| Date of Decision |  | April 14, 2016 |  |  |
| Proposed Effective Date |  | To be determined |  |  |
| Priority and Rank Assigned |  | To be determined |  |  |
| Nodal Protocol Sections Requiring Revision |  | 2.1, Definitions 2.2, Acronyms and Abbreviations 3.2.5, Publication of Resource and Load Information 3.2.6.2.1, Peak Load Estimate 3.6.1, Load Resource Participation 3.8.3, Quick Start Generation Resources 3.8.4, Hydro Generation Resources 3.9.1, Current Operating Plan (COP) Criteria 3.16, Standards for Determining Ancillary Service Quantities 3.17.1, Regulation Service 3.17.1, Fast Frequency Response Service (FFRS) (new) 3.17.2, Primary Frequency Response Service (PFRS) (new) 3.17.2, Responsive Reserve Service (deleted) 3.17.3, Contingency Reserve Service (CRS) (new) 3.17.3, Non-Spinning Reserve Service (deleted) 3.17.4, Supplemental Reserve Service (SRS) (new) 3.18, Resource Limits in Providing Ancillary Service 4.2.1.1, Ancillary Service Plan 4.4.7.1, Self-Arranged Ancillary Service Quantities 4.4.7.1.1, Negative Self-Arranged Ancillary Service Quantities 4.4.7.2, Ancillary Service Offers 4.4.7.2.1, Ancillary Service Offer Criteria 4.4.7.3, Ancillary Service Trades 4.4.7.3.1, Ancillary Service Trade Criteria 4.4.9.1, Three-Part Supply Offers 4.5.1, DAM Clearing Process 4.5.2, Ancillary Service Insufficiency 4.6.2.3.1, Day-Ahead Make-Whole Payment 4.6.4.1.1, Regulation Up Service (Reg-Up) Payment 4.6.4.1.2, Regulation Down Service (Reg-Down) Payment 4.6.4.1.3, Primary Frequency Response Service (PFRS) Payment (new) 4.6.4.1.3, Responsive Reserve Service Payment (deleted) 4.6.4.1.4, Fast Frequency Response Service (FFRS) Payment (new) 4.6.4.1.4, Non-Spinning Reserve Service Payment (deleted) 4.6.4.1.5, Contingency Reserve Service (CRS) Payment (new) 4.6.4.1.6, Supplemental Reserve Service (SRS) Payment (new) 4.6.4.2.1, Regulation Up Service (Reg-Up) Charge 4.6.4.2.2, Regulation Down Service (Reg-Down) Charge 4.6.4.2.3, Primary Frequency Response Service (PFRS) Charge (new) 4.6.4.2.3, Responsive Reserve Service Charge (deleted) 4.6.4.2.4, Fast Frequency Response Service (FFRS) Charge (new) 4.6.4.2.4, Non-Spinning Reserve Service Charge (deleted) 4.6.4.2.5, Contingency Reserve Service (CRS) Charge (new) 4.6.4.2.6, Supplemental Reserve Service (SRS) Charge (new) 6.1, Introduction 6.4.4.2, Energy Offer Curve for On-Line Non-Spinning (deleted) 6.4.9.2, Supplemental Ancillary Services Market 6.5.1.2, Centralized Dispatch 6.5.5.2, Operational Data Requirements 6.5.7.1.10, Network Security Analysis Processor and Security Violation Alarm 6.5.7.2, Resource Limit Calculator 6.5.7.5, Ancillary Services Capacity Monitor 6.5.7.6, Load Frequency Control 6.5.7.6.1, LFC Process Description 6.5.7.6.2, LFC Deployment (deleted) 6.5.7.6.2.1, Deployment of Regulation Service (deleted) 6.5.7.6.2.2, Deployment of Responsive Reserve Service (deleted) 6.5.7.6.2.3, Non-Spinning Reserve Service Deployment (deleted) 6.5.7.7, Ancillary Services Deployment and Recall (new) 6.5.7.7.1, Deployment and Recall of Regulation Service (new) 6.5.7.7.2, Deployment and Recall of Fast Frequency Response Service (new) 6.5.7.7.3, Deployment and Recall of Primary Frequency Response Service (new) 6.5.7.7.4, Deployment and Recall of Contingency Reserve Service (new) 6.5.7.7.5, Supplemental Reserve Service Deployment and Recall (new) 6.5.9.3.3, Watch 6.5.9.4, Energy Emergency Alert 6.5.9.4.1, General Procedures Prior to EEA Operations 6.5.9.4.2, EEA Levels 6.5.9.4.3, Restoration of Market Operations 6.6.5.1.1, General Generation Resource and Controllable Load Resource Base Point Deviation Charge 6.7.1, Payments for Ancillary Service Capacity Sold in a Supplemental Ancillary Service Market 6.7.2, Charges for Ancillary Service Capacity Replaced Due to Failure to Provide 6.7.3, Adjustments to Cost Allocations for Ancillary Services Procurement 6.7.4, Real-Time Ancillary Service Imbalance Payment or Charge 8.1, QSE and Resource Performance Monitoring 8.1.1.1, Ancillary Service and Reserves Qualification and Testing 8.1.1.2, General Capacity Testing Requirements 8.1.1.2.1, Ancillary Service Technical Requirements and Qualification Criteria and Test Methods 8.1.1.2.1.1, Regulation Service Qualification 8.1.1.2.1.2, Fast Frequency Response Service Qualification (new) 8.1.1.2.1.2, Responsive Reserve Service Qualification (deleted) 8.1.1.2.1.3, Primary Frequency Response Service Qualification (new) 8.1.1.2.1.3, Non-Spinning Reserve Qualification (deleted) 8.1.1.2.1.4, Contingency Reserve Service Qualification (new) 8.1.1.2.1.5, Supplemental Reserve Service Qualification (new) 8.1.1.2.1.7, OFF30 Reserve Qualification 8.1.1.3.2, Fast Frequency Response Service Capacity Monitoring Criteria (new) 8.1.1.3.2, Responsive Reserve Service Capacity Monitoring Criteria (deleted) 8.1.1.3.3, Primary Frequency Response Service Capacity Monitoring Criteria (new) 8.1.1.3.3, Non-Spinning Reserve Capacity Monitoring Criteria (deleted) 8.1.1.3.4, Contingency Reserve Service Capacity Monitoring Criteria (new) 8.1.1.3.5, Supplemental Reserve Service Capacity Monitoring Criteria (new) 8.1.1.4.1, Regulation Service and Generation Resource/Controllable Load Resource Energy Deployment Performance 8.1.1.4.2, Fast Frequency Response Service Energy Deployment Criteria (new) 8.1.1.4.2, Responsive Reserve Service Energy Deployment Criteria (deleted) 8.1.1.4.3, Primary Frequency Response Service Energy Deployment Criteria (new) 8.1.1.4.3, Non-Spinning Reserve Service Energy Deployment Criteria (deleted) 8.1.1.4.4, Contingency Reserve Service Energy Deployment Criteria (new) 8.1.1.4.5, Supplemental Reserve Service Energy Deployment Criteria (new) 8.5.1.1, Governor in Service 9.2.3, DAM Settlement Charge Types 9.5.3, Real-Time Market Settlement Charge Types |  |  |
| Other Binding Documents Requiring Revision or Related Revision Requests |  | - Methodologies for Determining Ancillary Service Requirements - Nodal Non-Spinning Reserve Service Deployment Procedures - Manual Deployment and Recall of RRS During Scarcity Conditions - Operating Procedures - Telemetry Standards - Methodology for Implementing Operating Reserve Demand Curve (ORDC) to Calculate Real-Time Reserve Price Adder - Setting the Shadow Price Caps and Power Balance Penalties in Security Constrained Economic Dispatch - Requirements for Aggregate Load Resource Participation in the ERCOT Markets - Nodal Operating Guides - Verifiable Cost Manual |  |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) improves Regulation-Up Service (Reg-Up) and Regulation-Down Service (Reg-Down); and replaces Non-Spinning Reserve (Non-Spin) and Responsive Reserve (RRS) Ancillary Services with a combination of four new Ancillary Services: Fast Frequency Response Service (FFRS), Primary Frequency Response Service (PFRS), Contingency Reserve Service (CRS), and Supplemental Reserve Service (SRS). |  |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) This NPRR proposes a redesign of the suite of Ancillary Services to ensure that the ERCOT Independent System Operator (ISO) continues to maintain grid reliability as the ERCOT System and Resource mix continue to evolve. It is the result of a series of weekly work sessions and workshops beginning in late 2013, additional work sessions with the ERCOT Technical Advisory Committee (TAC), and a stakeholder comment submission process based on the initial NPRR draft which was developed in June, 2014. It is also the result of numerous engineering studies performed by ERCOT Staff in anticipation of changes to the ERCOT System and regulatory requirements. Implicit in ERCOT’s analysis is the fact that ERCOT is a stand-alone interconnection, with a higher risk of significant frequency deviations than other ISOs. ERCOT has been successful in complying with North American Electric Reliability Corporation (NERC) Reliability Standards with its current suite of Ancillary Services. ERCOT’s average monthly Control Performance Standard (NERC CPS1) scores have consistently been well within NERC standards, and other performance measures reflect that the current ERCOT Ancillary Service construct has served ERCOT well from a reliability and secure operations perspective. However, the current Ancillary Service framework that was forklifted from the market design developed in the late 1990s does not adequately address ongoing changes to the ERCOT System nor anticipate other changes likely to occur in the future. These changes include, but are not limited to, increasing penetration of Distributed Generation (DG) and utility-scale intermittent renewable generation, fast-acting storage devices, and smart grid products that enable more sophisticated Load management and Demand response. Moreover, today’s generation mix in ERCOT is different from the mix that existed 15 years ago, and the current Ancillary Service suite is based on the inherent characteristics of the steam units that dominated that period. In particular, several distinct operational requirements are currently bundled into a single service, RRS. This creates an awkward fit for the capabilities of some existing Resources and new technologies which could otherwise provide valuable services. The scope of this NPRR is limited to operations related to frequency control — as currently addressed by Reg-Up, Reg-Down, RRS and Non-Spin. It does not contemplate any changes to Emergency Response Service (ERS), Voltage Support Service (VSS), Reliability Must-Run (RMR) units, or Black Start Services (BSS). This NPRR proposes the following future Ancillary Service framework and evolution from the current framework: - Reg-Up and Reg-Down, including the subset of Fast-Responding Regulation-Up and Regulation-Down Services (FRRS), remain largely unchanged, with the exception of incorporation of an equivalency ratio. - FFRS, PFRS, and CRS replace the current RRS. Both FFRS and CRS are designed with sub-groups. FFRS1 would be responding at a higher frequency set-point with limited deployment duration; FFRS2 would be provided at a lower frequency threshold with longer deployment duration. An equivalency ratio will be established between the FFRS and PFRS to ensure a reliable mix of these Ancillary Services is procured based on anticipated ERCOT System conditions. CRS1 Resources would be released to and Dispatched by Security-Constrained Economic Dispatch (SCED), while CRS2 Resources would be manually Dispatched (i.e., “blocky”). - SRS replaces the current Non-Spin, and would also consist of sub-groups for SCED-Dispatched Resources (SRS1) and manually Dispatched Resources (SRS2). After extensive dialogue with Market Participants, especially including the Load Serving Entities (LSEs) who carry and must pay for their Ancillary Service responsibilities, ERCOT agreed to an “adjustment period” to allow LSEs to adapt forward contracts and adequately hedge their future obligations. Accordingly, ERCOT proposes an implementation date for this NPRR at a date three years from the date of NPRR approval by the ERCOT Board. Finally, ERCOT notes that additional work will continue on the development of Synchronous Inertial Response Service (SIRS). A need has been identified for SIRS to be incorporated into the Ancillary Service framework at some point in the future; however, more detailed stakeholder discussions and product development will be needed. |  |  |
| Credit Work Group Review |  | To be determined |  |  |
| Procedural History |  | - On 11/18/14, NPRR667 and an Impact Analysis were posted. - On 12/11/14, PRS considered NPRR667. - On 1/21/15, ERCOT Steel Mill comments were posted. - On 1/21/15, Invenergy comments were posted. - On 1/22/15, TIEC comments were posted. - On 1/22/15, Luminant comments were posted. - On 1/23/15, DR Provider comments were posted. - On 1/23/15, Apex comments were posted. - On 2/3/15, CPS Energy comments were posted. - On 2/10/15, Citigroup comments were posted. - On 12/21/15, a Cost Benefit Analysis was posted. - On 12/22/15, ERCOT comments were posted. - On 1/25/16, SENA comments were posted. - On 1/25/16, Reliant comments were posted. - On 1/25/16, GDF Suez comments were posted. - On 1/25/16, Freeport LNG comments were posted. - On 1/25/16, Sierra Club comments were posted. - On 1/25/16, a second set of CPS Energy comments were posted. - On 1/25/16, ESA comments were posted. - On 1/25/16, Calpine comments were posted. - On 1/25/16, a second set of TIEC comments were posted. - On 1/25/16, “Co-ops” comments were posted. - On 1/25/16, a second set of Apex comments were posted. - On 1/25/16, Direct Energy comments were posted. - On 1/26/16, RES comments were posted. - On 3/3/16, a second set of ERCOT comments were posted. - On 3/4/16, a third and fourth set of ERCOT comments were posted. - On 3/7/16, Wind Coalition comments were posted. - On 4/5/16, a fifth set of ERCOT comments were posted. - On 4/12/16, a sixth set of ERCOT comments were posted. - On 4/14/16, PRS again considered NPRR667. |  |  |
| PRS Decision |  | On 12/11/14, PRS unanimously voted to table NPRR667. All Market Segments were present for the vote. On 4/14/16, PRS voted via roll call vote to table NPRR667 for one month. There were ten opposing votes from the Cooperative (4), Municipal (3), Independent Power Marketer (IPM) (2), and Independent Generator Market Segment. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 12/11/14, there was no discussion. On 4/14/16, participants discussed concerns with the reliability needs and project costs associated with a large scale redesign of the Ancillary Service market. Some participants posited that smaller adjustments to the existing Ancillary Service market could achieve several of the benefits of NPRR667 with minimal impacts to Qualified Scheduling Entity (QSE) systems. ERCOT reasserted its position that NPRR667 is the best method to improve the Ancillary Service framework in the ERCOT Region, and requested tabling of NPRR667 for an additional month for internal discussions. Some participants supported the rejection of NPRR667 and proposed to move forward with a new NPRR incorporating certain aspects of NPRR667 as well as NPRR756, Enhanced Ancillary Services. |  |  |

| Business Case |  |
| --- | --- |
| Qualitative Benefits | - Improves toolset to stabilize and maintain system frequency by providing more efficient ways to procure and deploy Ancillary Services. - More appropriately recognizes and compensates Resources providing Ancillary Services - Enables ERCOT to more efficiently meet upcoming changes to regulatory reliability standards - Better recognizes and leverages the capabilities of existing Resources and new technologies. - Positions ERCOT to more efficiently manage future changes to the ERCOT System and better aligns Resources’ capabilities with the Ancillary Services through performance-driven qualification. - Enables a more flexible procurement methodology which better aligns Ancillary Service requirements with system conditions. - Supports multiple market goals, including: - Pursues the appropriate incorporation of Load participation - Pursues the appropriate incorporation of emerging technologies - Collaborate with ERCOT on the review of Ancillary Service needs and implement changes as necessary. - Many of the drivers for this NPRR are likely to cause future market rules and system changes in a piecemeal fashion over the next several years if the current NPRR is not implemented. - This NPRR provides a roadmap for both ERCOT and the Market Participants to refer to and follow in order to transition to a better set of Ancillary Services and better procurement approach in a comprehensive and coordinated manner. Absent this NPRR, there is the possibility for less effective, “reactive” NPRRs to be developed and implemented, leaving little advance notice for the market. - While the exact number and scope of any such piecemeal future revisions is unknown, it is reasonable to expect that the cost to implement the revisions to the Ancillary Service framework proposed in this NPRR in a comprehensive manner will be lower than the cumulative cost of implementing each change individually. |
| Quantitative Benefits | A Cost Benefit Analysis of this NPRR is planned to be completed by a 3rd party vendor by late spring of 2015. |
| Impact to Market Segments | - Procures Ancillary Services more efficiently, relative to existing approach. - Better leverages the capabilities of existing resources and new technologies. - Creates new opportunities for participation by existing and new Resources. |
| Credit Implications | - To be determined. |
| Other |  |

| Sponsor |  |
| --- | --- |
| Name | Dan Woodfin / Joel Mickey |
| E-mail Address | Dan.Woodfin@ercot.com / Joel.Mickey@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-3115 (Dan) / 512-248-3925 (Joel) |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Cory Phillips |
| E-Mail Address | cory.phillips@ercot.com |
| Phone Number | 512-248-6464 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT Steel Mills 012115 | Proposed revisions to the qualification, monitoring, and deployment of CRS and SRS to utilize peaks rather than averages |
| Invenergy 012115 | Noted the lack of a “FFRS Down” product to manage over-frequency events |
| TIEC 012215 | Expressed concerns with the stated reliability need for NPRR667, the cost-benefit proposition, and the financial impacts of the equivalency ratios between PFR and FFR |
| Luminant 012215 | Proposed numerous revisions to NPRR667 pertaining to Quick Start Generation Resources (QSGRs) |
| DR Providers 012315 | Proposed revisions to telemetry and FFRS language |
| Apex 012315 | Expressed concerns with the lack of a “pay for performance” methodology and with the duration limits and restoration performance within NPRR667 |
| CPS Energy 020315 | Proposed eliminating the SRS product |
| Citigroup 021015 | Requested tabling of NPRR667 for concurrent consideration with other large scale projects |
| ERCOT 122215 | Incorporated the results of market workshops, including some modifications suggested by Market Participants that are acceptable to ERCOT as well as certain refinements and clarifications that ERCOT identified |
| SENA 012516 | Proposed postponing NPRR667 indefinitely |
| Reliant 012516 | Expressed doubts that full implementation of NPRR667 is necessary or in stakeholders’ economic interests |
| GDF Suez 012516 | Requested an evaluation of how much of the benefits of NPRR667 could be achieved by incremental changes to the current Ancillary Service market |
| Freeport LNG 012516 | Proposed an alternative, potentially lower cost approach as an alternative to NPRR667 |
| Sierra Club 012516 | Expressed general support for NPRR667 and suggested additional discussion points for stakeholders (ex: inertia) |
| CPS Energy 012516 | Proposed eliminating the SRS product |
| ESA 012516 | Expressed support for a full implementation of NPRR667 |
| Calpine 012516 | Proposed revisions and posed questions/comments for the 2/1/16 NPRR667 workshop |
| TIEC 012516 | Expressed concerns with the results of the CBA analysis, questioned the reliability need for NPRR667, and noted that if NPRR667 is pursued, there should not be separate clearing prices for load and generation |
| Co-ops 012516 | Noted concerns with the costs and assumptions within the CBA, posited that a full implementation of NPRR667 is no longer warranted, and listed a few concerns with the design of NPRR667 |
| Apex 012516 | Proposed increasing the duration of FFRS1 from 10 to 45 minutes and eliminating FRRS as a product |
| Direct Energy 012516 | Expressed support for NPRR667 and the commitment to implement the new Ancillary Services no sooner than three years after ERCOT Board approval |
| RES 012616 | Expressed support for NPRR667 |
| ERCOT 030316 | Proposed language implementing a floor for CRS1 and removing “Hydro” as a qualifier on Resrouces operating in synchronous condenser mode providing PFR |
| ERCOT 030416 | Responded to all submitted comments from January 2016 (except Calpine) |
| ERCOT 030416 | Responded to 1/25/16 Capline comments |
| Wind Coalition 030716 | Noted the Ancillary Service redesign should be as comprehensive as possible (focusing on providing response within the first second), and noted concerns with the CBA assumptions relating to inertia |
| ERCOT 040516 | Proposed changes to the Physical Responsive Capability (PRC) calculation |
| ERCOT 041216 | Requested tabling of NPRR667 for one month |

Market Rules Comments

Please note the baseline below reflects the initial proposed language changes, but as PRS has not yet recommend approval of any version of the revision language, it does not yet reflect the incorporation of any of the filed comments on NPRR667.  Similarly, it does not reflect baseline updates to Protocol language since the initial filing of NPRR667 in November 2014.

Proposed Protocol Language Revision

## 2.1	DEFINITIONS

Contingency Reserve Service (CRS)

An Ancillary Service provided by Generation Resources capable of ramping to a specified output level within ten minutes and Load Resources capable of providing Demand response within ten minutes.

CRS may be provided by two CRS sub-groups:

- Sub-group CRS1 includes Resources that are capable of responding to SCED Base Point Dispatch Instructions.

- Sub-group CRS2 includes Resources that are not SCED Dispatchable.

- Emergency Ramp Rate

The maximum rate of change (up and down) in MW per minute of a Resource that is provided to ERCOT in up to ten segments, each represented by a single MW per minute value (across the capacity of the Resource), which describes the available rate of change for the given range (between High Sustained Limit (HSL) and Low Sustained Limit (LSL)) of the generation or consumption of a Resource.  In Real-Time SCED Dispatch, the up and down Emergency Ramp Rates are telemetered by the QSE to ERCOT and represent the total capacity (in MW) that the Resource can change from its current actual generation or consumption within the next five minutes divided by five.

- Fast Frequency Response Service (FFRS)

- An Ancillary Service provided by Resources capable of automatically self-deploying and providing their full Ancillary Service Resource Responsibility within 30 cycles after frequency meets or drops below a preset threshold.

- FFRS may be provided by two FFRS sub-groups:

- Sub-group FFRS1 includes Resources capable of sustaining a full response for at least ten minutes and, once recalled, restoring their full FFRS Ancillary Service Resource Responsibility within 15 minutes.

- Sub-group FFRS2 includes Resources capable of sustaining a full response until receiving an ERCOT recall instruction or until the Resource’s FFRS Ancillary Service Resource Responsibility expires, whichever occurs first, and, once recalled, restoring their full FFRS Ancillary Service Resource Responsibility within 180 minutes.

- Load Frequency Control (LFC)

The deployment of those Resources that are providing Regulation Service to ensure that system frequency is maintained within predetermined limits and the deployment of those Resources that are providing Contingency Reserve Service (CRS) when necessary as backup regulation.  LFC does not include the deployment of Contingency Reserve Service Provided by Sub-group 2 Resources (CRS2) or Supplemental Reserve Service Provided by Sub-group 2 Resources (SRS2).

Primary Frequency Response (PFR)

The immediate proportional increase or decrease in real power output provided by a Resource and the natural real power dampening response provided by Load in response to system frequency deviations.  This response is in the direction that stabilizes frequency.

- Primary Frequency Response Service (PFRS)

An Ancillary Service provided by Resources with capacity reserved for Primary Frequency Response (PFR).

- Regulation Service

- Regulation Down Service (Reg-Down)

An Ancillary Service that provides capacity that can respond to signals from ERCOT within five seconds.  The Reg-Down Ancillary Service Resource Responsibility is the capacity available below any Base Point but above the LSL of a Generation Resource and may be called on to change output as necessary throughout the range of capacity available to maintain proper system frequency.  A Load Resource providing Reg-Down must be able to increase and decrease Load as deployed within its Ancillary Service Schedule for Reg-Down below the Load Resource’s MPC limit.

Regulation Up Service (Reg-Up)

An Ancillary Service that provides capacity that can respond to signals from ERCOT within five seconds.  The Reg-Up Ancillary Service Resource Responsibility is the capacity available above any Base Point but below the HSL of a Generation Resource and may be called on to change output as necessary throughout the range of capacity available to maintain proper system frequency.  A Load Resource providing Reg-Up must be able to increase and decrease Load as deployed within its Ancillary Service Schedule for Reg-Up above the Load Resource’s LPC limit.

- Supplemental Reserve Service (SRS)

- An Ancillary Service provided by Generation Resources capable of ramping to a specified output level within 30 minutes and Load Resources capable of providing Demand response within 30 minutes.

SRS may be provided by two SRS sub-groups:

- Sub-group SRS1 includes Resources that are capable of responding to SCED Base Point Dispatch Instructions.

- Sub-group SRS2 includes Resources that are not SCED Dispatchable.

- Value of Lost Load (VOLL)

A parameter approved by the ERCOT Board for implementing the Operating Reserve Demand Curve (ORDC).

## 2.2	ACRONYMS AND ABBREVIATIONS

CRS	Contingency Reserve Service

CRS1	Contingency Reserve Service Provided by Sub-group 1 Resources

CRS2	Contingency Reserve Service Provided by Sub-group 2 Resources

FFRS	Fast Frequency Response Service

FFRS1	Fast Frequency Response Service Provided by Sub-group 1 Resources

FFRS2	Fast Frequency Response Service Provided by Sub-group 2 Resources

PFR	Primary Frequency Response

PFRS	Primary Frequency Response Service

Reg-Down	Regulation Down Service

Reg-Up	Regulation Up Service

SRS	Supplemental Reserve Service

SRS1	Supplemental Reserve Service Provided by Sub-group 1 Resources

SRS2	Supplemental Reserve Service Provided by Sub-group 2 Resources

VOLL	Value of Lost Load

- 3.2.5	Publication of Resource and Load Information

(1)	Two days after the applicable Operating Day, ERCOT shall post on the MIS Public Area for the ERCOT System and, if applicable, for each Disclosure Area, the information derived from the first complete execution of SCED in each 15-minute Settlement Interval.  The Disclosure Area is the 2003 ERCOT Congestion Management Zones.  Posting requirements will be applicable to Generation Resources and Controllable Load Resources physically located in the defined Disclosure Area.  The information posted by ERCOT shall include:

(a)	An aggregate energy supply curve based on non-wind Generation Resources with Energy Offer Curves that are available to SCED.  The energy supply curves will be calculated beginning at the sum of the Low Sustained Limits (LSLs) and ending at the sum of the HSLs for non-wind Generation Resources with Energy Offer Curves, with the dispatch for each Generation Resource constrained between the Generation Resource’s LSL and HSL.  The result will represent the ERCOT System energy supply curve economic dispatch of the non-wind Generation Resources with Energy Offer Curves at various pricing points, not taking into consideration any physical limitations of the ERCOT System;

[NPRR588: Replace paragraph (a) above with the following upon system implementation:] (a) An aggregate energy supply curve based on non-IRR Generation Resources with Energy Offer Curves that are available to SCED. The energy supply curves will be calculated beginning at the sum of the Low Sustained Limits (LSLs) and ending at the sum of the HSLs for non-wind Generation Resources with Energy Offer Curves, with the dispatch for each Generation Resource constrained between the Generation Resource’s LSL and HSL. The result will represent the ERCOT System energy supply curve economic dispatch of the non-IRR Generation Resources with Energy Offer Curves at various pricing points, not taking into consideration any physical limitations of the ERCOT System;

(b)	An aggregate energy supply curve based on Wind-powered Generation Resources (WGRs) with Energy Offer Curves that are available to SCED.  The energy supply curves will be calculated beginning at the sum of the LSLs and ending at the sum of the HSLs for WGRs with Energy Offer Curves, with the dispatch for each WGR constrained between the WGR’s LSL and HSL.  The result will represent the ERCOT System energy supply curve economic dispatch of the WGRs with Energy Offer Curves at various pricing points, not taking into consideration any physical limitations of the ERCOT System;

[NPRR588: Insert paragraph (c) below upon system implementation and renumber accordingly:] (c) An aggregate energy supply curve based on PhotoVoltaic Generation Resources (PVGRs) with Energy Offer Curves that are available to SCED. The energy supply curves will be calculated beginning at the sum of the LSLs and ending at the sum of the HSLs for PVGRs with Energy Offer Curves, with the dispatch for each PVGR constrained between the PVGR’s LSL and HSL. The result will represent the ERCOT System energy supply curve economic dispatch of the PVGRs with Energy Offer Curves at various pricing points, not taking into consideration any physical limitations of the ERCOT System;

(c)	The sum of LSLs, sum of Output Schedules, and sum of HSLs for Generation Resources without Energy Offer Curves;

(d)	The sum of the Base Points, High Ancillary Service Limit (HASL) and Low Ancillary Service Limit (LASL) of non-wind Generation Resources with Energy Offer Curves, sum of the Base Points, HASL and LASL of WGRs with Energy Offer Curves, and the sum of the Base Points, HASL and LASL of all remaining Generation Resources dispatched in SCED;

[NPRR588: Replace paragraph (d) above with the following upon system implementation:] (d) The sum of the Base Points, High Ancillary Service Limit (HASL) and Low Ancillary Service Limit (LASL) of non-IRR Generation Resources with Energy Offer Curves, sum of the Base Points, HASL and LASL of WGRs with Energy Offer Curves, sum of the Base Points, HASL and LASL of PVGRs with Energy Offer Curves, and the sum of the Base Points, HASL and LASL of all remaining Generation Resources dispatched in SCED;

(e)	The sum of the telemetered Generation Resource net output used in SCED; and

(f)	An aggregate energy Demand curve based on the Real-Time Market (RTM) Energy Bid curves available to SCED.  The energy Demand curve will be calculated beginning at the sum of the Low Power Consumptions (LPCs) and ending at the sum of the Maximum Power Consumptions (MPCs) for Controllable Load Resources with RTM Energy Bids, with the dispatch for each Controllable Load Resource constrained between the Controllable Load Resource’s LPC and MPC.  The result will represent the ERCOT System Demand response capability available to SCED of the Controllable Load Resources with RTM Energy Bids at various pricing points, not taking into consideration any physical limitations of the ERCOT System.

(2)	Two days after the applicable Operating Day, ERCOT shall post on the MIS Public Area for the ERCOT System the following information derived from the first complete execution of SCED in each 15-minute Settlement Interval:

(a)	Each telemetered Dynamically Scheduled Resource (DSR) Load, and the telemetered DSR net output(s) associated with each DSR Load; and

(b)	The actual ERCOT Load as determined by subtracting the Direct Current Tie (DC Tie) Resource actual telemetry from the sum of the telemetered Generation Resource net output as used in SCED.

(3)	Two days after the applicable Operating Day, ERCOT shall post on the MIS Public Area the following information for the ERCOT System and, if applicable, for each Disclosure Area from the DAM for each hourly Settlement Interval:

(a)	An aggregate energy supply curve based on all energy offers that are available to the DAM, not taking into consideration Resource Startup Offer or Minimum-Energy Offer or any physical limitations of the ERCOT System.  The result will represent the energy supply curve at various pricing points for energy offers available in the DAM;

(b)	Aggregate minimum energy supply curves based on all Minimum-Energy Offers that are available to the DAM;

(c)	An aggregate energy Demand curve based on the DAM Energy Bid curves available to the DAM, not taking into consideration any physical limitations of the ERCOT System;

(d)	The aggregate amount of cleared energy bids and offers including cleared Minimum-Energy Offer quantities;

(e)	The aggregate Ancillary Service Offers (prices and quantities) in the DAM, for each type of Ancillary Service regardless of a Resource’s On-Line or Off-Line status, by sub-group if applicable.  Linked Ancillary Service Offers will be included as non-linked Ancillary Service Offers;

(f)	The aggregate Self-Arranged Ancillary Service Quantity, for each type of service, by hour;

(g)	The aggregate amount of cleared Ancillary Service Offers, by sub-group if applicable; and

(h)	The aggregate Point-to-Point (PTP) Obligation bids (not-to-exceed price and quantities) for the ERCOT System and the aggregate PTP Obligation bids that sink in the Disclosure Area for each Disclosure Area.

(4)	ERCOT shall post on the MIS Public Area the following information for each Resource for each 15-minute Settlement Interval 60 days prior to the current Operating Day:

(a)	The Generation Resource name and the Generation Resource’s Energy Offer Curve (prices and quantities):

(i)	As submitted;

(ii)	As submitted and extended (or truncated) with proxy Energy Offer Curve logic by ERCOT to fit to the operational HSL and LSL values that are available for dispatch by SCED; and

(iii)	As mitigated and extended for use in SCED, including the Incremental and Decremental Energy Offer Curves for DSRs;

(b)	The Generation Resource name and the Generation Resource’s Output Schedule;

(c)	For a DSR, the DSR Load and associated DSR name and DSR net output;

(d)	The Generation Resource name and actual metered Generation Resource net output;

(e)	The self-arranged Ancillary Service by service for each QSE;

(f)	The following Generation Resource data using a single snapshot during the first SCED execution in each Settlement Interval:

(i)	The Generation Resource name;

(ii)	The Generation Resource status;

(iii)	The Generation Resource HSL, LSL, HASL, LASL, High Dispatch Limit (HDL), and Low Dispatch Limit (LDL);

(iv)	The Generation Resource Base Point from SCED;

(v)	The telemetered Generation Resource net output used in SCED;

(vi)	The Ancillary Service Resource Responsibility for each Ancillary Service; and

(vii)	The Generation Resource Startup Cost and minimum energy cost used in the Reliability Unit Commitment (RUC); and

(g)	The following Load Resource data using a single snapshot during the first SCED execution in each Settlement Interval:

(i)	The Load Resource name;

(ii)	The Load Resource status;

(iii)	The Maximum Power Consumption (MPC for a Load Resource);

(iv)	The Low Power Consumption (LPC for a Load Resource);

(v)	The telemetered real power consumption; and

(vi)	The Ancillary Service Resource Responsibility for each Ancillary Service.

(5)	If any Real-Time Locational Marginal Price (LMP) exceeds 50 times the Fuel Index Price (FIP) during any 15-minute Settlement Interval for the applicable Operating Day, ERCOT shall post on the MIS Public Area the portion of any Generation Resource’s as-submitted and as-mitigated and extended Energy Offer Curve that is at or above 50 times the FIP for each 15-minute Settlement Interval seven days after the applicable Operating Day.

(6)	ERCOT shall post on the MIS Public Area the offer price and the name of the Entity submitting the offer for the highest-priced offer selected or Dispatched by SCED two days after the applicable Operating Day.  If multiple Entities submitted the highest-priced offers selected, all Entities shall be identified on the MIS Public Area.

(7)	ERCOT shall post on the MIS Public Area the bid price and the name of the Entity submitting the bid for the highest-priced bid selected or Dispatched by SCED two days after the applicable Operating Day.  If multiple Entities submitted the highest-priced bids selected, all Entities shall be identified on the MIS Public Area.

(8)	ERCOT shall post on the MIS Public Area for each Operating Day the following information for each Resource:

(a)	The Resource name;

(b)	The names of the Entities providing information to ERCOT;

(c)	The names of the Entities controlling each Resource.  ERCOT shall determine whether the Entity is in control of each Resource in accordance with subsection (e) of P.U.C. Subst. R. 25.502, Pricing Safeguards in Markets Operated by the Electric Reliability Council of Texas; and

(d)	Flag for Reliability Must-Run (RMR) Resources.

(9)	ERCOT shall post on the MIS Public Area the following information from the DAM for each hourly Settlement Interval for the applicable Operating Day 60 days prior to the current Operating Day:

(a)	The Generation Resource name and the Generation Resource’s Three-Part Supply Offer (prices and quantities), including Startup Offer and Minimum-Energy Offer, available for the DAM;

(b)	For each Settlement Point, individual DAM Energy-Only Offer Curves available for the DAM and the name of the QSE submitting the offer;

(c)	The Resource name and the Resource’s Ancillary Service Offers available for the DAM;

(d)	For each Settlement Point, individual DAM Energy Bids available for the DAM and the name of the QSE submitting the bid;

(e)	For each Settlement Point, individual PTP Obligation bids available to the DAM that sink at the Settlement Point and the QSE submitting the bid;

(f)	The awards for each Ancillary Service from DAM for each Generation Resource;

(g)	The awards for each Ancillary Service from DAM for each Load Resource;

(h)	The award of each Three-Part Supply Offer from the DAM and the name of the QSE receiving the award;

(i)	For each Settlement Point, the award of each DAM Energy-Only Offer from the DAM and the name of the QSE receiving the award;

(j)	For each Settlement Point, the award of each DAM Energy Bid from the DAM and the name of the QSE receiving the award; and

(k)	For each Settlement Point, the award of each PTP Obligation bid from the DAM that sinks at the Settlement Point, including whether or not the PTP Obligation bid was Linked to an Option, and the QSE submitting the bid.

3.2.6.2.1	Peak Load Estimate

ERCOT shall prepare, at least annually, a forecast of the total peak Load for both summer and winter Peak Load Seasons for the current year and a minimum of ten future years using an econometric forecast, taking into account econometric inputs, weather conditions, demographic data and other variables as deemed appropriate by ERCOT.  The firm Peak Load Season estimate shall be determined by the following equation:

FIRMPKLD s, i	=	TOTPKLD s, i – LRFFRS s, i – LRCRS s, i – LRSRS s, i –ERS s, i – CLR s, i – ENERGYEFF s, i

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| FIRMPKLD s, i | MW | Firm Peak Load Estimate—The Firm Peak Load Estimate for the Peak Load Season s for the year i. |
| TOTPKLD s, i | MW | Total Peak Load Estimate—The Total Peak Load Estimate for the Peak Load Season s for the year i. |
| LRFFRS s, i | MW | Load Resource providing Fast Frequency Response Service (FFRS)—The amount of FFRS a Load Resource is providing for the Peak Load Season s for the year i. |
| LRCRS s, i | MW | Load Resource providing Contingency Reserve Service (CRS) —The estimated amount of CRS that Load Resources are providing for the Peak Load Season s for the year i. |
| LRSRS s, i | MW | Load Resource providing Supplemental Reserve Service (SRS)—The estimated amount of SRS that Load Resources are providing for the Peak Load Season s for the year i. |
| ERS s, i | MW | Emergency Response Service (ERS)—The estimated amount of ERS for the Peak Load Season s for the year i calculated as follows: Year (i); Winter Peak Load; Summer Peak Load. Current Year (i = 1); The simple average of the amount of ERS procured by ERCOT for the current year Standard Contract Term of October 1 to January 31 for the ERS Time Periods covering all or any part of Hour Ending 0600 and Hour Ending 1800.; The amount of ERS procured by ERCOT for the current year Standard Contract Term of June 1 through September 30 for an ERS Time Period covering all or any part of Hour Ending 1800.. Second Year (i = 2); The current year Winter Peak Load ERS amount escalated by the compound annual growth rate of the three Winter Peak Load ERS amounts preceding the current year.; The current year Summer Peak Load ERS amount escalated by the compound annual growth rate of the three Summer Peak Load ERS amounts preceding the current period.. Third Year (i = 3); The second year Winter Peak Load ERS amount escalated by the compound annual growth rate of the three Winter Peak Load ERS amounts preceding the current year.; The second year Summer Peak Load ERS amount escalated by the compound annual growth rate of the three Summer Peak Load ERS amounts preceding the current year.. Years after Third Year (i > 3); Equal to third year amount.; Equal to third year amount.. |
| CLR s, i | MW | Amount of Controllable Load Resource—Estimated amount of Controllable Load Resource that is available for Dispatch by ERCOT during the current year i for the Peak Load Season s not already included in LRFFRS, LRCRS, or LRSRS. This value does not include Wholesale Storage Load (WSL). |
| ENERGYEFF s, i | MW | Amount of Energy Efficiency Programs Procured—Estimated amount of energy efficiency programs procured by Transmission and/or Distribution Service Providers (TDSPs) pursuant to P.U.C. Subst. R. 25.181, Energy Efficiency Goal, for the Peak Load Season s for the year i. ERCOT may also consider any energy efficiency and/or Demand response initiatives reported by Non-Opt-In Entities (NOIEs). |
| i | None | Year. |
| s | None | Peak Load Season. |

- 3.6.1	Load Resource Participation

(1)	A Load Resource may participate by providing:

(a)	Ancillary Service:

(i)	Regulation Up (Reg-Up) Service as a Controllable Load Resource capable of providing Primary Frequency Response (PFR);

(ii)	Regulation Down (Reg-Down) Service as a Controllable Load Resource capable of providing PFR;

(iii)	Primary Frequency Response Service (PFRS) as a Controllable Load Resource qualified for Security-Constrained Economic Dispatch (SCED) and capable of providing PFR;

(iv)	Fast Frequency Response Service (FFRS) as a Load Resource controlled by high-set under-frequency relay or similar trigger mechanisms;

(v)	Contingency Reserve Service Provided by Sub-group 1 Resources  (CRS1) as a Controllable Load Resource qualified for SCED and capable of providing PFR; or Contingency Reserve Service Provided by Sub-group 2 Resources  (CRS2) as a Load Resource other than a Controllable Load Resource; and

(vi)	Supplemental Reserve Service Provided by Sub-group 1 Resources  (SRS1) as a Controllable Load Resource qualified for SCED and capable of providing PFR; or Supplemental Reserve Service Provided by Sub-group 2 Resources (SRS2) as a Load Resource other than a Controllable Load Resource;

(b)	Energy in the form of Demand response from a Controllable Load Resource in Real-Time via SCED;

(c)	Emergency Response Service (ERS) for hours in which the Load Resource does not have an Ancillary Service Resource Responsibility; and

(d)	Voluntary Load response in Real-Time.

(2)	Except for voluntary Load response and ERS, loads participating in any ERCOT market must be registered as a Load Resource and are subject to qualification testing administered by ERCOT.  All ERCOT Settlements resulting from Load Resource participation are made only with the QSE representing the Load Resource.

(3)	The Settlement Point for a Controllable Load Resource with a Real-Time Market (RTM) Energy Bid is its Load Zone Settlement Point.

- 3.8.3	Quick Start Generation Resources

(1)	The QSE for a Quick Start Generation Resource (QSGR) that is available for deployment by SCED and that does not have Ancillary Service Resource Responsibility for Contingency Reserve Service Provided by Sub-group 1 Resources (CRS1) in an Operating Hour shall set the COP Resource Status to ON, and the COP Low Sustained Limit (LSL) and COP HSL values to the expected sustainable LSL and HSL for the QSGR for the hour.  If the QSGR is providing Supplemental Reserve Service Provided by Sub-group 1 Resources (SRS1), then the Ancillary Service Resource Responsibility for SRS1 shall be set to the Resource’s QSE-assigned SRS1 responsibility in the COP.  If the QSGR’s SRS1 responsibility is greater than the difference between HSL and LSL, then the QSGR that is available for deployment by SCED shall set the COP LSL to zero.

[NPRR272: Replace paragraph (1) above with the following upon system implementation:] (1) The QSE for a Quick Start Generation Resource (QSGR) that is available for deployment by SCED and that does not have Ancillary Service Resource Responsibility for Contingency Reserve Service Provided by Sub-group 1 Resources (CRS1) in an Operating Hour, shall set the COP Resource Status to OFFQS, and the COP Low Sustained Limit (LSL) and COP HSL values to the expected sustainable LSL and HSL for the QSGR for the hour. If the QSGR is providing Supplemental Reserve Service Provided by Sub-group 1 Resources (SRS1), then the Ancillary Service Resource Responsibility for SRS1 shall be set to the Resource’s QSE-assigned SRS1 responsibility in the COP.

(2)	The QSGR that is available for deployment by SCED shall telemeter a Resource Status of ON and an LSL of zero prior to receiving a deployment instruction from SCED.  This status is necessary in order for SCED to recognize that the Resource can be Dispatched.  The status of the breaker shall be open and the output of the Resource shall be zero in order for the State Estimator to correctly assess the state of the system.  After being deployed for energy from SCED, the Resource shall telemeter an LSL equal to or less than the Resource’s actual output until the Resource has ramped to its physical LSL.  After reaching its physical LSL, the QSGR shall telemeter an LSL that reflects its physical LSL.

[NPRR272: Replace paragraph (2) above with the following upon system implementation:] (2) The QSGR that is available for deployment by SCED shall telemeter a Resource Status of OFFQS and a LSL of zero prior to receiving a deployment instruction from SCED. This status is necessary in order for SCED to recognize that the Resource can be Dispatched. The status of the breaker shall be open and the output of the Resource shall be zero in order for the State Estimator to correctly assess the state of the system. After being deployed for energy from SCED, the Resource shall telemeter an LSL equal to or less than the Resource’s actual output until the Resource has ramped to its physical LSL. After reaching its physical LSL, the QSGR shall telemeter an LSL that reflects its physical LSL.

(3)	A QSGR with a telemeter breaker status of open and a telemeter Resource Status of ON shall not provide Regulation Service or Primary Frequency Response Service (PFRS).

[NPRR272: Replace paragraph (3) above with the following upon system implementation:] (3) A QSGR with a telemeter breaker status of open and a telemeter Resource Status OFFQS shall not provide Regulation Service or Primary Frequency Response Service (PFRS).

(4)	ERCOT shall adjust the QSGR’s Mitigated Offer Cap curve as described in Section 4.4.9.4.1, Mitigated Offer Cap.

(5)	For a QSGR that is physically Off-Line, the Resource Entity shall submit a Normal Ramp Rate curve and Emergency Ramp Rate curve indicating QSGR’s ability to reach its ten-minute tested output from zero output in five minutes.  This is necessary to prevent SCED from deploying multiple QSGRs due to ramp limitation in the first five minutes after being Dispatched by SCED.  QSGRs shall be exempt from Base Point Deviation Charges as described in Section 6.6.5.3, Generators Exempt from Deviation Charges.

(6)	Any hour in which the QSE for the QSGR has shown the Resource as available for SCED Dispatch as described in this Section 3.8.3 is considered a QSE-Committed Interval.

(7)	QSEs must submit and maintain an Energy Offer Curve for their QSGRs for all hours in which the COP Resource Status is submitted as ON or OFFAS.  If a valid Energy Offer Curve or an Output Schedule does not exist for any QSGR for which a Resource Status of ON is telemetered at the end of the Adjustment Period, then ERCOT shall notify the QSE and set the Output Schedule equal to the then-current telemetered output of the Resource until an Output Schedule or Energy Offer Curve is submitted in a subsequent Adjustment Period.  For use as SCED inputs, ERCOT shall create proxy Energy Offer Curves for the Resource as described in paragraph (4) of Section 6.5.7.3, Security Constrained Economic Dispatch.

[NPRR272: Replace paragraph (7) above with the following upon system implementation:] (7) QSEs must submit and maintain an Energy Offer Curve for their QSGRs for all hours in which the COP Resource Status is submitted as OFFQS. If a valid Energy Offer Curve or an Output Schedule does not exist for any QSGR for which a Resource Status of OFFQS is telemetered at the end of the Adjustment Period, then ERCOT shall notify the QSE and set the Output Schedule equal to the then-current telemetered output of the Resource until an Output Schedule or Energy Offer Curve is submitted in a subsequent Adjustment Period. For use as SCED inputs, ERCOT shall create proxy Energy Offer Curves for the Resource as described in paragraph (4) of Section 6.5.7.3, Security Constrained Economic Dispatch.

(8)	Other than for the potential decommitment of a QSGR as described in Section 3.8.3.1, Quick Start Generation Resource Decommitment Decision Process, following a SCED QSGR deployment, the QSGR is expected to follow the SCED Base Points.

- 3.8.4	Hydro Generation Resources

Hydro Generation Resources operating in synchronous condenser fast-response mode and triggered by an under-frequency relay device at the frequency set point specified in paragraph (3) of Section 8.1.1.2.1.3, Primary Frequency Response Service Qualification, may provide PFRS.

- 3.9.1	Current Operating Plan (COP) Criteria

(1)	Each QSE that represents a Resource must submit a COP to ERCOT that reflects expected operating conditions for each Resource for each hour in the next seven Operating Days.

(2)	Each QSE that represents a Resource shall update its COP reflecting changes in availability of any Resource as soon as reasonably practicable, but in no event later than 60 minutes after the event that caused the change.

(3)	The Resource capacity in a QSE’s COP must be sufficient to supply the Ancillary Service Supply Responsibility of that QSE.

(4)	Load Resource COP values may be adjusted to reflect Distribution Losses in accordance with Section 8.1.1.2, General Capacity Testing Requirements.

(5)	A COP must include the following for each Resource represented by the QSE:

(a)	The name of the Resource;

(b)	The expected Resource Status:

(i)	Select one of the following for Generation Resources synchronized to the ERCOT System that best describes the Resource’s status.  These Resource Statuses are to be used for COP and/or Real-Time telemetry purposes, as appropriate.

(A)	ONRUC – On-Line and the hour is a RUC-Committed Hour;

(B)	ONREG – On-Line Resource with Energy Offer Curve providing Regulation Service;

(C)	ON – On-Line Resource with Energy Offer Curve or Off-Line Quick Start Generation Resource (QSGR) available for Security-Constrained Economic Dispatch (SCED) Dispatch;

[NPRR272: Replace paragraph (5)(b)(i)(C) above with the following upon system implementation:] (C) ON – On-Line Resource with Energy Offer Curve;

(D)	ONDSR – On-Line Dynamically Scheduled Resource (DSR);

(E)	ONOS – On-Line Resource with Output Schedule;

(F)	ONOSREG – On-Line Resource with Output Schedule providing Regulation Service;

(G)	ONDSRREG – On-Line DSR providing Regulation Service;

(H)	ONTEST – On-Line blocked from SCED for operations testing (while ONTEST, a Generation Resource may be shown on Outage in the Outage Scheduler);

(I)	ONEMR – On-Line EMR (available for commitment or dispatch only for ERCOT-declared Emergency Conditions; the QSE may appropriately set LSL and High Sustained Limit (HSL) to reflect operating limits);

(J)	ONPFR – On-Line as a synchronous condenser (hydro) providing  Primary Frequency Response Service (PFRS) but unavailable for Dispatch by SCED and available for commitment by RUC;

(K)	ONOPTOUT – On-Line and the hour is a RUC Buy-Back Hour;

(L)	SHUTDOWN – The Resource is On-Line and in a shutdown sequence, and has no Ancillary Service Obligations other than Off-Line Contingency Reserve Service (CRS) and/or Supplemental Reserve Service (SRS) which the Resource will provide following the shutdown.  This Resource Status is only to be used for Real-Time telemetry purposes; and

(M)	STARTUP – The Resource is On-Line and in a start-up sequence and has no Ancillary Service Obligations.  This Resource Status is only to be used for Real-Time telemetry purposes.

[NPRR272: Insert paragraph (5)(b)(i)(N) upon system implementation:] (N) OFFQS – Off-Line but available for SCED deployment. Only qualified QSGRs may utilize this status.

(ii)	Select one of the following for Off-Line Generation Resources not synchronized to the ERCOT System that best describes the Resource’s status.  These Resource Statuses are to be used for COP and/or Real-Time telemetry purposes, as appropriate.

(A)	OUT – Off-Line and unavailable;

(B)	OFFAS – Off-Line but reserved for CRS and/or SRS;

(C)	OFF – Off-Line but available for commitment in the Day-Ahead Market (DAM) and RUC; and

(D)	EMR – Available for commitment only for ERCOT-declared Emergency Condition events; the QSE may appropriately set LSL and HSL to reflect operating limits; and

(iii)	Select one of the following for Load Resources.  These Resource Statuses are to be used for COP and/or Real-Time telemetry purposes.

(A)	ONRGL – Available for Dispatch as a Controllable Load Resource for Regulation Service by Load Frequency Control (LFC) and, for any remaining Dispatchable capacity, by SCED with an Real-Time Market (RTM) Energy Bid;

(B)	ONCLR – Available for Dispatch as a Controllable Load Resource for one or more of Fast Frequency Response Service (FFRS), Primary Frequency Response Service (PFRS), Contingency Reserve Service Provided by Sub-group 1 Resources (CRS1), and Supplemental Reserve Service Provided by Sub-group 1 Resources (SRS1) by SCED with an RTM Energy Bid;

(C)	ONRL – Available for Dispatch as a Load Resource other than a Controllable Load Resource for one or more of FFRS, Contingency Reserve Service Provided by Sub-group 2 Resources (CRS2), and Supplemental Reserve Service Provided by Sub-group 2 Resources (SRS2); and

(D)	OUTL – Not available;

(c)	The HSL;

(d)	The LSL;

(e)	The High Emergency Limit (HEL);

(f)	The Low Emergency Limit (LEL); and

(g)	Ancillary Service Resource Responsibility capacity in MW for:

(i)	Regulation Up Service (Reg-Up);

(ii)	Regulation Down Service (Reg-Down);

(iii)	PFRS;

(iv)	FFRS;

(v)	CRS; and

(vi)	SRS .

(6)	For Combined Cycle Generation Resources, the above items are required for each operating configuration.  In each hour only one Combined Cycle Generation Resource in a Combined Cycle Train may be assigned one of the On-Line Resource Status codes described above.

(a)	During a RUC study period, if a QSE’s COP reports multiple Combined Cycle Generation Resources in a Combined Cycle Train to be On-Line for any hour, then until the QSE corrects its COP, the On-Line Combined Cycle Generation Resource with the largest HSL is considered to be On-Line and all other Combined Cycle Generation Resources in the Combined Cycle Train are considered to be Off-Line.  Furthermore, until the QSE corrects its COP, the Off-Line Combined Cycle Generation Resources as designated through the application of this process are ineligible for RUC commitment or de-commitment Dispatch Instructions.

(b)	For any hour in which QSE-submitted COP entries are used to determine the initial state of a Combined Cycle Generation Resource for a DAM or Day-Ahead Reliability Unit Commitment (DRUC) study and the COP shows multiple Combined-Cycle Generation Resources in a Combined Cycle Train to be in an On-line Resource Status, then until the QSE corrects its COP, the On-Line Combined Cycle Generation Resource that has been On-Line for the longest time from the last recorded start by ERCOT systems, regardless of the reason for the start, combined with the COP Resource Status for the remaining hours of the current Operating Day, is considered to be On-Line at the start of the DRUC study period and all other COP-designated Combined Cycle Generation Resources in the Combined Cycle Train are considered to be Off-Line.

(c)	The DAM and RUC shall honor the registered hot, intermediate or cold Startup Costs for each Combined Cycle Generation Resource registered in a Combined Cycle Train when determining the transition costs for a Combined Cycle Generation Resource.  In the DAM and RUC, the Startup Cost for a Combined Cycle Generation Resource shall be determined by the positive transition cost from the On-Line Combined Cycle Generation Resource within the Combine Cycle Train or from a shutdown condition, whichever ERCOT determines to be appropriate.

(7)	ERCOT may accept COPs only from QSEs.

(8)	For the first 48 hours of the COP, a QSE representing a Wind-powered Generation Resource (WGR) must enter an HSL value that is less than or equal to the amount for that Resource from the most recent Short-Term Wind Power Forecast (STWPF) provided by ERCOT.

[NPRR615: Replace paragraph (8) above with the following upon system implementation:] (8) For the first 48 hours of the COP, a QSE representing a Wind-powered Generation Resource (WGR) must enter an HSL value that is less than or equal to the amount for that Resource from the most recent Short-Term Wind Power Forecast (STWPF) provided by ERCOT, and a QSE representing a PhotoVoltaic Generation Resource (PVGR) must enter an HSL value that is less than or equal to the amount for that Resource from the most recent Short-Term PhotoVoltaic Power Forecast (STPPF) provided by ERCOT.

(9)	For hours 49 to 168 of the COP, a QSE representing a WGR shall enter an HSL value equal to their best estimate, which may be based on the wind power profile as published on the ERCOT website.

[NPRR588: Replace paragraph (9) above with the following upon system implementation:] (9) For hours 49 to 168 of the COP, a QSE representing an Intermittent Renewable Resource (IRR) shall enter an HSL value equal to its best estimate, which may be based on the appropriate power profile if published on the ERCOT website.

(10)	A QSE representing a Generation Resource that is not actively providing Ancillary Services or is providing Off-Line CRS and/or SRS that the Resource will provide following the shutdown, may only use a Resource Status of SHUTDOWN to indicate to ERCOT through telemetry that the Resource is operating in a shutdown sequence or a Resource Status of ONTEST to indicate in the COP and through telemetry that the Generation Resource is performing a test of its operations either manually dispatched by the QSE or by ERCOT as part of the test.  A QSE representing a Generation Resource that is not actively providing Ancillary Services may only use a Resource Status of STARTUP to indicate to ERCOT through telemetry that the Resource is operating in a start-up sequence requiring manual control and is not available for Dispatch.

(11)	If a QSE has not  submitted a valid COP for any Generation Resource for any hour in the DAM or RUC Study Period, then the Generation Resource is considered to have a Resource Status as OUT thus not available for DAM awards or RUC commitments for those hours.

(12)	If a COP is not available for any Resource for any hour from the current hour to the start  of the DAM period or RUC study, then the Resource Status for those hours are considered equal to the last known Resource Status from a previous hour’s COP or from telemetry as appropriate for that Resource.

3.16	Standards for Determining Ancillary Service Quantities

(1)	ERCOT shall comply with the requirements for determining Ancillary Service quantities as specified in these Protocols and the ERCOT Operating Guides.

(2)	ERCOT shall, at least annually, determine with supporting data, the methodology for determining the quantity requirements for each Ancillary Service needed for reliability, including minimum amounts and/or maximum amounts for each Ancillary Service, equivalency ratio between applicable Ancillary Services, and limitations on the quantity of an Ancillary Service that can be provided by various Resource types and the Direct Current (DC) Ties.

(3)	The ERCOT Board shall review and approve ERCOT's methodology for determining all quantities and equivalency ratios as described in paragraph (2) above.

(4)	If ERCOT determines a need for additional Ancillary Service Resources under these Protocols or the ERCOT Operating Guides, after an Ancillary Service Plan for a specified day has been posted, ERCOT shall inform the market by posting notice on the Market Information System (MIS) Secure Area, of ERCOT’s intent to procure additional Ancillary Service Resources under Section 6.4.9.2, Supplemental Ancillary Services Market.  ERCOT shall post the reliability reason for the increase in service requirements.

(5)	ERCOT shall post engineering studies, including relevant underlying data, on the MIS Secure Area supporting the ERCOT Board approved methodology for determining the requirements for each specific Ancillary Service.

(6)

ERCOT shall monitor synchronous inertia from all On-Line Resources and post the quantity to the MIS Public Area in Real-Time.

3.17.1	Fast Frequency Response Service (FFRS)

Fast Frequency Response Service (FFRS) is a service intended to arrest system frequency decay.  FFRS is automatically deployed when system frequency is at or below a predetermined threshold value established by ERCOT.  Resources providing FFRS must provide their full FFRS capacity within 30 cycles (0.5 seconds).  ERCOT may also deploy FFRS manually to maintain reliable and secure operations. FFRS may be provided by two FFRS sub-groups, FFRS Provided by Sub-group 1 Resources (FFRS1) and FFRS Provided by Sub-group 2 Resources (FFRS2), as defined in Section 2.1, Definitions.

3.17.2	Primary Frequency Response Service (PFRS)

Primary Frequency Response Service (PFRS) is a continuous service intended to arrest and stabilize or maintain the frequency of the ERCOT System.  PFRS is automatically deployed when system frequency deviation exceeds a predetermined threshold value.  Resources providing PFRS must deliver their required response, up to their full PFRS Ancillary Service Resource Responsibility, within 16 seconds.  Resources that provide PFRS must reserve capacity for this Ancillary Service and be able to assist in arresting and stabilizing over or under-frequency excursions.

3.17.3	Contingency Reserve Service (CRS)

Contingency Reserve Service (CRS) is intended to restore frequency to its nominal value following a system disturbance.  Resources providing CRS may also be used to provide a backup source of Regulation Service. ERCOT may also deploy CRS manually to maintain reliable and secure operations.  CRS may be provided by two CRS sub-groups, CRS Provided by Sub-group 1 Resources (CRS1) and CRS Provided by Sub-group 2 Resources (CRS2), as defined in Section 2.1, Definitions.  The CRS provided by both sub-groups must be fully deliverable within ten minutes of the CRS Dispatch Instruction.

3.17.4	Supplemental Reserve Service (SRS)

(1)	Supplemental Reserve Service (SRS) is intended to mitigate in resseen events including, but not limited to:

(a)	Large net Load forecast errors or ramps; and

(b)	Severe weather conditions.

(2)	SRS may be provided by two SRS sub-groups, SRS Provided by Sub-group 1 Resources (SRS1) and SRS Provided by Sub-group 2 Resources (SRS2), as defined in Section 2.1, Definitions.  The SRS provided by both groups must be fully deliverable within 30 minutes of the SRS Dispatch Instruction.

3.17.5	Regulation Service

(1)	Regulation Up Service (Reg-Up) is a service that provides capacity that can respond to signals from ERCOT within five seconds.  The amount of Reg-Up  Ancillary Service Resource Responsibility is the amount of capacity available from a Resource that may be called on to increase or decrease output or consumption as necessary to maintain proper system frequency. A Generation Resource providing Reg-Up must be able to increase energy output when deployed and decrease energy output when recalled.  A Load Resource providing Reg-Up must be able to decrease Load when deployed and increase Load when recalled.  Fast-Responding Regulation Service Up (FRRS-Up) is a subset of Reg-Up in which the participating Resource provides Reg-Up capacity to ERCOT within 60 cycles of either its receipt of an ERCOT Dispatch Instruction or the detection of a trigger frequency independent of an ERCOT Dispatch Instruction.  ERCOT dispatches Reg-Up by a Load Frequency Control (LFC) signal.  The LFC signal for FRRS-Up is separate from the LFC signal for other Reg-Up.

()	Regulation Down Service (Reg-Down) Service is a service that provides capacity that can respond to signals from ERCOT within five seconds.  The amount of Reg-Down Ancillary Service Resource Responsibility is the amount of capacity available from a Resource that may be called on to increase or decrease output or consumption as necessary to maintain proper system frequency.  A Generation Resource providing Reg-Down must be able to decrease energy output when deployed and increase energy output when recalled. A Load Resource providing Reg-Down must be able to increase Load when deployed and decrease Load when recalled.  Fast-Responding Regulation Service Down (FRRS-Down) is a subset of Reg-Down Service in which a participating Resource provides Reg-Down capacity to ERCOT within 60 cycles of either its receipt of an ERCOT Dispatch Instruction or the detection of a trigger frequency independent of an ERCOT Dispatch Instruction.  ERCOT dispatches Reg-Down by an LFC signal.  The LFC signal for FRRS-Down is separate from the LFC signal for other Reg-Down.

(3)	A single Resource shall not be allcarry more than 25% of the system-wide Reg-Up or Reg-Down requirement for any hour.

- 3.18	Resource Limits in Providing Ancillary Service

For both Generation Resources and Load Resources, the High Sustained Limit (HSL) must be greater than or equal to the sum of the Low Sustained Limit (LSL) and the Ancillary Service Resource Responsibilities for Fast Frequency Response Service (FFRS), Primary Frequency Response Service (PFRS), Regulation Up Service (Reg-Up), Regulation Down Service (Reg-Down), and Contingency Reserve Service (CRS).

(a)	The full amount of RRS provided from a Generation Resource must be less than or equal to 24% of thermal unit HSL for an Ancillary Service Offer, must be less than or equal to ten times the Emergency Ramp Rate, and must be frequency responsive;

- 4.2.1.1	Ancillary Service Plan

(1)	ERCOT shall analyze the expected Load conditions for the Operating Day and develop an Ancillary Service Plan that identifies the Ancillary Service MW necessary for each hour of the Operating Day.  The MW of each Ancillary Service required may vary from hour to hour depending on ERCOT System conditions.  ERCOT must post the Ancillary Service Plan to the Market Information System (MIS) Public Area by 0600 of the Day-Ahead.  This posting shall include equivalency ratios between applicable Ancillary Services.

(2)	If ERCOT determines that an Emergency Condition may exist that would adversely affect ERCOT System reliability, it may increase the requirement amounts of each Ancillary Service from the monthly amounts determined previously, as described in Section 3.16, Standards for Determining Ancillary Service Quantities, and must post any change to the MIS Public Area by 0600 of the Day-Ahead.

(3)	ERCOT shall determine the total required amount of each Ancillary Service under Section 3.16, or use its operational judgment and experience to change the daily quantity of each required Ancillary Service.

(4)	ERCOT shall include in the Ancillary Service Plan enough capacity to automatically control frequency with the intent to meet North American Electric Reliability Corporation (NERC) Reliability Standards.

(5)	ERCOT shall notify the Qualified Scheduling Entity (QSE) representing a Reliability Must-Run (RMR) Unit for any unit that is being committed in the Day-Ahead Market (DAM) or the Day-Ahead Reliability Unit Commitment (DRUC) at the same time that the DAM and DRUC participants are notified of the results of that respective process.

(6)	Once specified by ERCOT for an hour and published on the MIS Public Area, Ancillary Service quantity requirements for an Operating Day may not be decreased.

- 4.4.7.1	Self-Arranged Ancillary Service Quantities

(1)	A QSE may self-arrange all or a portion thereof, but not to exceed, the Ancillary Service Obligation allocated to it by ERCOT.  If a QSE elects to self-arrange Ancillary Service capacity, then ERCOT shall not pay the QSE for the Self-Arranged Ancillary Service Quantities for the portion that meets its Ancillary Service Obligation.

(2)	The QSE must indicate before 1000 in the Day-Ahead the Self-Arranged Ancillary Service Quantities, by service, so ERCOT can determine how much Ancillary Service capacity, by service, needs to be obtained through the DAM.

(3)	At or after 1000 in the Day-Ahead, a QSE may not change its Self-Arranged Ancillary Service Quantities unless ERCOT opens a Supplemental Ancillary Service Market (SASM).

(4)	Before 1430 in the Day-Ahead, all Self-Arranged Ancillary Service Quantities must be represented by physical capacity, either by Generation Resources or Load Resources, or backed by Ancillary Service Trades.

(5)	When a QSE chooses to self-arrange all or a portion of its Ancillary Service Obligations, it commits to the following conditions:

(a)	The QSE may self-arrange:

(i)	Regulation Up Service (Reg-Up), with the option of self-arranging Fast Responding Regulation Up Service (FRRS-Up) which counts towards Reg-Up self-arrangement, as described in paragraph (e) below;

(ii)	Regulation Down Service (Reg-Down), with the option of self-arranging Fast Responding Regulation Down Service (FRRS-Down) which counts towards Reg-Down self-arrangement, as described in paragraph (e) below;

(iii)	Primary Frequency Response Service (PFRS);

(iv)	Fast Frequency Response Service (FFRS);

(v)	Contingency Reserve Service (CRS); and

(vi)	Supplemental Reserve Service (SRS).

(b)	The QSE may provide all or part of its Self-Arranged Ancillary Service Quantity from one or more Resources it represents;

(c)	The QSE may provide all or a part of its Self-Arranged Ancillary Service Quantity through an Ancillary Service Trade;

(d)	The additional Self-Arranged Ancillary Service Quantity specified by the QSE in response to a SASM notice by ERCOT to obtain additional Ancillary Services in the Adjustment Period cannot be more than the additional Ancillary Service amount allocated by ERCOT to that QSE, as stated in the SASM notice, and cannot be changed once committed to ERCOT; and

(e)	If a QSE does not self-arrange all of its Ancillary Service Obligation, ERCOT shall procure the remaining amount of that QSE’s Ancillary Service Obligation.

(i)	For self-arranged FRRS-Up, the QSE shall not self-arrange more than its Load Ratio Share (LRS) multiplied by the maximum amount of FRRS-Up allowed in the posted Ancillary Service Plan for a given hour.  Self-arranged FRRS-Up MW quantities multiplied by the equivalency ratio between Reg-Up and FRRS-Up is counted towards the self-arrangement of Reg-Up.

(ii)	For self-arranged FRRS-Down, the QSE shall not self-arrange more than its LRS multiplied by the maximum amount of FRRS-Down allowed in the posted Ancillary Service Plan for a given hour.  Self-arranged FRRS-Down MW quantities multiplied by the equivalency ratio between Reg-Down and FRRS-Down is counted towards the self-arrangement of Reg-Down.

(iii)	For self-arranged FFRS Provided by Sub-group 1 Resources (FFRS1), the QSE shall not self-arrange more than its LRS multiplied by the maximum amount of FFRS1 allowed in the posted Ancillary Service Plan for a given hour. In addition, the total FFRS (FFRS1 plus FFRS Provided by Sub-group 2 Resources (FFRS2)) that is self-arranged cannot exceed the QSE’s LRS multiplied by the maximum amount of FFRS allowed as posted in the Ancillary Service Plan for a given hour.

(iv)	For self-arranged CRS Provided by Sub-group 2 Resources (CRS2), the QSE shall not self-arrange more than its LRS multiplied by the difference between the total CRS required and the minimum amount of CRS Provided by Sub-group 1 Resources (CRS1) required as posted in the Ancillary Service Plan for a given hour.

(v)	For self-arranged SRS Provided by Sub-group 2 Resources (SRS2), the QSE shall not self-arrange more than its LRS multiplied by the difference between the total SRS required and the minimum amount of SRS Provided by Sub-group 1 Resources (SRS1) required as posted in the Ancillary Service Plan for a given hour.

(f)	A QSE has the option of self-arranging PFRS in lieu of self-arranging FFRS with the use of the applicable equivalency ratio between PFRS and FFRS. A QSE shall not self-arrange FFRS in lieu of self-arranging PFRS.

- 4.4.7.1.1	Negative Self-Arranged Ancillary Service Quantities

(1)	A QSE may submit a negative Self-Arranged Ancillary Service Quantity in the DAM.  ERCOT shall procure all negative Self-Arranged Ancillary Service Quantities submitted by a QSE.

(2)	Procurements of negative Self-Arranged Ancillary Service Quantities by ERCOT shall be settled in the same manner as Ancillary Service Obligations that are not self-arranged and according to the charges defined in Section 4.6.4.2, Charges for Ancillary Services Procurement in the DAM, and Section 6.7, Real-Time Settlement Calculations for the Ancillary Services.

(3)	A QSE may not submit a negative Self-Arranged Ancillary Service Quantity in the DAM that is less than -500 MW per Ancillary Service.  For compliance purposes, a QSE may not submit a negative Self-Arranged Ancillary Service Quantity in the DAM that is greater in magnitude than the absolute value of the net sales of its Ancillary Service Trades per Ancillary Service.

- 4.4.7.2	Ancillary Service Offers

(1)	By 1000 in the Day-Ahead, a QSE may submit Generation Resource-specific Ancillary Service Offers to ERCOT for the DAM and may offer the same Generation Resource capacity for any or all of the Ancillary Service products simultaneously with any Energy Offer Curves from that Generation Resource in the DAM.  A QSE may also submit Ancillary Service Offers in a Supplemental Ancillary Service Market (SASM).  Offers of more than one Ancillary Service product from one Generation Resource may be inclusive or exclusive of each other and of any Energy Offer Curves, as specified according to a procedure developed by ERCOT.

(2)	By 1000 in the Day-Ahead, a QSE may submit Load Resource-specific Ancillary Service Offers for to ERCOT and may offer the same Load Resource capacity for any or all of those Ancillary Service products simultaneously.  Ancillary Service Offers for more than one Ancillary Service product from one Load Resource may be inclusive or exclusive of each other, as specified according to a procedure developed by ERCOT, except that Ancillary Service Offers for more than one Ancillary Service product from a Load Resource controlled by high-set under-frequency relay operating a breaker are considered to be mutually exclusive.

(3)	Ancillary Service Offers remain active for the offered period until:

(a)	Selected by ERCOT;

(b)	Automatically inactivated by the software at the offer expiration time specified by the QSE when the offer is submitted; or

(c)	Withdrawn by the QSE, but a withdrawal is not effective if the deadline for submitting offers has already passed.

(4)	A Load Resource that is not a Controllable Load Resource may specify whether its Ancillary Service Offer may only be procured by ERCOT as a block.

4.4.7.2.1	Ancillary Service Offer Criteria

(1)	Each Ancillary Service Offer must be submitted by a QSE and must include the following information:

(a)	The selling QSE;

(b)	The Resource represented by the QSE from which the offer would be supplied;

(c)	The quantity in MW and Ancillary Service type from that Resource for this specific offer and the specific quantity in MW and Ancillary Service type of any other Ancillary Service offered from this same capacity;

(d)	An Ancillary Service Offer linked to a Three-Part Supply Offer from a Resource designated to be Off-Line for the offer period in its COP may only be struck if the Three-Part Supply Offer is struck.  The total capacity struck must be within limits as defined in item (4)(c)(iii) of Section 4.5.1, DAM Clearing Process;

(e)	An Ancillary Service Offer linked to other Ancillary Service Offers or an Energy Offer Curve from a Resource designated to be On-Line for the offer period in its COP may only be struck if the total capacity struck is within limits as defined in item (4)(c)(iii) of Section 4.5.1;

(f)	The first and last hour of the offer;

(g)	A fixed quantity block, or variable quantity block indicator for the offer:

(i)	If a fixed quantity block, not to exceed 150 MW, which may only be offered by a Load Resource other than a Controllable Load Resource providing FFRS1 or FFRS2, and/or CRS2, and/or SRS2, for which only one Ancillary Service will be awarded and may clear at a Market Clearing Price for Capacity (MCPC) below the Ancillary Service Offer price for that block, the single price (in $/MW) and single quantity (in MW) for all hours offered in that block; or

(ii)	If a variable quantity block, which may be offered by a Generation Resource or a Load Resource, the single price (in $/MW) and single “up to” quantity (in MW) contingent on the purchase of all hours offered in that block; and

(h)	The expiration time and date of the offer.

(2)	A valid Ancillary Service Offer in the DAM must be received before 1000 for the effective DAM.  A valid Ancillary Service Offer in an SASM must be received before the applicable deadline for that SASM.

(3)	No Ancillary Service Offer price may exceed the System-Wide Offer Cap (SWCAP) (in $/MW).  No Ancillary Service Offer price may be less than $0 per MW.

(4)	The minimum amount per Resource for each Ancillary Service product that may be offered is one-tenth (0.1) MW.

(5)	A Resource may offer more than one Ancillary Service.

(6)	Offers for Load Resources may be adjusted to reflect Distribution Losses in accordance with Section 8.1.1.2, General Capacity Testing Requirements.

(7)	A Load Resource that is qualified to perform as a Controllable Load Resource may not offer to provide Ancillary Services as a Controllable Load Resource and a Load Resource controlled by high-set under-frequency relay simultaneously behind a common breaker.

4.4.7.3	Ancillary Service Trades

(1)	An Ancillary Service Trade is the information for a QSE-to-QSE transaction that transfers an obligation to provide Ancillary Service capacity between a buyer and a seller.

(2)	An Ancillary Service Trade that is reported to ERCOT by 1430 in the Day-Ahead changes the Ancillary Service Supply Responsibility of the buyer and seller in the DRUC process.  An Ancillary Service Trade that is reported to ERCOT after 1430 in the Day-Ahead changes the Ancillary Service Supply Responsibility of the buyer and seller in any applicable HRUC process, the deadline for which is after the trade is submitted.

(3)	As soon as practicable, ERCOT shall notify each QSE through the Messaging System of any of its Ancillary Service Trades that are invalid Ancillary Service Trades.  The QSE may correct and resubmit any invalid Ancillary Service Trade, but the reporting time of the trade is determined by when the validated Ancillary Service Trade was submitted and not when the original invalid Ancillary Service Trade was submitted.

(4)	A QSE with an FFRS obligation may transfer its obligation to another QSE via Ancillary Service Trade(s) for PFRS using the applicable equivalency ratio between PFRS and FFRS in the posted Ancillary Service Plan for a given hour.  A QSE with a PFRS obligation may not transfer its obligation to another QSE via Ancillary Service Trade(s) for FFRS.

(5)	A QSE with an FRRS-Up Ancillary Service Supply Responsibility has the option of transferring its Ancillary Service Supply Responsibility to another QSE via Ancillary Service Trade(s) for Reg-Up using the applicable equivalency ratio between Reg-Up and FRRS-Up in the posted Ancillary Service Plan for a given hour.  A QSE with a Reg-Up Ancillary Service Supply Responsibility shall not transfer its Ancillary Service Supply Responsibility to another QSE via Ancillary Service Trade(s) for FRRS-Up.

(6)	A QSE with an FRRS-Down Ancillary Service Supply Responsibility has the option of transferring its Ancillary Service Supply Responsibility to another QSE via Ancillary Service Trade(s) for Reg-Down using the applicable equivalency ratio between Reg-Down and FRRS-Down in the posted Ancillary Service Plan for a given hour.  A QSE with a Reg-Down Ancillary Service Supply Responsibility shall not transfer its Ancillary Service Supply Responsibility to another QSE via Ancillary Service Trade(s) for FRRS-Down.

4.4.7.3.1	Ancillary Service Trade Criteria

(1)	Each Ancillary Service Trade must be reported by a QSE and must include the following information:

(a)	The buying QSE;

(b)	The selling QSE;

(c)	The type of Ancillary Service;

(d)	The quantity in MW; and

(e)	The first and last hours of the trade.

(2)	An Ancillary Service Trade must be confirmed by both the buying QSE and selling QSE to be considered valid and to be used in an ERCOT process.

4.4.9.1	Three-Part Supply Offers

(1)	A Three-Part Supply Offer consists of a Startup Offer, a Minimum-Energy Offer, and an Energy Offer Curve.  ERCOT must validate each Startup Offer, Minimum-Energy Offer, and Energy Offer Curve before it can be used in any ERCOT process.

(2)	The DAM uses all three parts of the Three-Part Supply Offer and also uses Energy Offer Curves submitted without a Startup Offer and without a Minimum-Energy Offer.  The RUC only uses the Startup Offer and the Minimum-Energy Offer components for determining RUC commitments, but the Energy Offer Curve may be used in Settlement to claw back some or all of a RUC-committed Resource’s energy payments.  The Energy Offer Curve may also be used by SCED in Real-Time Operations.

(3)	A QSE may submit an Energy Offer Curve without also submitting a Startup Offer and a Minimum-Energy Offer for the DAM and during the Adjustment Period, but only Three-Part Supply Offers are used in the RUC process.  A QSE that submits an Energy Offer Curve without also submitting a Startup Offer and a Minimum-Energy Offer is considered not to be offering the Resource into the RUC, but that does not prevent the Resource from being committed in the RUC process like any other Resource that does not submit an offer in the RUC.

[NPRR515: Insert paragraphs (3)(a) – (3)(c) below upon system implementation:] (a) A QSE that submits an Energy Offer Curve without a Startup Offer and a Minimum-Energy Offer for the DAM for any given hour will be considered by the DAM to be self-committed for that hour, as long as an Off-Line Ancillary Service Offer for CRS and/or SRS was not also submitted for that hour. (b) A Combined Cycle Generation Resource will be considered by the DAM to be self-committed if: (i) Its QSE submits an Energy Offer Curve without a Startup Offer and a Minimum-Energy Offer for the DAM for that Combined Cycle Generation Resource and no other Combined Cycle Generation Resource within the Combined Cycle Train; and (ii) Its QSE submits no Off-Line Ancillary Service Offer for CRS and/or SRS for any Combined Cycle Generation Resource within the Combined Cycle Train. (c) When the DAM considers a self-committed offer for clearing, the Resource constraints identified in paragraph (4)(c)(ii) of Section 4.5.1, DAM Clearing Process, other than HSL, are ignored.

(4)	For any hours in which the Resource is not RUC-committed, ERCOT shall consider all Three-Part Supply Offers in the RUC process until:

(a) 	The QSE withdraws the offer; or

(b) 	The offer expires by its terms.

- 4.5.1	DAM Clearing Process

(1)	At 1000 in the Day-Ahead, ERCOT shall start the Day-Ahead Market (DAM) clearing process.  If the processing of DAM bids and offers after 0900 is significantly delayed or impacted by a failure of ERCOT software or systems that directly impacts the DAM, ERCOT shall post a Notice as soon as practicable on the Market Information System (MIS) Public Area, in accordance with paragraph (1) of Section 4.1.2, Day-Ahead Process and Timing Deviations, extending the start time of the execution of the DAM clearing process by an amount of time at least as long as the duration of the processing delay plus ten minutes.  In no event shall the extension exceed more than one hour from when the processing delay is resolved.

(2)	ERCOT shall complete a Day-Ahead Simultaneous Feasibility Test (SFT).  This test uses the Day-Ahead Updated Network Model topology and evaluates all Congestion Revenue Rights (CRRs) for feasibility to determine hourly oversold quantities.

(3)	The purpose of the DAM is to economically and simultaneously clear offers and bids described in Section 4.4, Inputs into DAM and Other Trades.

(4)	The DAM uses a multi-hour mixed integer programming algorithm to maximize bid-based revenues minus the offer-based costs over the Operating Day, subject to security and other constraints, and ERCOT Ancillary Service procurement requirements.

- The bid-based revenues include revenues from DAM Energy Bids and Point-to-Point (PTP) Obligation bids.

(b)	The offer-based costs include costs from the Startup Offer, Minimum Energy Offer, and Energy Offer Curve of any Resource that submitted a Three-Part Supply Offer, DAM Energy-Only Offers and Ancillary Service Offers.

(c)	Security constraints specified to prevent DAM solutions that would overload the elements of the ERCOT Transmission Grid include the following:

(i)	Transmission constraints – transfer limits on energy flows through the ERCOT Transmission Grid, e.g., thermal or stability limits.  These limits must be satisfied by the intact network and for certain specified contingencies.

These constraints may represent:

(A)	Thermal constraints – protect Transmission Facilities against thermal overload.

(B)	Generic constraints – protect the ERCOT Transmission Grid against transient instability, dynamic stability or voltage collapse.

(C)	Power flow constraints – the energy balance at required Electrical Buses in the ERCOT Transmission Grid must be maintained.

(ii)	Resource constraints – the physical and security limits on Resources that submit Three-Part Supply Offers:

(A)	Resource output constraints – the Low Sustained Limit (LSL) and High Sustained Limit (HSL) of each Resource; and

(B)	Resource operational constraints – includes minimum run time, minimum down time, and configuration constraints.

(iii)	Other constraints –

(A)	Linked offers – the DAM may not select any one part of that Resource capacity to provide more than one Ancillary Service or to provide both energy and an Ancillary Service in the same Operating Hour.  The DAM may, however, select part of that Resource capacity to provide one Ancillary Service and another part of that capacity to provide a different Ancillary Service or energy in the same Operating Hour, provided that a Generation Resource may not offer, and the DAM may not select, linked Energy and Off-Line Ancillary Service Offers for Contingency Reserve Service (CRS) and/or Supplemental Reserve Service (SRS) in the same Operating Hour. However, offers may be submitted for multiple configurations in a Combined Cycle Train and the DAM may award, for the same hour, energy and On-Line Ancillary Services to one configuration and Off-Line Ancillary Service(s) of CRS and/or SRS to another Off-Line configuration provided that the Off-Line configuration can be brought On-Line in the required time for the offered service and have the ability to meet the combined total of energy and Ancillary Service awards of the Combined Cycle Train. For a given hour, only one configuration can be awarded energy and On-Line Ancillary Services and one other Off-Line configuration can be awarded Off-Line Ancillary Services.

(B)	The sum of the awarded Ancillary Service capacities and energy for each Resource must be within the Resource limits specified in the Current Operating Plan (COP) and Section 3.18, Resource Limits in Providing Ancillary Service, and the Resource Parameters as described in Section 3.7, Resource Parameters.

(C)	Block Ancillary Service Offers for a Load Resource – blocks will not be cleared unless the entire quantity block can be awarded.  Because block Ancillary Service Offers cannot set the Market Clearing Price for Capacity (MCPC), a block Ancillary Service Offer may clear below the Ancillary Service Offer price for that block.

(D)	Block DAM Energy Bids, DAM Energy-Only Offers, and PTP Obligation bids – blocks will not be cleared unless the entire time and/or quantity block can be awarded.  Because quantity block bids and offers cannot set the Settlement Point Price, a quantity block bid or offer may clear in a manner inconsistent with the bid or offer price for that block.

(E)	Combined Cycle Generation Resources – The DAM may commit a Combined Cycle Generation Resource in a time period that includes the last hour of the Operating Day only if that Combined Cycle Generation Resource can transition to a shutdown condition in the DAM Operating Day.

(d)	Ancillary Service needs for each Ancillary Service include the needs specified in the Ancillary Service Plan that are not part of the Self-Arranged Ancillary Service Quantity and that must be met from available DAM Ancillary Service Offers while co-optimizing with DAM Energy Offers.  ERCOT may not buy more of one Ancillary Service in place of the quantity of a different service.  See Section 4.5.2, Ancillary Service Insufficiency, for what happens if insufficient Ancillary Service Offers are received in the DAM.

(5)	ERCOT shall determine the appropriate Load distributions to allocate offers, bids, and source and sink of CRRs at a Load Zone across the Electrical Buses that are modeled with Load in that Load Zone.  The default distribution is the State Estimator hourly distribution for the seven days before the Operating Day.  If ERCOT decides, in its sole discretion, to change this distribution for reasons such as anticipated weather events or holidays, ERCOT shall select a State Estimator distribution from a proxy day reasonably reflecting the anticipated distribution in the Operating Day.  ERCOT may also modify this distribution to account for predicted differences in network topology between the proxy day and Operating Day.  ERCOT shall develop a methodology, subject to Technical Advisory Committee (TAC) approval, to describe the modification of the proxy day bus-load distribution for this purpose.

(6)	ERCOT shall allocate offers, bids, and source and sink of CRRs at a Hub using the distribution factors specified in the definition of that Hub in Section 3.5.2, Hub Definitions.

(7)	A Resource that has a Three-Part Supply Offer cleared in the DAM may be eligible for Make-Whole Payment of the Startup Offer and Minimum Energy Offer submitted by the Qualified Scheduling Entity (QSE) representing the Resource under Section 4.6, DAM Settlement.

(8)	The DAM Settlement is based on hourly MW awards and on Day-Ahead hourly Settlement Point Prices.  All PTP Options settled in the DAM are settled based on the Day-Ahead Settlement Point Prices (DASPPs).  ERCOT shall assign a Locational Marginal Price (LMP) to de-energized Electrical Buses for use in the calculation of the DASPPs by using heuristic rules applied in the following order:

(a)	Use an appropriate LMP predetermined by ERCOT as applicable to a specific Electrical Bus; or if not so specified

(b)	Use the following rules in order:

(i)	Use average LMP for Electrical Buses within the same station having the same voltage level as the de-energized Electrical Bus, if any exist.

(ii)	Use average LMP for all Electrical Buses within the same station, if any exist.

(iii)	Use System Lambda.

(9)	The Day-Ahead MCPC for each hour for each Ancillary Service, except Fast Frequency Response Service (FFRS), Fast Responding Regulation Up Service (FRRS-Up), and Fast Responding Regulation Down Service (FRRS-Down) is the Shadow Price for that Ancillary Service for the hour as determined by the DAM algorithm.  The equivalency ratio from the posted Ancillary Service Plan between Primary Frequency Response Service (PFRS) and FFRS, Reg-Up and FRRS-Up, Reg-Down and FRRS-Down will be utilized by the DAM clearing process to substitute between these Ancillary Services.

(a)	The MCPC for FFRS for a given hour will be the product of the equivalency ratio between PFRS and FFRS and the MCPC for PFRS, and MCPC for FFRS shall be capped at Value of Lost Load (VOLL).

(b)	The MCPC for FRRS-Up for a given hour will be the product of the equivalency ratio between Reg-Up and FRRS-Up and the MCPC for Reg-Up, and the MCPC for FRRS-Up shall be capped at the VOLL.

(c)	The MCPC for FRRS-Down for a given hour will be the product of the equivalency ratio between Reg-Down and FRRS-Down and the MCPC for Reg-Down, and the MCPC for FRRS-Down shall be capped at the VOLL.

(10)	If the Day-Ahead MCPC cannot be calculated by ERCOT, the Day-Ahead MCPC for the particular Ancillary Service is equal to the Day-Ahead MCPC for that Ancillary Service in the same Settlement Interval of the preceding Operating Day.

(11)	If the DASPPs cannot be calculated by ERCOT, all CRRs shall be settled based on Real-Time prices.  Settlements for all CRRs shall be reflected on the Real-Time Settlement Statement.

- 4.5.2	Ancillary Service Insufficiency

(1)	ERCOT shall determine if there is an insufficiency in Ancillary Service Offers before executing the DAM.  If ERCOT receives insufficient Ancillary Service Offers in the DAM to procure one or more required Ancillary Service such that the Ancillary Service Plan is deficient and system security and reliability is threatened:

(a)	ERCOT shall declare an Ancillary Service insufficiency and issue a Watch under Section 6.5.9.3.3, Watch.

(b)	ERCOT shall request additional Ancillary Service Offers.

(i)	A QSE may resubmit an offer for an Ancillary Service that it submitted before the Watch for the same Ancillary Service, but the resubmitted offer must meet the following criteria to be considered a valid offer:

(A)	The offer quantity may not be less than the offer quantity submitted before the Watch, unless the  portion of the offer not resubmitted was priced higher than the portion of the offer that is being resubmitted; and

(B)	For the amount of the offer quantity that is not more than the offer quantity submitted before the Watch, the offer must be priced equal to or less than the price of the offer submitted before the Watch.

(ii)	For any amount of the offer that is greater in quantity than the QSE’s offer that was not submitted before the Watch, the incremental amount of the offer may be submitted at a price subject to the offer cap.

(c)	ERCOT shall not begin executing the DAM sooner than 30 minutes after issuing the Watch.  If the additional Ancillary Service Offers are still insufficient to supply the Ancillary Service required in the Day-Ahead Ancillary Service Plan then ERCOT shall run the DAM by reducing the Ancillary Service Plan quantities only for purposes of the DAM by the amount of insufficiency.

(d)	When ERCOT must reduce the Ancillary Service Plan for purposes of the DAM due to insufficient Ancillary Service Offers, ERCOT shall preserve the Ancillary Service Plan in the DAM in the following order of priority:

(i)	Regulation Up Service (Reg-Up);

(ii)	Regulation Down Service (Reg-Down);

(iii)	PFRS;

(iv)	FFRS;

(v)	CRS; and

(vi)	SRS.

(2)	ERCOT shall procure the difference in capacity between the Day-Ahead Ancillary Service Plan and the DAM-reduced Ancillary Service Plan amounts using the Day-Ahead Reliability Unit Commitment (DRUC) from Resources that are qualified to provide the needed Ancillary Service.

- 4.6.2.3.1	Day-Ahead Make-Whole Payment

(1)	ERCOT shall pay the QSE a Day-Ahead Make-Whole Payment for an eligible Resource, except that the Day-Ahead Make-Whole RMR Revenue amount is calculated but not paid for any RMR Unit, for each Operating Hour in a DAM-commitment period.

(2)	Any Ancillary Service Offer cleared for the same Operating Hour, QSE, and Generation Resource as a Three-Part Supply Offer cleared in the DAM shall be included in the calculation of the Day-Ahead Make-Whole Payment.

(3)	The guaranteed cost, energy revenue, and Ancillary Service revenue calculated for each Combined Cycle Generation Resource are each summed for the Combined Cycle Train, and the the Day-Ahead Make-Whole Amount is calculated for the Combined Cycle Train.

(4)	For an Aggregate Generation Resource (AGR), Startup Cost shall be scaled according to the ratio of the maximum number of its generators online during a contiguous block of DAM-committed Intervals, as indicated by telemetry, compared to the total number of generators registered to the AGR and used in the approved verifiable cost for the AGR.

(5)	The Day-Ahead Make-Whole Payment to each QSE for each DAM-committed Generation Resource (excluding RMR Units) is calculated as follows:

DAMWAMT q, p, r, h	=	(-1) * Max (0, DAMGCOST q, p, r + DAEREV q, p, r, h

+ DAASREV q, r, h) * DAESR q, p, r, h / (DAESR q, p, r, h)

(6)	The Day-Ahead Make-Whole RMR Revenue to each QSE for each DAM-committed RMR Unit is calculated as follows:

DAMWRMRREV q, p,r, h  = (-1) * Max (0, DAMGCOST q, p, r +DAEREV q, p, r, h

+ DAASREV q, r, h) * DAESR q, p, r, h / (DAESR q, p, r, h)

(7)	The Day-Ahead Make-Whole Guaranteed Costs are calculated for each eligible DAM-Committed Generation Resource (including RMR Units) as follows:

For non-Combined Cycle Trains,

DAMGCOST q, p, r	=	DASUO q, p, r + (DAMEO q, p, r, h * DALSL q, p, r, h)

+ (DAAIEC q, p, r, h * (DAESR q, p, r, h – DALSL q, p, r, h))

For an AGR,

DAMGCOST q, p, r	=		      DASUPR q, p, r + (DAMEO q, p, r, h * DALSL q, p, r, h)

+ (DAAIEC q, p, r, h * (DAESR q, p, r, h – DALSL q, p, r, h))

Where:

DASUPR q, p, r	 =	 Min(DASUO q, p, r, DASUCAP q, p, r)

If ERCOT has approved verifiable Startup Costs

Then:

DASUCAP q, p, r        =	Maxc(AGRRATIO q, p, r ) * verifiable Startup Costs q, r

Where:

AGRRATIO q, p, r	 =	AGRMAXON q, p, r / AGRTOT q, p, r

Otherwise:

DASUCAP q, p, r       = 	Maxc(AGGRATIO q,p,r) * RCGSC

For Combined Cycle Trains,

DAMGCOST q, p, r	=	DASUO q, p, r +  (DAMEO q, p, r, h * DALSL q, p, r, h)

+ (Max (0, DASUO afterCCGR – DASUO beforeCCGR))

+  (DAAIEC q, p, r, h * (DAESR q, p, r, h – DALSL q, p, r, h))

[NPRR617: Replace paragraph (7) above with the following upon system implementation:] (7) The Day-Ahead Make-Whole Guaranteed Costs are calculated for each eligible DAM-Committed Generation Resource (including RMR Units) as follows: For non-Combined Cycle Trains, DAMGCOST q, p, r = Min(DASUO q, p, r , DASUCAP q, p, r) + (Min(DAMEO q, p, r, h , DAMECAP p,q, r,h )* DALSL q, p, r, h) + (DAAIEC q, p, r, h * (DAESR q, p, r, h – DALSL q, p, r, h)) For a Resource which is not an AGR, If ERCOT has approved verifiable Startup Costs and minimum-energy costs for the Resource, Then: DASUCAP p,q, r = verifiable Startup Costs q, r, s DAMECAP p,q,r,h = verifiable minimum-energy costs q, r, i Otherwise: DASUCAP p,q, r = Resource Category Startup Offer Generic Cap (RCGSC) DAMECAP p,q, r, h = Resource Category Minimum-Energy Generic Cap (RCGMEC) For an AGR, DAMGCOST q, p, r = DASUPR q, p, r + (Min(DAMEOq, p, r, h, DAMECAP p,q,r,h) * DALSL q, p, r, h) + (DAAIEC q, p, r, h * (DAESR q, p, r, h – DALSL q, p, r, h)) Where: DASUPR q, p, r = Min(DASUO q, p, r, DASUCAP q, p, r) If ERCOT has approved verifiable Startup Costs Then: DASUCAP q, p, r = Maxc(AGRRATIO q, p, r ) * verifiable Startup Costs q, r Where: AGRRATIO q, p, r = AGRMAXON q, p, r / AGRTOT q, p, r Otherwise: DASUCAP q, p, r = Maxc(AGGRATIO q,p,r) * RCGSC For Combined Cycle Trains, DAMGCOST q, p, r = Min(DASUO q, p, r , DASUCAPq, p, r) + (Min(DAMEO q, p, r, h , DAMECAP q, p, r,h) * DALSL q, p, r, h) + (Max(0, Min(DASUO afterCCGR , DASUCAPafterCCGR) – Min(DASUO beforeCCGR , DASUCAPbeforeCCGR)) + (DAAIEC q, p, r, h * (DAESR q, p, r, h – DALSL q, p, r, h))

(8)	The Day-Ahead Make-Whole Revenue is calculated for each DAM-Committed Generation Resource (including RMR Units) as follows:

DAEREV q, p, r, h		=	(-1) * DASPP p, h * DAESR q, p, r, h

DAASREV q, r, h 		=	((-1) * MCPCRU DAM, h * PCRUR r, q, DAM, h)

+ ((-1) * MCPCFRRSU DAM, h  * PCFRRSU r, q,DAM, h)

+ ((-1) * MCPCRD DAM, h  * PCRDR r, q,DAM, h)

+ ((-1) * MCPCFRRSD DAM, h  * PCFRRSD r, q,DAM, h)

+ ((-1) * MCPCPFRS DAM, h  * PCPFRSR r, q,DAM, h)

+ ((-1) * MCPCFFRS DAM, h  * PCFFRSR r, q,DAM, h)

+ ((-1) * MCPCCRS DAM, h  * PCCRSR r, q,DAM, h)

+ ((-1) * MCPCSRS DAM, h  * PCSRSR r, q,DAM, h)

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| DAMWAMT q, p, r, h | $ | Day-Ahead Make-Whole Payment per QSE per Settlement Point per Resource per hourThe payment to QSE q to make-whole the Startup Cost and energy cost of Resource r committed in the DAM at Resource Node p for the hour h. When a Combined Cycle Generation Resource is committed in the DAM, payment is made to the Combined Cycle Train for the DAM-committed Combined Cycle Generation Resource. |
| DAMWRMRREV q, p, r, h | $ | Day-Ahead Make-Whole RMR Revenue per QSE per Settlement Point per RMR Resource per hourThe revenue calculated but not paid to QSE q to make-whole the Startup Cost and energy cost of the RMR Resource r committed in the DAM at Resource Node p for the hour h. When a Combined Cycle Generation Resource that is an RMR Resource is committed in the DAM, revenue is calculated for the Combined Cycle Train for the Combined Cycle Generation Resource. |
| DAMGCOST q, p, r | $ | Day-Ahead Market Guaranteed Amount per QSE per Settlement Point per ResourceThe sum of the Startup Cost and the operating energy costs of the DAM-committed Resource r at Resource Node p represented by QSE q, for the DAM-commitment period. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| DAEREV q, p, r, h | $ | Day-Ahead Energy Revenue per QSE per Settlement Point per Resource by hourThe revenue received in the DAM for Resource r at Resource Node p represented by QSE q, based on the DAM Settlement Point Price, for the hour h. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| DAASREV q, r, h | $ | Day-Ahead Ancillary Service Revenue per QSE per Resource by hourThe revenue received in the DAM for Resource r represented by QSE q, based on the Market Clearing Price for Capacity (MCPC) for each Ancillary Service in the DAM, for the hour h. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| DASPP p, h | $/MWh | Day-Ahead Settlement Point Price by Settlement Point by hourThe DAM Settlement Point Price at Resource Node p for the hour h. |
| DAESR q, p, r, h | MW | Day-Ahead Energy Sale from Resource per QSE by Settlement Point per Resource by hourThe amount of energy cleared through Three-Part Supply Offers in the DAM for Resource r at Resource Node p represented by QSE q for the hour h. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| DASUPR q, p, r | $/MWh | Day-Ahead Startup Price per QSE per Settlement Point per Resource—The derived Startup Price for an AGR r at Resource Node p represented by QSE q, for the first hour of the DAM-commitment period. |
| DASUCAP q, p, r, | $/MWh | Day-Ahead Startup Cap per QSE per Settlement Point per Resource—The amount used for AGR r as Startup Costs. The cap is the RCGSC unless ERCOT has approved verifiable unit-specific Startup Costs for that Resource, in which case the startup cap is the scaled verifiable unit-specific Startup Cost. See Section 5.6.1, Verifiable Costs, for more information on verifiable costs. |
| [NPRR617: Replace the variable “DASUCAP q, p, r,” above with the following upon system implementation:] DASUCAP q, p, r,; $/start; Day-Ahead Startup Cap per QSE per Settlement Point per Resource—The amount used for AGR r or Resource r as Startup Costs. The cap is the Resource Category Startup Offer Generic Cap (RCGSC) unless ERCOT has approved verifiable unit-specific Startup Costs for that Resource, in which case the startup cap is the scaled verifiable unit-specific Startup Cost for the AGR or the verifiable unit-specific Startup Cost for non-AGR Resources. See Section 5.6.1, Verifiable Costs, for more information on verifiable costs... |
| [NPRR617: Insert the variable “DAMECAP p,q,r,h” below upon system implementation:] DAMECAP p,q,r,h; $/MWh; Day-Ahead Minimum-Energy Cap —The amount used for Resource r for minimum-energy costs. The minimum cost is the Resource Category Minimum-Energy Generic Cap (RCGMEC) unless ERCOT has approved verifiable unit-specific minimum energy costs for that Resource, in which case the minimum energy cap is the verifiable unit-specific minimum energy cost. See Section 5.6.1 for more information on verifiable costs. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train... |
| RCGSC | $/Start | Resource Category Generic Startup Cost—The Resource Category Generic Startup Cost cap for the category of the Resource, according to Section 4.4.9.2.3, Startup Offer and Minimum-Energy Offer Generic Caps, for the Operating Day. |
| PCRUR r, q, DAM, h | MW | Procured Capacity for Reg-Up from Resource per Resource per QSE per hour in DAM—The Regulation Up (Reg-Up) capacity quantity awarded to QSE q in the DAM for Resource r for the hour h. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MCPCRU DAM, h | $/MW per hour | Market Clearing Price for Capacity for Reg-Up per hour in DAM—The DAM MCPC for Reg-Up for the hour h. |
| PCRDR r, q, DAM, h | MW | Procured Capacity for Reg-Down from Resource per Resource per QSE per hour in DAM—The Regulation Down (Reg-Down) capacity quantity awarded to QSE q in the DAM for Resource r for the hour h. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MCPCRD DAM, h | $/MW per hour | Market Clearing Price for Capacity for Reg-Down per hour in DAM—The DAM MCPC for Reg-Down for the hour h. |
| PCFRRSU r, q, DAM, h | MW | Procured Capacity for FRRS-Up from Resource per Resource per QSE per hour in DAM—The FRRS-Up capacity quantity awarded to QSE q in the DAM for Resource r for the hour h. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MCPCFRRSU DAM, h | $/MW per hour | Market Clearing Price for Capacity for FRRS-Up per hour in DAM—The DAM MCPC for FRRS-Up for the hour h. |
| PCFRRSD r, q, DAM, h | MW | Procured Capacity for FRRS-Down from Resource per Resource per QSE per hour in DAM—The FRRS-Down capacity quantity awarded to QSE q in the DAM for Resource r for the hour h. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MCPCFRRSD DAM, h | $/MW per hour | Market Clearing Price for Capacity for FRRS-Down per hour in DAM—The DAM MCPC for FRRS-Down for the hour h. |
| MCPCPFRS DAM, h | $/MW per hour | Market Clearing Price for Capacity for Primary Frequency Response Service (PFRS) in DAM—The DAM MCPC for PFRS for the hour h. |
| PCPFRSR r, q,DAM, h | MW | Procured Capacity for Primary Frequency Response Service from Resource per Resource per QSE in DAM—The PFRS capacity quantity awarded to QSE q in the DAM for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MCPCFFRS DAM,h | $/MW per hour | Market Clearing Price for Capacity for Fast Frequency Response Service (FFRS) in DAM—The DAM MCPC for FFRS for the hour h. |
| PCFFRSR r, q,DAM, h | MW | Procured Capacity for Fast Frequency Response Service from Resource per Resource per QSE in DAM—The FFRS capacity quantity awarded to QSE q in the DAM for Resource r for the hour h. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MCPCCRS DAM, h | $/MW per hour | Market Clearing Price for Capacity for Contingency Reserve Service (CRS) in DAM—The DAM MCPC for CRS for the hour h. |
| PCCRSR r, q, DAM,h | MW | Procured Capacity for Contingency Reserve Service from Resource per Resource per QSE in DAM—The CRS capacity quantity awarded to QSE q in the DAM for Resource r for the hour h. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MCPCSRS DAM,h | $/MW per hour | Market Clearing Price for Capacity for Supplemental Reserve Service (SRS) in DAM—The DAM MCPC for SRS for the hour h. |
| PCSRSR r, q, DAM,h | MW | Procured Capacity for Supplemental Reserve Service from Resource per Resource per QSE in DAM—The SRS capacity quantity awarded to QSE q in the DAM for Resource r for the hour h. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| DASUO q, p, r | $/start | Day-Ahead Startup Offer per QSE per Settlement Point per Resource—The Startup Offer included in the Three-Part Supply Offer submitted in the DAM associated with Resource r at Resource Node p represented by QSE q, for the first hour of the DAM-commitment period. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| AGRRATIO q, p, r | none | Aggregate Generation Resource Ratio per QSE per Settlement Point per Aggregate Generation Resource—A value which represents the ratio of the maximum number of generators online in an hour, as indicated by telemetry, compared to the total number of generators registered to the AGR and used in the approved verifiable cost for the AGR. The value is only applicable if the Resource is an AGR. |
| AGRMAXON q, p, r | none | Aggregate Generation Resource Maximum Online per QSE per Settlement Point per Aggregate Generation Resource—The maximum number of generators online during an hour, as indicated by telemetry. The value is only applicable if the Resource is an AGR. |
| AGRTOT q, p, r | none | Aggregate Generation Resource Total per QSE per Settlement Point per Aggregate Generation Resource—The total number of generators registered to the AGR and used in the approved verifiable cost for the AGR. The value is only applicable if the Resource is an AGR. |
| DAMEO q, p, r, h | $/MWh | Day-Ahead Minimum-Energy Offer per QSE per Settlement Point per Resource per hour—The Minimum-Energy Offer included in the Three-Part Supply Offer submitted in the DAM associated with Resource r at Resource Node p represented by QSE q, for the hour h. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| DALSL q, p, r, h | MW | Day-Ahead Low Sustained Limit per QSE per Settlement Point per Resource per hourThe Low Sustained Limit (LSL) of Resource r at Resource Node p represented by QSE q, for the hour h as seen in the 1000 Day-Ahead snapshot. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| DAAIEC q, p, r h | $/MWh | Day-Ahead Average Incremental Energy Cost per QSE per Settlement Point per Resource per hourThe average incremental energy cost, calculated according to the Energy Offer Curve capped by the generic energy price, for the output levels between the DAESR and the LSL of Resource r at Resource Node p represented by QSE q, for the hour h. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| q | none | A QSE. |
| p | none | A Resource Node Settlement Point. |
| r | none | A DAM-committed Generation Resource. |
| h | none | An hour in the DAM-commitment period. |
| c | none | A contiguous block of DAM-committed hours. |
| afterCCGR | none | The Combined Cycle Generation Resource to which a Combined Cycle Train transitions. |
| beforeCCGR | none | The Combined Cycle Generation Resource from which a Combined Cycle Train transitions. |

(9)	The calculation of the Day-Ahead Average Incremental Energy Cost for each Resource for each hour is illustrated with the picture below, where Pcap is the Energy Offer Curve Cap.  The method to calculate such cost is described in Section 4.6.5, Calculation of “Average Incremental Energy Cost” (AIEC).

$/

MWh

DASPP

P cap

P3

P2

P1

Q (P1) 	Q (P2)	   Q (P3)	Q (P cap)	        Q cleared	MW

[LSL]				     [DAESR]

Energy Offer Curve

The area under the capped Energy Offer Curve equals (DAAIEC * (DAESR – LSL))

(10)	The total of the Day-Ahead Make-Whole Payments to each QSE for non-RMR Generation Resources for a given hour is calculated as follows:

DAMWAMTQSETOT q	=	DAMWAMT q, p, r

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| DAMWAMTQSETOT q | $ | Day-Ahead Make-Whole Payment QSE Total per QSEThe total of the Day-Ahead Make-Whole Payments to QSE q for the DAM-committed non-RMR Generation Resources represented by this QSE for the hour. |
| DAMWAMT q, p, r | $ | Day-Ahead Make-Whole Payment per QSE per Settlement Point per ResourceThe payment to QSE q to make-whole the Startup Cost and energy cost of Resource r committed in the DAM at Resource Node p for the hour. When a Combined Cycle Generation Resource is committed in the DAM, payment is made to the Combined Cycle Train for the DAM-committed Combined Cycle Generation Resource. |
| q | none | A QSE. |
| p | none | A Settlement Point. |
| r | none | A DAM-committed non-RMR Generation Resource. |

Q (P1) 	Q (P2)	   Q (P3)	Q (P cap)	        Q cleared	MW

[LSL]				     [DAESR]

Energy Offer Curve

The area under the capped Energy Offer Curve equals (DAAIEC * (DAESR – LSL))

(11)	The total of the Day-Ahead Make-Whole RMR Revenue for each QSE for RMR Units for a given hour is calculated as follows:

DAMWRMRREVQSETOT q	=	DAMWRMRREV q, p, r

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| DAMWRMRREVQSETOT q | $ | Day-Ahead Make-Whole RMR Revenue QSE Total per QSEThe total of the Day-Ahead Make-Whole Revenue calculated for QSE q for DAM-committed RMR Units represented by this QSE for the hour. |
| DAMWRMRREV q, p, r, | $ | Day-Ahead Make-Whole RMR Revenue per QSE per Settlement Point per RMR Resource per hour—The revenue calculated but not paid to QSE q to make-whole the Startup Cost and energy cost of the RMR Resource r committed in the DAM at Resource Node p for the hour. When a Combined Cycle Generation Resource that is an RMR Resource is committed in the DAM, revenue is calculated for the Combined Cycle |
| q | none | A QSE. |
| p | none | A Settlement Point. |
| r | none | A DAM-committed RMR Unit. |

- 4.6.4.1.1	Regulation Up Service (Reg-Up) Payment

ERCOT shall pay each QSE whose Ancillary Service Offers to provide Reg-Up to ERCOT were cleared in the DAM, for each hour as follows:

PCRUAMT q	=	(-1) * (MCPCRU DAM * PCRU q + MCPCFRRSU DAM * PCFRRSU q)

Where:

PCRU q		=PCRUR r, q, DAM

PCFRRSU q	=ΣrPCFRRSUR r, q, DAM

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| PCRUAMT q | $ | Procured Capacity for Reg-Up Amount per QSE in DAM—The DAM Reg-Up payment for QSE q for the hour. |
| PCFRRSU q | MW | Procured Capacity for FRRS-Up per QSE in DAM—The total FRRS-Up Service capacity quantity awarded to QSE q in the DAM for all the Resources represented by this QSE for the hour. |
| PCRU q | MW | Procured Capacity for Reg-Up per QSE in DAM—The total Reg-Up capacity quantity awarded to QSE q in the DAM for all the Resources represented by this QSE for the hour. |
| PCFRRSUR r, q, DAM | MW | Procured Capacity for FRRS-Up from Resource per Resource per QSE in DAM—The FRRS-Up capacity quantity awarded to QSE q in the DAM for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| PCRUR r, q, DAM | MW | Procured Capacity for Reg-Up from Resource per Resource per QSE in DAM—The Reg-Up capacity quantity awarded to QSE q in the DAM for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MCPCFRRSU DAM | $/MW per hour | Market Clearing Price for Capacity for FRRS-Up in DAM—The DAM MCPC for FRRS-Up for the hour. |
| MCPCRU DAM | $/MW per hour | Market Clearing Price for Capacity for Reg-Up in DAM—The DAM MCPC for Reg-Up for the hour. |
| r | none | A Resource. |
| q | none | A QSE. |

- 4.6.4.1.2	Regulation Down Service (Reg-Down) Payment

ERCOT shall pay each QSE whose Ancillary Service Offers to provide Reg-Down to ERCOT were cleared in the DAM, for each hour as follows:

PCRDAMT q	=	(-1) * (MCPCRD DAM * PCRD q + MCPCFRRSD DAM * PCFRRSD q)

Where:

PCRD q		=PCRDR r, q, DAM

PCFRRSD q	=ΣrPCFRRSDR r, q, DAM

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| PCRDAMT q | $ | Procured Capacity for Reg-Down Amount per QSE in DAM—The DAM Reg-Down payment for QSE q for the hour. |
| PCFRRSD q | MW | Procured Capacity for FRRS-Down per QSE in DAM—The total FRRS-Down Service capacity quantity awarded to QSE q in the DAM for all the Resources represented by this QSE for the hour. |
| PCRD q | MW | Procured Capacity for Reg-Down per QSE in DAM—The total Reg-Down capacity quantity awarded to QSE q in the DAM for all the Resources represented by this QSE for the hour. |
| PCFRRSDR r, q, DAM | MW | Procured Capacity for FRRS-Down from Resource per Resource per QSE in DAM—The FRRS-Down capacity quantity awarded to QSE q in the DAM for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| PCRDR r, q, DAM | MW | Procured Capacity for Reg-Down from Resource per Resource per QSE in DAM—The Reg-Down capacity quantity awarded to QSE q in the DAM for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MCPCFRRSD DAM | $/MW per hour | Market Clearing Price for Capacity for FRRS-Down in DAM—The DAM MCPC for FRRS-Down for the hour. |
| MCPCRD DAM | $/MW per hour | Market Clearing Price for Capacity for Reg-Down in DAM—The DAM MCPC for Reg-Down for the hour. |
| r | none | A Resource. |
| q | none | A QSE. |

Σr

4.6.4.1.3	Primary Frequency Response Service (PFRS) Payment

ERCOT shall pay each QSE whose Ancillary Service Offers to provide PFRS to ERCOT were cleared in the DAM, for each hour as follows:

PCPFRSAMT q	=	(-1) * MCPCPFRS DAM * PCPFRS q

Where:

PCPFRS q		=ΣrPCPFRSR r, q, DAM

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| PCPFRSAMT q | $ | Procured Capacity for PFRS Amount per QSE in DAM—The DAM PFRS payment for QSE q for the hour. |
| PCPFRS q | MW | Procured Capacity for PFRS per QSE in DAM—The total PFRS capacity quantity awarded to QSE q in the DAM for all the Resources represented by this QSE for the hour. |
| PCPFRSR r, q, DAM | MW | Procured Capacity for PFRS from Resource per Resource per QSE in DAM—The PFRS capacity quantity awarded to QSE q in the DAM for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MCPCPFRS DAM | $/MW per hour | Market Clearing Price for Capacity for PFRS in DAM—The DAM MCPC for PFRS for the hour. |
| r | none | A Resource. |
| q | none | A QSE. |

Σr

4.6.4.1.4	Fast Frequency Response Service (FFRS) Payment

ERCOT shall pay each QSE whose Ancillary Service Offers to provide FFRS to ERCOT were cleared in the DAM, for each hour as follows:

PCFFRSAMT q	=	(-1) * MCPCFFRS DAM * PCFFRS q

Where:

PCFFRS q		=ΣrPCFFRSR r, q, DAM

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| PCFFRSAMT q | $ | Procured Capacity for FFRS Amount per QSE in DAM—The DAM FFRS payment for QSE q for the hour. |
| PCFFRS q | MW | Procured Capacity for FFRs per QSE in DAM—The total FFRS capacity quantity awarded to QSE q in the DAM for all the Resources represented by this QSE for the hour. |
| PCFFRSR r, q, DAM | MW | Procured Capacity for FFRS from Resource per Resource per QSE in DAM—The FFRS capacity quantity awarded to QSE q in the DAM for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MCPCFFRS DAM | $/MW per hour | Market Clearing Price for Capacity for FFRS in DAM—The DAM MCPC for FFRS for the hour. |
| r | none | A Resource. |
| q | none | A QSE. |

4.6.4.1.5	Contingency Reserve Service (CRS) Payment

ERCOT shall pay each QSE whose Ancillary Service Offers to provide CRS to ERCOT were cleared in the DAM, for each hour as follows:

PCCRSAMT q	=	(-1) * MCPCCRS DAM * PCCRS q

Where:

PCCRS q		=ΣrPCCRSR r, q, DAM

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| PCCRSAMT q | $ | Procured Capacity for CRS Amount per QSE in DAM—The DAM CRS payment for QSE q for the hour. |
| PCCRS q | MW | Procured Capacity for CRS per QSE in DAM—The total CRS capacity quantity awarded to QSE q in the DAM for all the Resources represented by this QSE for the hour. |
| PCCRSR r, q, DAM | MW | Procured Capacity for CRS from Resource per Resource per QSE in DAM—The CRS capacity quantity awarded to QSE q in the DAM for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MCPCCRS DAM | $/MW per hour | Market Clearing Price for Capacity for CRS in DAM—The DAM MCPC for CRS for the hour. |
| r | none | A Resource. |
| q | none | A QSE. |

4.6.4.1.6	Supplemental Reserve Service (SRS) Payment

ERCOT shall pay each QSE whose Ancillary Service Offers to provide SRS to ERCOT were cleared in the DAM, for each hour as follows:

PCSRSAMT q	=	(-1) * MCPCSRS DAM * PCSRS q

Where:

PCSRS q		=ΣrPCSRSR r, q, DAM

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| PCSRSAMT q | $ | Procured Capacity for SRS Amount per QSE in DAM—The DAM SRS payment for QSE q for the hour. |
| PCSRS q | MW | Procured Capacity for SRS per QSE in DAM—The total SRS capacity quantity awarded to QSE q in the DAM for all the Resources represented by this QSE for the hour. |
| PCSRSR r, q, DAM | MW | Procured Capacity for SRS from Resource per Resource per QSE in DAM—The SRS capacity quantity awarded to QSE q in the DAM for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| MCPCSRS DAM | $/MW per hour | Market Clearing Price for Capacity for SRS in DAM—The DAM MCPC for SRS for the hour. |
| r | none | A Resource. |
| q | none | A QSE. |

4.6.4.2.1	Regulation Up Service (Reg-Up) Charge

Each QSE shall pay to ERCOT a Reg-Up charge for each hour as follows:

DARUAMT q	=	DARUPR * DARUQ q

Where:

DARUPR	= 	(-1) * PCRUAMTTOT / DARUQTOT

PCRUAMTTOT =	ΣqPCRUAMT q

DARUQTOT	=	ΣqDARUQ q

DARUQ q	=	DARUO q – DASARUQ q – ERFRRSUP * DASAFRRSUPQ q

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| DARUAMT q | $ | Day-Ahead Reg-Up Amount per QSE—QSE q’s share of the DAM cost for Reg-Up, for the hour. |
| DARUPR | $/MW per hour | Day-Ahead Reg-Up Price—The Day-Ahead Reg-Up price for the hour. |
| DARUQ q | MW | Day-Ahead Reg-Up Quantity per QSE—The portion of QSE q’s Day-Ahead Ancillary Service Obligation that is not self-arranged, for the hour. |
| ERFRRSUP | none | Equivalency Ratio for FRRS-Up—The equivalency ratio between Reg-Up and FRRS-Up, for the hour. |
| PCRUAMTTOT | $ | Procured Capacity for Reg-Up Amount Total in DAM—The total of the DAM Reg-Up payments for all QSEs for the hour. |
| PCRUAMT q | $ | Procured Capacity for Reg-Up Amount per QSE in DAM—The DAM Reg-Up payment for QSE q for the hour. |
| DARUQTOT | MW | Day-Ahead Reg-Up Quantity Total—The sum of every QSE’s portion of its Day-Ahead Ancillary Service Obligation that is not self-arranged, for the hour. |
| DARUO q | MW | Day-Ahead Reg-Up Obligation per QSE—The Reg-Up capacity obligation for QSE q for the DAM for the hour. |
| DASAFRRSUPQ q | MW | Day-Ahead Self-Arranged FRRS-Up Quantity per QSE—The self-arranged FRRS-Up quantity submitted by QSE q before 1000 in the Day-Ahead. |
| DASARUQ q | MW | Day-Ahead Self-Arranged Reg-Up Quantity per QSE—The self-arranged Reg-Up quantity submitted by QSE q before 1000 in the Day-Ahead. |
| q | none | A QSE. |

4.6.4.2.2	Regulation Down Service (Reg-Down) Charge

Each QSE shall pay to ERCOT a Reg-Down charge for each hour as follows:

DARDAMT q	=	DARDPR * DARDQ q

Where:

DARDPR	= 	(-1) * PCRDAMTTOT / DARDQTOT

PCRDAMTTOT	=		ΣqPCRDAMT q

DARDQTOT	=	ΣqDARDQ q

DARDQ q	=	DARDO q – DASARDQ q – ERFRRSDN * DASAFRRSDNQ q

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| DARDAMT q | $ | Day-Ahead Reg-Down Amount per QSE—QSE q’s share of the DAM cost for Reg-Down, for the hour. |
| DARDPR | $/MW per hour | Day-Ahead Reg-Down Price—The Day-Ahead Reg-Down price for the hour. |
| DARDQ q | MW | Day-Ahead Reg-Down Quantity per QSE—The portion of QSE q’s Day-Ahead Ancillary Service Obligation that is not self-arranged, for the hour. |
| ERFRRSDN | none | Equivalency Ratio for FRRS-Down—The equivalency ratio between Reg-Down and FRRS-Down, for the hour. |
| PCRDAMTTOT | $ | Procured Capacity for Reg-Down Amount Total in DAM—The total of the DAM Reg-Down payments for all QSEs for the hour. |
| PCRDAMT q | $ | Procured Capacity for Reg-Down Amount per QSE in DAM—The DAM Reg-Down payment for QSE q for the hour. |
| DARDQTOT | MW | Day-Ahead Reg-Down Quantity Total—The sum of every QSE’s portion of its Day-Ahead Ancillary Service Obligation that is not self-arranged, for the hour. |
| DARDO q | MW | Day-Ahead Reg-Down Obligation per QSE—The Reg-Down capacity obligation for QSE q for the DAM for the hour. |
| DASAFRRSDNQ q | MW | Day-Ahead Self-Arranged FRRS-Down Quantity per QSE—The self-arranged FRRS-Down quantity submitted by QSE q before 1000 in the Day-Ahead. |
| DASARDQ q | MW | Day-Ahead Self-Arranged Reg-Down Quantity per QSE—The Self-Arranged Reg-Down Quantity submitted by QSE q before 1000 in the Day-Ahead. |
| q | none | A QSE. |

Σq

Σq

4.6.4.2.3	Primary Frequency Response Service (PFRS) Charge

Each QSE shall pay to ERCOT a PFRS charge for each hour as follows:

DAPFRSAMT q	=	DAPFRSPR * DAPFRSQ q

Where:

DAPFRSPR	= 	(-1) * PCPFRSAMTTOT / DAPFRSQTOT

PCPFRSAMTTOT		=	ΣqPCPFRSAMT q

DAPFRSQTOT	=	ΣqDAPFRSQ q

DAPFRSQ q	=	DAPFRSO q – DASAPFRSQ q

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| DAPFRSAMT q | $ | Day-Ahead PFRS Amount per QSE—QSE q’s share of the DAM cost for PFRS, for the hour. |
| DAPFRSPR | $/MW per hour | Day-Ahead PFRS Price—The Day-Ahead PFRS price for the hour. |
| DAPFRSQ q | MW | Day-Ahead PFRS Quantity per QSE—The portion of QSE q’s Day-Ahead PFRS Ancillary Service Obligation that is not self-arranged, for the hour. |
| PCPFRSAMTTOT | $ | Procured Capacity for PFRS Amount Total in DAM—The total of the DAM PFRS payments for all QSEs for the hour. |
| PCPFRSAMT q | $ | Procured Capacity for PFRS Amount per QSE for DAM—The DAM PFRS payment for QSE q for the hour. |
| DAPFRSQTOT | MW | Day-Ahead PFRS Quantity Total—The sum of every QSE’s portion of its Day-Ahead PFRS Ancillary Service Obligation that is not self-arranged, for the hour. |
| DAPFRSO q | MW | Day-Ahead PFRS Obligation per QSE—The PFRS capacity obligation for QSE q for the DAM for the hour. |
| DASAPFRSQ q | MW | Day-Ahead Self-Arranged PFRS Quantity per QSE—The self-arranged PFRS quantity submitted by QSE q before 1000 in the Day-Ahead. |
| q | none | A QSE. |

Σq

Σq

4.6.4.2.4	 Fast Frequency Response Service (FFRS) Charge

Each QSE shall pay to ERCOT an FFRS charge for each hour as follows:

DAFFRSAMT q	=	DAFFRSPR * DAFFRSQ q

Where:

DAFFRSPR	= 	(-1) * PCFFRSAMTTOT / DAFFRSQTOT

PCFFRSAMTTOT		=	ΣqPCFFRSAMT q

DAFFRSQTOT	=	ΣqDAFFRSQ q

DAFFRSQ q	=	DAFFRSO q – DASAFFRSQ q

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| DAFFRSAMT q | $ | Day-Ahead FFRS Amount per QSE—QSE q’s share of the DAM cost for FFRS, for the hour. |
| DAFFRSPR | $/MW per hour | Day-Ahead FFRS Price—The Day-Ahead FFRS price for the hour. |
| DAFFRSQ q | MW | Day-Ahead FFRS Quantity per QSE—The portion of QSE q’s Day-Ahead FFRS Ancillary Service Obligation that is not self-arranged, for the hour. |
| PCFFRSAMTTOT | $ | Procured Capacity for FFRS Amount Total in DAM—The total of the DAM FFRS payments for all QSEs for the hour. |
| PCFFRSAMT q | $ | Procured Capacity for FFRS Amount per QSE for DAM—The DAM FFRS payment for QSE q for the hour. |
| DAFFRSQTOT | MW | Day-Ahead FFRS Quantity Total—The sum of every QSE’s portion of its Day-Ahead FFRS Ancillary Service Obligation that is not self-arranged, for the hour. |
| DAFFRSO q | MW | Day-Ahead FFRS Obligation per QSE—The FFRS capacity obligation for QSE q for the DAM for the hour. |
| DASAFFRSQ q | MW | Day-Ahead Self-Arranged FFRS Quantity per QSE—The self-arranged FFRS quantity submitted by QSE q before 1000 in the Day-Ahead. |
| q | none | A QSE. |

4.6.4.2.5	 Contingency Reserve Service (CRS) Charge

Each QSE shall pay to ERCOT a CRS charge for each hour as follows:

DACRSAMT q	=	DACRSPR * DACRSQ q

Where:

DACRSPR	= 	(-1) * PCCRSAMTTOT / DACRSQTOT

PCCRSAMTTOT		=	ΣqPCCRSAMT q

DACRSQTOT	=	ΣqDACRSQ q

DACRSQ q	=	DACRSO q – DASACRSQ q

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| DACRSAMT q | $ | Day-Ahead CRS Amount per QSE—QSE q’s share of the DAM cost for CRS, for the hour. |
| DACRSPR | $/MW per hour | Day-Ahead CRS Price—The Day-Ahead CRS price for the hour. |
| DACRSQ q | MW | Day-Ahead CRS Quantity per QSE—The portion of QSE q’s Day-Ahead CRS Ancillary Service Obligation that is not self-arranged, for the hour. |
| PCCRSAMTTOT | $ | Procured Capacity for CRS Amount Total in DAM—The total of the DAM CRS payments for all QSEs for the hour. |
| PCCRSAMT q | $ | Procured Capacity for CRS Amount per QSE for DAM—The DAM CRS payment for QSE q for the hour. |
| DACRSQTOT | MW | Day-Ahead CRS Quantity Total—The sum of every QSE’s portion of its Day-Ahead CRS Ancillary Service Obligation that is not self-arranged, for the hour. |
| DACRSO q | MW | Day-Ahead CRS Obligation per QSE—The CRS capacity obligation for QSE q for the DAM for the hour. |
| DASACRSQ q | MW | Day-Ahead Self-Arranged CRS Quantity per QSE—The self-arranged CRS quantity submitted by QSE q before 1000 in the Day-Ahead. |
| q | none | A QSE. |

4.6.4.2.6	 Supplemental Reserve Service (SRS) Charge

Each QSE shall pay to ERCOT an SRS charge for each hour as follows:

DASRSAMT q	=	DASRSPR * DASRSQ q

Where:

DASRSPR	= 	(-1) * PCSRSAMTTOT / DASRSQTOT

PCSRSAMTTOT		=	ΣqPCSRSAMT q

DASRSQTOT	=	ΣqDASRSQ q

DASRSQ q	=	DASRSO q – DASASRSQ q

The above variables are defined as follows:

| Variable | Unit | Definition |
| --- | --- | --- |
| DASRSAMT q | $ | Day-Ahead SRS Amount per QSE—QSE q’s share of the DAM cost for SRS, for the hour. |
| DASRSPR | $/MW per hour | Day-Ahead SRS Price—The Day-Ahead SRS price for the hour. |
| DASRSQ q | MW | Day-Ahead SRS Quantity per QSE—The portion of QSE q’s Day-Ahead SRS Ancillary Service Obligation that is not self-arranged, for the hour. |
| PCSRSAMTTOT | $ | Procured Capacity for SRS Amount Total in DAM—The total of the DAM SRS payments for all QSEs for the hour. |
| PCSRSAMT q | $ | Procured Capacity for SRS Amount per QSE for DAM—The DAM SRS payment for QSE q for the hour. |
| DASRSQTOT | MW | Day-Ahead SRS Quantity Total—The sum of every QSE’s portion of its Day-Ahead SRS Ancillary Service Obligation that is not self-arranged, for the hour. |
| DASRSO q | MW | Day-Ahead SRS Obligation per QSE—The SRS capacity obligation for QSE q for the DAM for the hour. |
| DASASRSQ q | MW | Day-Ahead Self-Arranged SRS Quantity per QSE—The self-arranged SRS quantity submitted by QSE q before 1000 in the Day-Ahead. |
| q | none | A QSE. |

6.1	Introduction

(1)	This Section addresses the following components: the Adjustment Period and Real-Time Operations, including Emergency Operations.

(2)	The Adjustment Period provides each Qualified Scheduling Entity (QSE) the opportunity to adjust its trades, Self-Schedules, and Resource commitments as more accurate information becomes available under Section 6.4, Adjustment Period.  During the Adjustment Period, ERCOT continues to evaluate system sufficiency and security by use of Hour-Ahead Reliability Unit Commitment (RUC) processes, as described in Section 5, Transmission Security Analysis and Reliability Unit Commitment.  Under certain conditions during the Adjustment Period, ERCOT may also open one or more Supplemental Ancillary Service Markets (SASMs), as described in Section 6.4.9.2, Supplemental Ancillary Services Market.

(3)	During Real-Time operations, ERCOT dispatches Resources under normal system conditions and behavior based on economics and reliability to match system Load with On-Line generation while observing Resource and transmission constraints. The Security-Constrained Economic Dispatch (SCED) process produces Base Points for Resources. ERCOT uses the Base Points from the SCED process and uses the deployment of Ancillary Services described in Section 3.17, Ancillary Service Capacity Products, to control frequency and solve potential reliability issues.

(4)	Under Emergency Conditions, as described in Section 6.5.9, Emergency Operations, ERCOT may implement manual procedures and must keep the Market Participants informed of the status of the system.

(5)	Real-Time energy settlements use Real-Time Settlement Point Prices that are calculated for Resource Nodes, Load Zones, and Hubs for a 15-minute Settlement Interval, using the Locational Marginal Prices (LMPs) from all of the executions of SCED in the Settlement Interval.  In contrast, the Day-Ahead Market (DAM) energy settlements will use DAM Settlement Point Prices that are calculated for Resource Nodes, Load Zones, and Hubs for a one-hour Settlement Interval.

(6)	To the extent that the ERCOT CEO or designee determines that Market Participant activities have produced an outcome inconsistent with the efficient operation of the ERCOT-administered markets as defined in subsection (c)(2) of P.U.C. Subst. R. 25.503, Oversight of Wholesale Market Participants, ERCOT may prohibit the activity by Notice for a period beginning on the date of the Notice and ending no later than 45 days after the date of the Notice.  ERCOT may issue subsequent Notices on the same activity.  The ERCOT CEO may deem any Nodal Protocol Revision Request (NPRR) designed to correct the activity or issues affecting the activity as Urgent pursuant to Section 21.5, Urgent Nodal Protocol Revision Requests.

- 6.4.9.2	Supplemental Ancillary Services Market

(1)	During the Adjustment Period, ERCOT may procure additional Ancillary Services described in Section 3.17, Ancillary Service Capacity Products, for the reasons, and in the amounts, specified in Section 6.4.9.1, Evaluation and Maintenance of Ancillary Service Capacity Sufficiency, using a SASM.

(2)	ERCOT shall allow QSEs to request to modify their Ancillary Service positions through a reconfiguration SASM.  The reconfiguration SASM is executed at 0900 daily.  This SASM allows QSEs to potentially change their Ancillary Service Supply Responsibility from hour ending 1300 through hour ending 2400 of the current Operating Day.  QSEs attempt to reduce their Ancillary Service Supply Responsibility through the reconfiguration SASM by submitting less Ancillary Service capacity in their Resource’s COPs than their Ancillary Service Supply Responsibility.  The difference between the Ancillary Service Supply Responsibility and the COP Ancillary Service capacity is the reconfiguration amount that is procured by the reconfiguration SASM.  The QSE must also have valid Ancillary Service Offers of an amount equal to or greater than their requested reconfiguration amount.  The reconfiguration SASM shall not be executed if there are not enough offers to procure the Ancillary Service reconfiguration amount.

(3)	The SASM process for acquiring more Ancillary Service capacity or an Ancillary Service reconfiguration must use the following timelines:

(a)	For Ancillary Service capacity related to ERCOT desired increases, for replacement of Ancillary Service capacity related to undeliverability or for failure of a QSE to provide one or more Ancillary Services, ERCOT shall send a notice at time X to all QSEs of the SASM.  Time X may be any time not less than two hours before the start of the Operating Hour for which the additional Ancillary Services capacity is required.

| SASM Process | QSE Activities: | ERCOT Activities: |
| --- | --- | --- |
| Time = X |  | Notify all QSEs of intent to procure Ancillary Services. Notify QSEs of any additional Ancillary Service Obligation, allocated to each LSE and aggregated to the QSE level. |
| Time = X plus 30 minutes | May submit additional Self-Arranged Ancillary Service Quantities limited to the additional Ancillary Services Obligation of the QSE and Ancillary Service Offers. | Determine the amount of Ancillary Services to be procured. |
| Time = X plus 35 minutes |  | Execute SASM. |
| Time = X plus 45 minutes |  | Notify QSEs with awards of results. Post the quantities and MCPCs of Ancillary Services bought in the SASM. |
| Time = X plus 60 minutes | Submit updated COP with updated Ancillary Service Resource Responsibility. | Validate COPs for Ancillary Service Resource Responsibility. |

(b)	For an Ancillary Services reconfiguration, ERCOT shall execute a SASM at 0900 (time E), for hour ending 1300 through hour ending 2400 of the current Operating Day.

| SASM Process | QSE Activities: | ERCOT Activities: |
| --- | --- | --- |
| Time = E – 15 minutes | QSEs nominate quantities of Ancillary Services that shall be included in the reconfiguration SASM by submitting COPs with less Ancillary Service capacity than their Ancillary Service Supply Responsibility and submitting Ancillary Service Offers to cover the difference between the Ancillary Service Supply Responsibility and COP Ancillary Service capacity. | ERCOT sets the quantities of Ancillary Services to be procured in the SASM equal to the difference between total Ancillary Service Supply Responsibility and total COP Ancillary Service capacity. |
| Time = E |  | Execute SASM for hour ending 1300 through hour ending 2400 of the current Operating Day. |
| Time = E plus 15 minutes |  | Notify QSEs with awards of results. Post the quantities and MCPCs of Ancillary Services bought in the SASM. |
| Time = E plus 30 minutes | Submit updated COP with updated Ancillary Service Resource Responsibility. | Validate COPs for Ancillary Service Resource Responsibility. |

(4)	Each QSE that is awarded capacity in a SASM is paid the SASM MCPC for the quantity it is awarded.

(5)	For purpose of Settlement, the reduction to the Ancillary Service Supply Responsibility is considered a failure quantity and each QSE that has their Ancillary Service Supply Responsibility reduced by a reconfiguration SASM is charged in accordance with Sections 6.7.2, Charges for Ancillary Service Capacity Replaced Due to Failure to Provide, and 6.7.3, Adjustments to Cost Allocations for Ancillary Services Procurement.  QSEs participating in reconfiguration SASMs are not subject to performance metrics for “failure to provide” amounts until the end of the Adjustment Period for each hour cleared in the reconfiguration SASM.

(6)	ERCOT shall allocate additional Ancillary Service Obligations to QSEs using the same percentages as the original Day-Ahead allocation of Ancillary Service Obligations.

6.5.1.2	Centralized Dispatch

(1)	ERCOT shall centrally Dispatch Resources and Transmission Facilities under these Protocols, including deploying energy by establishing Base Points, and Emergency Base Points, and by deploying Ancillary Services as described in Section 3.17, Ancillary Service Capacity Products to ensure operational security.

(2)	ERCOT shall verify that either an Energy Offer Curve providing prices for the Resource between its High Sustained Limit (HSL) and Low Sustained Limit (LSL) or an Output Schedule has been submitted for each On-Line Resource an hour before the end of the Adjustment Period for the upcoming Operating Hour.  ERCOT shall notify Qualified Scheduling Entities (QSEs) that have not submitted an Output Schedule or Energy Offer Curve through the Market Information System (MIS) Certified Area.

(3)	ERCOT is the regional security coordinator for the ERCOT Region and is responsible for all regional security coordination as defined in the NERC Operating Manual and applicable ERCOT operating manuals or Operating Guides.

(4)	ERCOT may only issue Dispatch Instructions for the Real-Time operation of Transmission Facilities to a Transmission Service Provider (TSP), for the Real-Time operation of distribution facilities to a Distribution Service Provider (DSP), or for a Resource to the QSE that represents it.

(5)	ERCOT shall post shift schedules on the MIS Secure Area.

- 6.5.5.2	Operational Data Requirements

(1)	ERCOT shall use Operating Period data to monitor and control the reliability of the ERCOT Transmission Grid and shall use it in network analysis software to predict the short-term reliability of the ERCOT Transmission Grid.  Each TSP, at its own expense, may obtain that Operating Period data from ERCOT or directly from QSEs.

(2)	A QSE representing a Generation Resource connected to Transmission Facilities or distribution facilities shall provide the following Real-Time telemetry data to ERCOT for each Generation Resource.  ERCOT shall make that data available, in accordance with ERCOT Protocols, NERC Reliability Standards, and Governmental Authority requirements, to requesting TSPs and DSPs operating within ERCOT.  Such data must be provided to the requesting TSP or DSP at the requesting TSP’s or DSP’s expense, including:

(a)	Net real power (in MW) as measured by installed power metering or as calculated in accordance with the Operating Guides based on metered gross real power and conversion constants determined by the Resource Entity and provided to ERCOT through the Resource Registration process.  Net real power represents the actual generation of a Resource for all real power dispatch purposes, including use in Security-Constrained Economic Dispatch (SCED), determination of the High Ancillary Service Limit (HASL), High Dispatch Limit (HDL), Low Dispatch Limit (LDL) and Low Ancillary Service Limit (LASL), and is consistent with telemetered HSL, LSL and Non-Frequency Responsive Capacity (NFRC);

(b)	Gross real power (in MW) as measured by installed power metering or as calculated in accordance with the Operating Guides based on metered real power, which may include Supervisory Control and Data Acquisition (SCADA) metering, and conversions constants determined by the Resource Entity and provided to ERCOT through the Resource Registration process;

(c)	Gross Reactive Power (in Megavolt-Amperes reactive (MVAr));

(d)	Net Reactive Power (in MVAr);

(e)	Power to standby transformers serving plant auxiliary Load;

(f)	Status of switching devices in the plant switchyard not monitored by the TSP or DSP affecting flows on the ERCOT Transmission Grid;

(g)	Any data mutually agreed to by ERCOT and the QSE to adequately manage system reliability;

(h)	Generation Resource breaker and switch status;

(i)	HSL, which for Combined Cycle Generation Resources shall:

(i)	Reflect the HSL of the current operating configuration; and

(ii)	When providing PFRS, reflect updates to HSL as needed to be consistent with Resource performance limitations of PFRS provision;

(j)	NFRC currently available (unloaded) and included in the HSL of the Combined Cycle Generation Resource’s current configuration;

(k)	High Emergency Limit (HEL), under Section 6.5.9.2, Failure of the SCED Process;

(l)	Low Emergency Limit (LEL), under Section 6.5.9.2;

(m)	LSL;

(n)	Configuration identification for Combined Cycle Generation Resources;

(o)	Ancillary Service Schedule for each quantity of FFRS, Primary Frequency Response Service (PFRS), CRS, and SRS which is equal to the Ancillary Service Resource Responsibility minus the amount of Ancillary Service deployment;

(p)	Ancillary Service Resource Responsibility for each quantity of FFRS, PFRS, Regulation Up Service (Reg-Up), Regulation Down Service (Reg-Down), CRS, and SRS.  The sum of Ancillary Service Resource Responsibility for all Resources represented by a QSE is equal to the Ancillary Service Supply Responsibility for that QSE;

[NPRR524: Replace paragraph (2)(p)above with the following upon implementation of a manual workaround:] (p) Ancillary Service Resource Responsibility for each quantity of FFRS, PFRS, Regulation Up Service (Reg-Up), Regulation Down Service (Reg-Down), CRS, and SRS. The sum of Ancillary Service Resource Responsibility for all Resources represented by a QSE is equal to the Ancillary Service Supply Responsibility for that QSE.

(q)	Reg-Up and Reg-Down participation factors represent how a QSE is planning to deploy the Ancillary Service energy on a percentage basis to specific qualified Resource(s).  The Reg-Up and Reg-Down participation factors for a Resource providing Fast Responding Regulation Up Service (FRRS-Up) or Fast Responding Regulation Down Service (FRRS-Down) shall be zero; and

(r)	The designated Master QSE of a Generation Resource that has been split to function as two or more Split Generation Resources shall provide Real-Time telemetry for items (a), (b), (c), (d), (e), (g), and (h) above, PSS and AVR status for the total Generation Resource in addition to the Split Generation Resource the Master QSE represents.

(3)	For each Wind-powered Generation Resource (WGR), the QSE shall set the HSL equal to the current net output capability of the facility.  The net output capability should consider the net real power of the WGR, turbine availability, weather conditions, and whether the WGR net output is being affected by compliance with a SCED Dispatch Instruction.

[NPRR588: Replace paragraph (3) above with the following upon system implementation:] (3) For each Intermittent Renewable Resource (IRR), the QSE shall set the HSL equal to the current net output capability of the facility. The net output capability should consider the net real power of the IRR generation equipment, IRR generation equipment availability, weather conditions, and whether the IRR net output is being affected by compliance with a SCED Dispatch Instruction.

(4)	For each Aggregate Generation Resource (AGR), the QSE shall telemeter the number of its generators online.

(5)	A QSE representing a Load Resource connected to Transmission Facilities or distribution facilities shall provide the following Real-Time data to ERCOT for each Load Resource and ERCOT shall make the data available, in accordance with ERCOT Protocols, NERC standards and policies, and Governmental Authority requirements, to the Load Resource’s host TSP or DSP at the TSP’s or DSP’s expense.  The Load Resource’s net real power consumption, Low Power Consumption (LPC) and Maximum Power Consumption (MPC) shall be telemetered to ERCOT using a positive (+) sign convention:

(a)	Load Resource net real power consumption (in MW);

(b)	Any data mutually agreed to by ERCOT and the QSE to adequately manage system reliability;

(c)	Load Resource breaker status;

(d)	LPC (in MW);

(e)	MPC (in MW);

(f)	Ancillary Service Schedule (in MW) for each quantity of FFRS, PFRS, CRS, and SRS, which is equal to the Ancillary Service Resource Responsibility minus the amount of Ancillary Service deployment;

(g)	Ancillary Service Resource Responsibility (in MW) for each quantity of PFRS, Reg-Up, Reg-Down, CRS, and SRS for Controllable Load Resources;

(h)	Ancillary Service Resource Responsibility (in MW) for each quantity of FFRS, CRS, and SRS for all Load Resources, excluding Controllable Load Resources;

(i)	The status of the high-set under-frequency relay, if required for qualification;

(j)	For a Controllable Load Resource providing any Ancillary Service, the Scheduled Power Consumption that represents zero Ancillary Service deployments;

(k)	For a single-site Controllable Load Resource with registered maximum Demand response capacity of ten MW or greater, net Reactive Power (in MVAr);

(l)	Resource Status (Resource Status shall be ONRL if high-set under-frequency relay is active);

(m)	Reg-Up and Reg-Down services participation factor, which represents how a QSE is planning to deploy the Ancillary Service energy on a percentage basis to specific qualified Resource(s).  The Reg-Up and Reg-Down services participation factors for a Resource providing FRRS-Up or FRRS-Down shall be zero; and

(n)	For a Controllable Load Resource providing any Ancillary Service, the “Scheduled Power Consumption Plus Two Hours,” representing the QSE’s forecast of the Controllable Load Resource’s instantaneous power consumption that represents zero Ancillary Service deployments for a point two hours in the future.

(6)	A QSE with Resources used in SCED shall provide communications equipment to receive ERCOT-telemetered control deployments.

(7)	A QSE providing any Regulation Service shall provide telemetry indicating the appropriate status of Resources providing Reg-Up or Reg-Down, including status indicating whether the Resource is temporarily blocked from receiving Reg-Up and/or Reg-Down deployments from the QSE.  This temporary blocking will be indicated by the enabling of the Raise Block Status and/or Lower Block Status telemetry points.

(a)	Raise Block Status and Lower Block Status are telemetry points used in transient unit conditions to communicate to ERCOT that a Resource’s ability to adjust its output has been unexpectedly impaired.

(b)	When one or both of the telemetry points are enabled for a Resource, ERCOT will cease using the regulation capacity assigned to that Resource for Ancillary Service deployment.

(c)	This hiatus of deployment will not excuse the Resource’s obligation to provide the Ancillary Services for which it has been committed.

(d)	These telemetry points shall only be utilized during unforeseen transient unit conditions such as plant equipment failures.  Raise Block Status and Lower Block Status shall only be enabled until the Resource operator has time to update the Resource limits and Ancillary Service telemetry to reflect the problem.

(e)	The Resource limits and Ancillary Service telemetry shall be updated as soon as practicable.  Raise Block Status and Lower Block Status will then be disabled.

(8)	Real-Time data for reliability purposes must be accurate to within three percent.  This telemetry may be provided from relaying accuracy instrumentation transformers.

(9)	Each QSE shall report the current configuration of combined-cycle Resources that it represents to ERCOT.

(10)	The telemetered Resource Status for a Combined Cycle Generation Resource may only be assigned a Resource Status of OFFAS if no generation units within that Combined Cycle Generation Resource are On-Line.

(11)	A QSE representing Combined Cycle Generation Resources shall provide ERCOT with the possible operating configurations for each power block with accompanying limits.  Combined Cycle Train power augmentation methods may be included as part of one or more of the registered Combined Cycle Generation Resource configurations.  Power augmentation methods may include:

(a)	Combustion turbine inlet air cooling methods;

(b)	Duct firing;

(c)	Other ways of temporarily increasing the output of Combined Cycle Generation Resources; and

(d)	For Qualifying Facilities (QFs), an LSL that represents the minimum energy available for Dispatch by SCED, in MW, from the Combined Cycle Generation Resource based on the minimum stable steam delivery to the thermal host plus a justifiable reliability margin that accounts for changes in ambient conditions.

[NPRR568: Insert paragraphs (12), (13), and (14) below upon Phase 2 system implementation:] (12) Each QSE qualified to provide OFF10 capacity shall accurately report the current availability of On-Line (OFF10) reserve capacity for each Resource it represents to ERCOT through Real-Time telemetry. (a) For On-Line Resources and Quick Start Generation Resources (QSGRs) that are available for deployment by SCED, the values provided shall only include capacity that has been tested by ERCOT to be available in the appropriate time frame and is not already captured in the telemetered HSL or telemetered OFF30 capacity of the Resource. (b) For Off-Line Resources, the OFF10 capacity provided shall only include capacity that has been tested by ERCOT to be available within ten minutes and is not already captured in the telemetered OFF30 capacity of the Resource. (c) ERCOT shall validate during the qualification process that the telemetered OFF10 capacity is viable in ten minutes. The telemetered OFF10 capacity shall be capped at the OFF10 MW quantities qualified pursuant to Section 8.1.1.2.1.6, OFF10 Reserve Qualification, or tested pursuant to Section 8.1.1.2, General Capacity Testing Requirements. (13) Each QSE qualified to provide OFF30 capacity shall accurately report the current availability of Off-Line (OFF30) reserve capacity of Resources it represents to ERCOT through Real-Time telemetry. (a) For On-Line Resources and QSGRs that are available for deployment by SCED, the values provided shall only include capacity that has been tested by ERCOT to be available in the appropriate time frame and is not already captured in the telemetered HSL or telemetered OFF10 capacity of the Resource. (b) For Off-Line Resources, the OFF30 capacity provided shall only include capacity that has been tested by ERCOT to be available in the appropriate time frame and is not already captured in the telemetered OFF10 capacity of the Resource. (c) ERCOT shall validate during the qualification process that the telemetered OFF30 capacity is viable in 30 minutes. The telemetered OFF30 shall be capped at the OFF30 MW quantities qualified pursuant to Section 8.1.1.2.1.7, OFF30 Reserve Qualification, or tested pursuant to Section 8.1.1.2. (14) A QSE representing a Resource that is capable of storing energy and releasing that energy at a later time to generate electric energy as both a Load Resource and a Generation Resource is expected to manage the state of charge of the Resource in order to accurately report the HSL, the amount of capacity that can be provided simultaneously from both the Generation Resource and the Load Resource through OFF10 and OFF30, and the net real power consumption data to ERCOT.

- 6.5.7.1.10	Network Security Analysis Processor and Security Violation Alarm

(1)	Using the input provided by the State Estimator, ERCOT shall use the NSA processor to perform analysis of all contingencies in the active list.  For each contingency, ERCOT shall use the NSA processor to monitor the elements for limit violations.  ERCOT shall use the NSA processor to verify Electrical Bus voltage limits to be within a percentage tolerance as outlined in the Operating Guides.  Contingency security violations for transmission lines and transformers occur if:

(a)	The predicted post-contingency MVA exceeds 100% of the Emergency Rating after consideration of Dynamic Ratings; and

(b)	A RAP or SPS is not defined allowing relief within the time allowed by the security criteria as defined in Operating Guide Section 2.2.2, Security Criteria.

(2)	When the NSA processor notifies ERCOT of a security violation, ERCOT shall immediately:

(a)	Initiate the process described in Section 6.5.7.1.11, Transmission Network and Power Balance Constraint Management;

(b)	Seek to determine what unforeseen change in system condition has arisen that has resulted in the security violation, especially those that were 125% or greater of the Emergency Rating for a single SCED interval or greater than 100% of the Emergency Rating for a duration of 30 minutes or more; and

(c)	Where possible, seek to reverse the action (e.g. initiating a transmission clearance that the system was not properly pre-dispatched for) that has led to a security violation until further preventative action(s) can be taken.

(3)	If SCED does not resolve a transmission security violation, ERCOT shall attempt to relieve the security violation by:

(a)	Confirming that pre-determined RAPs are properly modeled in the system;

(b)	Instructing Resources to follow Base Points from SCED if those Resources are not already doing so;

(c)	Instructing Resources to update the Resources Status in the COP from ONTEST to ON in order to provide more capacity to SCED;

(d)	Deploying Resource-Specific CRS and/or SRS;

(e)	Committing additional Generation Resources through the Reliability Unit Commitment (RUC) process;

(f)	Removing conflicting non-cascading constraints from the SCED process;

(g)	Re-Dispatching generation by over-riding HDLs and LDLs;

(h)	Instructing TSPs to utilize Reactive Power devices to manage voltage; and

(i)	If all other mechanisms have failed, ERCOT may authorize the expedited use of a Temporary Outage Action Plan (TOAP) or Mitigation Plan.

(4)	NSA must be capable of analyzing contingencies, including the effects of SPSs and RAPs.  The NSA must fully integrate the evaluation and deployment of SPSs and RAPs and notify the ERCOT Operator of the application of these SPSs and RAPs to the solution.

(5)	The Real-Time NSA may employ the use of appropriate ranking and other screening techniques to further reduce computation time by executing one or two iterations of the contingency study to gauge its impact and discard further study if the estimated result is inconsequential.

(6)	ERCOT shall report monthly:

(a)	All security violations that were 125% or greater of the Emergency Rating for a single SCED interval or greater than 100% of the Emergency Rating for a duration of 30 minutes or more during the prior reporting month and the number of occurrences and congestion cost associated with each of the constraints causing the security violations on a rolling 12 month basis.

(b)	Operating conditions on the ERCOT System that contributed to each transmission security violation reported in paragraph (6)(a) above.  Analysis should be made to understand the root cause and what steps could be taken to avoid a recurrence in the future.

6.5.7.2	Resource Limit Calculator

(1)	ERCOT shall calculate the HASL, LASL, SURAMP, SDRAMP, HDL and LDL within four seconds after a change of the Resource-specific attributes provided as part of the QSE’s SCADA telemetry under Section 6.5.5.2, Operational Data Requirements.  The formulas described below define which Resource-specific attributes must be used to calculate each Resource limit.  The Resource limits are used as inputs into both the SCED process and the Ancillary Service Capacity Monitor as described in Section 6.5.7.6, Load Frequency Control.  These Resource limits help ensure that the deployments produced by the SCED and Load Frequency Control (LFC) processes will respect the commitment of a Resource to provide Ancillary Services as well as individual Resource physical limitations.

(2)	The figures below illustrate how the Resource Limit Calculator determines the Resource limits for Generation and Load Resources:

Generation Resources:

LSL

HSL

Time

LSL

-

LASL

-

HASL

-

Generation

Increase

Generation

Decrease

Services

Provided: Reg

Down

Provided: Reg Up,

Responsive, Non-SpinPFRS, FFRS, CRS,

SRS

Current

Telemetry

HDL

LDL

Ramp

Rate

5 Minutes

Generation

Quantity

Offer Curve Generation

LSL

HSL

-

-

-

Generation

Increase

Generation

Decrease

Ramp

Rate

5 Minutes

-

0

-

-

Generation

Increase

Generation

Decrease

Ramp

Rate

5 Minutes

Ancillary

Load Resources:

Time

LSL = LPC -

LASL  -

HASL  -

Ancillary Services Provided: Reg-Down

Current Load

Telemetry

HDL

LDL

5-30 Minutes

Load

Quantity

Bid Curve Load

LSL/LPC

HSL/MPC

0

Increasing

Consumption

Decreasing

Consumption

Ramp

Rate

Ancillary Services Provided: Reg-Up, PFRS, FFRS, CRS, SRSRRS, Non-Spin

HSL = MPC -

Normal Load

Fluctuation

(3)	For Generation Resources, HASL is calculated as follows:

HASL	=	Max (LASL, (HSLTELEM – (FFRSSTELEM + PFRSSTELEM + RUSTELEM + CRSSTELEM + SRSSTELEM)))

| Variable | Description |
| --- | --- |
| HASL | High Ancillary Service Limit. |
| HSLTELEM | High Sustained Limit provided via telemetry – per Section 6.5.5.2. |
| LASL | Low Ancillary Service Limit. |
| FFRSSTELEM | FFRS Ancillary Service Schedule provided by telemetry. |
| PFRSSTELEM | PFRS Ancillary Service Schedule provided by telemetry. |
| CRSSTELEM | CRS Ancillary Service Schedule provided by telemetry |
| SRSSTELEM | SRS Ancillary Service Schedule provided by telemetry |
| RUSTELEM | Reg-Up Ancillary Service Resource Responsibility designation provided by telemetry. |

(4)	For Generation Resources, LASL is calculated as follows:

LASL	=	LSLTELEM + RDSTELEM

| Variable | Description |
| --- | --- |
| LASL | Low Ancillary Service Limit. |
| LSLTELEM | Low Sustained Limit provided via telemetry. |
| RDSTELEM | Reg-Down Ancillary Service Resource Responsibility designation provided by telemetry. |

(5)	For each Generation Resource, the SURAMP is calculated as follows:

SURAMP	=	RAMPRATE – (RUSTELEM * REGP / 5)

| Variable | Description |
| --- | --- |
| SURAMP | SCED Up Ramp Rate. |
| RAMPRATE | Resource’s Normal Ramp Rate up, as telemetered by the QSE, when CRS and/or PFRS Ancillary Service Schedule is not released to SCED by ERCOT or when the subject Resource does not have any PFRS or CRS Ancillary Service Resource Responsibility. Resource’s Emergency Ramp Rate up, as telemetered by the QSE, when CRS and/or PFRS Ancillary Service Schedule is released to SCED by ERCOT. |
| RUSTELEM | Reg-Up Ancillary Service Resource Responsibility designation provided by telemetry. |
| REGP | Percentage of Regulation Service for which ramp rate will be reserved in Real-Time. The value will be between one and zero. Market Participants will be notified of the change in this value. |

(6)	For each Generation Resource, the SDRAMP is calculated as follows:

SDRAMP	=	NORMRAMP – (RDSTELEM * REGP / 5)

| Variable | Description |
| --- | --- |
| SDRAMP | SCED Down Ramp Rate. |
| NORMRAMP | Normal Ramp Rate down, as telemetered by the QSE. |
| RDSTELEM | Reg-Down Ancillary Service Resource Responsibility designation by Resource provided via telemetry. |
| REGP | Percentage of Regulation Service for which ramp rate will be reserved in Real-Time. The value will be between one and zero. Market Participants will be notified of the change in this value. |

(7)	For Generation Resources, HDL is calculated as follows:

(a)	If the telemetered Resource Status is SHUTDOWN, then

HDL	=	POWERTELEM – (SDRAMP * 5)

(b)	If the telemetered Resource Status is any status code specified in item (5)(b)(i) of Section 3.9.1, Current Operating Plan (COP) Criteria, other than SHUTDOWN, then

HDL	=	Min (POWERTELEM + (SURAMP * 5), HASL)

| Variable | Description |
| --- | --- |
| HDL | High Dispatch Limit. |
| POWERTELEM | Gross or net real power provided via telemetry. |
| SURAMP | SCED Up Ramp Rate. |
| SDRAMP | SCED Down Ramp Rate. |
| HASL | High Ancillary Service Limit – definition provided in Section 2, Definitions and Acronyms. |

(8)	For Generation Resources, LDL is calculated as follows:

(a)	If the telemetered Resource Status is STARTUP, then

LDL	=	POWERTELEM + (SURAMP * 5)

(b)	If the telemetered Resource Status is any status code specified in item (5)(b)(i) of Section 3.9.1 other than STARTUP, then

LDL	=	Max (POWERTELEM - (SDRAMP * 5), LASL)

| Variable | Description |
| --- | --- |
| LDL | Low Dispatch Limit. |
| POWERTELEM | Gross or net real power provided via telemetry. |
| SDRAMP | SCED Down Ramp Rate. |
| LASL | Low Ancillary Service Limit – definition provided in Section 2. |

(9)	For Load Resources, HASL is calculated as follows:

HASL	=	Max (LPCTELEM, (MPCTELEM – RDSTELEM))

| Variable | Description |
| --- | --- |
| HASL | High Ancillary Service Limit. |
| LPCTELEM | Low Power Consumption provided via telemetry. |
| MPCTELEM | Maximum Power Consumption provided via telemetry. |
| RDSTELEM | Reg-Down Ancillary Service Resource Responsibility designation provided by telemetry. |

(10)	For Load Resources, LASL is calculated as follows:

LASL	=	Min (HASL, (LPCTELEM + (PFRSSTELEM + FFRSTELEM + RUSTELEM + CRSSTELEM + SRSSTELEM)))

| Variable | Description |
| --- | --- |
| LASL | Low Ancillary Service Limit. |
| HASL | High Ancillary Service Limit. |
| LPCTELEM | Low Power Consumption provided via telemetry. |
| PFRSSTELEM | PFRS Ancillary Service Schedule provided by telemetry. |
| CRSSTELEM | CRS Ancillary Service Schedule provided by telemetry |
| SRSSTELEM | SRS Ancillary Service Schedule provided by telemetry |
| RUSTELEM | Reg-Up Ancillary Service Resource Responsibility designation provided by telemetry. |
| FFRSTELEM | FFRS Ancillary Service Schedule provided by telemetry |

(11)	For each Load Resource, the SURAMP is calculated as follows:

SURAMP	=	RAMPRATE – (RUSTELEM * REGP / 5)

| Variable | Description |
| --- | --- |
| SURAMP | SCED Up Ramp Rate. |
| RAMPRATE | Resource’s Normal Ramp Rate up, as telemetered by the QSE, when CRS and/or PFRS Ancillary Service Schedule is not released to SCED by ERCOT, or when the subject Resource does not have any PFRS or CRS Ancillary Service Resource Responsibility. Resource’s Emergency Ramp Rate up, as telemetered by the QSE, when CRS and/or PFRS Ancillary Service Schedule is released to SCED by ERCOT.CRS not depl RRS. |
| RUSTELEM | Reg-Up Ancillary Service Resource Responsibility designation provided by telemetry. |
| REGP | Percentage of Regulation Service for which ramp rate will be reserved in Real-Time. The value will be between one and zero. Market Participants will be notified of the change in this value. |

(12)	For each Load Resource, the SDRAMP is calculated as follows:

SDRAMP	=	NORMRAMP – (RDSTELEM * REGP / 5)

| Variable | Description |
| --- | --- |
| SDRAMP | SCED Down Ramp Rate. |
| NORMRAMP | Normal Ramp Rate down, as telemetered by the QSE. |
| RDSTELEM | Reg-Down Ancillary Service Resource Responsibility designation by Resource provided via telemetry. |
| REGP | Percentage of Regulation Service for which ramp rate will be reserved in Real-Time. The value will be between one and zero. Market Participants will be notified of the change in this value. |

(13)	For Load Resources, HDL is calculated as follows:

HDL	=	Min (POWERTELEM + (SDRAMP * 5), HASL)

| Variable | Description |
| --- | --- |
| HDL | High Dispatch Limit. |
| POWERTELEM | Net real power flow provided via telemetry. |
| SDRAMP | SCED Down Ramp Rate. |
| HASL | High Ancillary Service Limit – definition provided in Section 2. |

(14)	For Load Resources, LDL is calculated as follows:

LDL	=	Max (POWERTELEM - (SURAMP * 5), LASL)

| Variable | Description |
| --- | --- |
| LDL | Low Dispatch Limit. |
| POWERTELEM | Net real power flow provided via telemetry. |
| SURAMP | SCED Up Ramp Rate. |
| LASL | Low Ancillary Service Limit – definition provided in Section 2. |

6.5.7.5	Ancillary Services Capacity Monitor

(1)	ERCOT shall calculate the following every ten seconds and provide Real-Time summaries to ERCOT Operators and all Market Participants using ICCP, giving updates of calculations every ten seconds, and posting on the MIS Public Area, giving updates of calculations every five minutes, which show the Real-Time total system amount of:

(a)	PFRS capacity;

(b)	FFRS1 capacity;

(c)	FFRS2 capacity;

(d)	CRS1 capacity available from On-Line Generation Resources and Controllable Load Resources with Energy Offer Curves;

(e)	CRS1 capacity available from Off-Line Generation Resources;

(f)	CRS1 capacity available from Generation Resources with Output Schedules;

(g)	CRS2 capacity available from Load Resources;

(h)	SRS1 capacity available from Off-Line Generation Resources;

(i)	SRS1 capacity available from On-Line Generation Resources and Controllable Load Resources with Energy Offer Curves;

(j)	SRS1 capacity available from Generation Resources with Output Schedules;

(k)	SRS2 capacity available from Load Resources, excluding Controllable Load Resources; (g)	a

Undeployed Reg-Up and undeployed Reg-Down;

(i)	Available capacity from Controllable Load Resources in the ERCOT System that can be used to decrease Base Points (energy consumption) in SCED;

(n)	Available capacity from Controllable Load Resources in the ERCOT System that can be used to increase Base Points (energy consumption) in SCED;

(o)	Available capacity with Energy Offer Curves in the ERCOT System that can be used to increase Generation Resource Base Points in SCED;

(p)	Available capacity with Energy Offer Curves in the ERCOT System that can be used to decrease Generation Resource Base Points in SCED;

(q)	Available capacity without Energy Offer Curves in the ERCOT System that can be used to increase Generation Resource Base Points in SCED;

(r)	Available capacity without Energy Offer Curves in the ERCOT System that can be used to decrease Generation Resource Base Points in SCED; and

(s)	The ERCOT-wide Physical Responsive Capability (PRC) calculated as follows:

generationresourcei=onlineonlinegenerationAllresourcesPRC1 =			Min(Max((RDF*HSL – Actual Net Telemetered Output)i , 0.0) , 0.2*RDF*HSLi),

generationresourcei=onlineonlinegenerationAllresourceswhere the included On-Line Generation Resources do not include WGRs, nuclear Generation Resources, or Generation Resources with an output less than or equal to 95% of telemetered LSL or with a telemetered status of ONTEST, STARTUP, or SHUTDOWN.

generationresourcei=onlineonlinegenerationAllresources

generationresourcei=onlineonlinegenerationAllresources

PRC2 =	((Hydro-synchronous condenser output)i as qualified by item (9) of Operating Guide Section 2.3.1.2, Additional Operational Details for PFRS Providers))





resources

load

online

All

resource

load

online

i

PRC3 =			(FFRS Schedule MW)i





resources

load

online

All

resource

load

online

i

PRC4 =	Min(Max((LRDF_1*Actual Net Telemetered Consumption – LPC)i, 0.0), (0.2 * LRDF_1 * Actual Net Telemetered Consumption)) from all Controllable Load Resources active in SCED and carrying Ancillary Service Resource Responsibility





resources

load

online

All

resource

load

online

i

PRC5 =	Min(Max((LRDF_2 * Actual Net Telemetered Consumption – LPC)i, 0.0), (0.2 * LRDF_2 * Actual Net Telemetered Consumption)) from all Controllable Load Resources active in SCED and not carrying Ancillary Service Resource Responsibility

PRC =	PRC1 + PRC2 + PRC3 + PRC4 + PRC5

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| PRC1 | MW | Generation On-Line greater than 0 MW |
| PRC2 | MW | Hydro-synchronous condenser output |
| PRC3 | MW | FFRS chedule from Resources providing FFRS |
| PRC4 | MW | Capacity from Controllable Load Resources active in SCED and carrying Ancillary Service Resource Responsibility |
| PRC5 | MW | Capacity from Controllable Load Resources active in SCED and not carrying Ancillary Service Resource Responsibility |
| PRC | MW | Physical Responsive Capability |
| RDF |  | The currently approved Reserve Discount Factor |
| LRDF_1 |  | The currently approved Load Resource Reserve Discount Factor for Controllable Load Resources carrying Ancillary Service Resource Responsibility |
| LRDF_2 |  | The currently approved Load Resource Reserve Discount Factor for Controllable Load Resources not carrying Ancillary Service Resource Responsibility |

[NPRR495 & NPRR573: Replace applicable portions of paragraph (1) above with the following upon system implementation:] (1) ERCOT shall calculate the following every ten seconds and provide Real-Time summaries to ERCOT Operators and all Market Participants using ICCP, giving updates of calculations every ten seconds, and posting on the MIS Public Area, giving updates of calculations every five minutes, which show the Real-Time total system amount of: (a) PFR, FFR, CRS, and SRS capacity available from: (i) Generation Resources; (ii) Load Resources excluding Controllable Load Resources; and (iii) Controllable Load Resources; (b) Ancillary Service Resource Responsibility and Ancillary Service Schedule for PFRS from: (i) Generation Resources; and (ii) Controllable Load Resources; (c) CRS1, derived from telemetered Ancillary Service Resource Responsibility and Ancillary Service Schedule for CRS from: (i) On-Line Generation Resources with Energy Offer Curves; (ii) On-Line Generation Resources with Output Schedules; (iii) Controllable Load Resources; and (iv) Off-Line Generation Resources (d) CRS2, derived from telemetered Ancillary Service Resource Responsibility and Schedule for CRS from all Load Resources, excluding Controllable Load Resources; (e) SRS1, derived from telemetered Ancillary Service Resource Responsibility and Schedule for SRS from (i) On-Line Generation Resources with Energy Offer Curves; (ii) Off-Line Generation Resources; (iii) Controllable Load Resources; (iv) Generation Resources with Output Schedules; (f) SRS2, derived from telemetered Ancillary Service Resource Responsibility and Schedule for SRS from all Load Resources, excluding Controllable Load Resources (g) Undeployed Reg-Up and Reg-Down; (h) Ancillary Service Resource Responsibility for Reg-Up and Reg-Down; (i) Deployed Reg-Up and Reg-Down; (j) Available capacity: (i) With Energy Offer Curves in the ERCOT System that can be used to increase Generation Resource Base Points in SCED; (ii) With Energy Offer Curves in the ERCOT System that can be used to decrease Generation Resource Base Points in SCED; (iii) Without Energy Offer Curves in the ERCOT System that can be used to increase Generation Resource Base Points in SCED; (iv) Without Energy Offer Curves in the ERCOT System that can be used to decrease Generation Resource Base Points in SCED; (v) With RTM Energy Bid curves from available Controllable Load Resources in the ERCOT System that can be used to decrease Base Points (energy consumption) in SCED; and (vi) With RTM Energy Bid curves from available Controllable Load Resources in the ERCOT System that can be used to increase Base Points (energy consumption) in SCED; (k) The ERCOT-wide Physical Responsive Capability (PRC) calculated as follows: (l) Qualified PFRS,FFRS, Reg, CRS and SRS capacity from: (i) Generation Resources; (ii) Load Resources excluding Controllable Load Resources; and generationresourcei=onlineonlinegenerationAllresources(iii) Controllable Load Resources; PRC1 = Min(Max((RDF*HSL – Actual Net Telemetered Output)i , 0.0) , 0.2*RDF*HSLi), where the included On-Line Generation Resources do not include WGRs, nuclear Generation Resources, or Generation Resources with an output less than or equal to 95% of telemetered LSL or with a telemetered status of ONTEST, STARTUP, or SHUTDOWN.   WGRs online All WGRs online i PRC2 = Min(Max((RDFW*HSL – Actual Net Telemetered Output)i , 0.0) , 0.2*RDFW*HSLi), where the included On-Line WGRs only include WGRs that are Primary Frequency Response-capable. generationresourcei=onlineonlinegenerationAllresources generationresourcei=onlineonlinegenerationAllresources PRC3 = ((Hydro-synchronous condenser output)i as qualified by item (9) of Operating Guide Section 2.3.1.2, Additional Operational Details for PFRS Providers))   resources load online All resource load online i PRC4 = (FFRS capacity MW )i   resources load online All resource load online i PRC5 = Min(Max((LRDF_1*Actual Net Telemetered Consumption – LPC)i, 0.0), (0.2 * LRDF_1 * Actual Net Telemetered Consumption)) from all Controllable Load Resources active in SCED and carrying Ancillary Service Resource Responsibility   resources load online All resource load online i PRC6 = Min(Max((LRDF_2 * Actual Net Telemetered Consumption – LPC)i, 0.0), (0.2 * LRDF_2 * Actual Net Telemetered Consumption)) from all Controllable Load Resources active in SCED and not carrying Ancillary Service Resource Responsibility PRC = PRC1 + PRC2 + PRC3+ PRC4 + PRC5 + PRC6 The above variables are defined as follows: Variable; Unit; Description. PRC1; MW; Generation On-Line greater than 0 MW. PRC2; MW; WGRs On-Line greater than 0 MW. PRC3; MW; Hydro-synchronous condenser output. PRC4; MW; FFRS Ancillary Service Schedule from Resources providing FFRS. PRC5; MW; Capacity from Controllable Load Resources active in SCED and carrying Ancillary Service Resource Responsibility. PRC6; MW; Capacity from Controllable Load Resources active in SCED and not carrying Ancillary Service Resource Responsibility. PRC; MW; Physical Responsive Capability. RDF; The currently approved Reserve Discount Factor. RDFW; The currently approved Reserve Discount Factor for WGRs. LRDF_1; The currently approved Load Resource Reserve Discount Factor for Controllable Load Resources carrying Ancillary Service Resource Responsibility. LRDF_2; The currently approved Load Resource Reserve Discount Factor for Controllable Load Resources not carrying Ancillary Service Resource Responsibility.

(2)	Each QSE shall operate Resources providing Ancillary Service capacity to meet its obligations.  If a QSE experiences temporary conditions where its total obligation for providing Ancillary Service cannot be met on the QSE’s Resources, then the QSE may add additional capability from other Resources that it represents.  It adds that capability by changing the Resource Status and updating the Ancillary Service Schedules and Ancillary Services Resource Responsibility of the affected Resources and notifying ERCOT under Section 6.4.9.1, Evaluation and Maintenance of Ancillary Service Capacity Sufficiency.  If the QSE is unable to meet its total obligations to provide committed Ancillary Services capacity, the QSE shall notify ERCOT immediately of the expected duration of the QSE’s inability to meet its obligations.  ERCOT shall determine whether replacement Ancillary Services will be procured to account for the QSE’s shortfall according to Section 6.4.9.1.

(3)	The Load Resource Reserve Discount Factors for Controllable Load Resources (LRDF_1 and LRDF_2) shall be subject to review and approval by TAC and shall be posted to the MIS Public Area no later than three Business Days after TAC approval.

6.5.7.6	Load Frequency Control

The function of LFC is to maintain system frequency without a cost optimization function.  ERCOT shall execute LFC every four seconds to reduce system frequency deviations from scheduled frequency by providing a control signal to each QSE that represents Resources providing Regulation Service and by providing ERCOT’s control signal to release PFRS and CRS1  to SCED.

- 6.5.7.6.1	LFC Process Description

(1)	The LFC system corrects system frequency based on the Area Control Error (ACE) algorithm and Good Utility Practice.

(2)	The ACE algorithm subtracts the actual frequency in Hz from the scheduled system frequency (normally 60 Hz), and multiplies the result by the frequency bias constant of MW/0.1 Hz.  The ACE algorithm then takes that product and subtracts a configurable portion of the sum of the difference between the Updated Desired Base Point and Real-Time net MW output as appropriate.  LFC shall ensure that the total reduction will not exceed the system-wide regulation requirement.  This calculation produces an ACE value, which is a MW-equivalent correction needed to control the actual system frequency to the scheduled system frequency value.

(3)	The LFC module receives inputs from Real-Time telemetry that includes Resource output and actual system frequency.  The LFC uses actual Resource information calculated from SCADA to determine available Resource capacity providing Ancillary Services.

(4)	Based on the ACE MW correction, the LFC issues a set of control signals every four seconds to each QSE providing Regulation and, if required, each QSE providing CRS1 by releasing the capacity to SCED.  Control must be proportional to the QSE’s share of each of the services that it is providing, respecting the QSE’s Resources’ capability to provide regulation control.  Control signals are provided to the QSE using the ICCP data link.  QSEs shall receive an Updated Desired Base Point updated every four seconds by LFC.  ERCOT will provide an Operations Notice of any methodology change to the determination of the Updated Desired Base Point within 60 minutes of the change.

(5)	Each QSE shall allocate its Regulation energy deployment among its Resources to meet a deployment signal, and shall provide ERCOT with the participation factor of each Resource via telemetry in accordance with Section 6.5.7.6.2.1, Deployment of Regulation Service, and Section 6.4.9.1, Evaluation and Maintenance of Ancillary Service Capacity Sufficiency.  A QSE may allocate Regulation Service Ancillary Service Resource Responsibility to any Resource telemetering a Resource Status of ONOPTOUT.  Each QSE’s allocation of Regulation Service to its Resources must be consistent with the telemetry provided under Section 6.5.5.2, Operational Data Requirements.  Each QSE’s allocation of its Regulation energy deployment among its Resources to meet a deployment signal must ensure the participation factors of all its Generation Resources in comparison to all its Controllable Load Resources remains constant.

(6)	If all Reg-Up capacity has been deployed, ERCOT shall use the LFC system to release CRS1 capacity from Generation Resources and Controllable Load Resources to SCED.

(7)	When a QSE deploys CRS1, the QSE shall deploy Resources consistent with the performance criteria for CRS1 in Section 8.1.1.4.4, Contingency Reserve Service Energy Deployment Criteria.

(8)	The inputs for LFC include:

(a)	Actual system frequency;

(b)	Scheduled system frequency;

(c)	Capacity available for Regulation by QSE;

(d)	Telemetered high and low Regulation availability status indications for each Resource available for Regulation deployments for ERCOT information;

(e)	Resource limits calculated by ERCOT as described Section 6.5.7.2, Resource Limit Calculator;

(f)	Resource Regulation participation factor;

(g)	CRS1 Ancillary Service Schedule by QSE;

(h)	ERCOT System frequency bias; and

(i)	Telemetered Resource output.

(9)	If system frequency deviation is greater than an established threshold, ERCOT may issue Dispatch Instructions to those Resources not providing Reg-Up or Reg-Down that have Base Points directionally opposite ACE, to temporarily suspend ramping to their Base Point until frequency deviation returns to zero.

6.5.7.7	Ancillary Services Deployment and Recall

ERCOT may deploy and recall Regulation Service, FFRS, PFRS, CRS and SRS only as prescribed by their respective specific functions to maintain frequency and system security.  ERCOT may not substitute one Ancillary Service for another.

- 6.5.7.7.1	Deployment and Recall of Regulation Service

(1)	ERCOT shall deploy Reg-Up and Reg-Down necessary to maintain ERCOT System frequency to meet NERC Control Area and other Control Area performance criteria as specified in these Protocols and the Operating Guides.

(2)	Reg-Up is a deployment or recall of a deployment referenced to the Resource’s Base Point in response to a change (up or down) in ERCOT System frequency to maintain the target ERCOT System frequency within predetermined limits according to the Operating Guides.

(3)	Reg-Down is a deployment or recall of a deployment referenced to the Resource’s Base Point in response to a change (up or down) in ERCOT System frequency to maintain the target ERCOT System frequency within predetermined limits according to the Operating Guides.

(4)	These requirements also apply to the deployment or recall of a deployment of Reg-Up and Reg-Down:

(a)	Deployment or recall of a deployment must be accomplished through use of an automatic signal from ERCOT to each QSE provider of Reg-Up and Reg-Down.

(b)	ERCOT shall minimize Reg-Up and Reg-Down energy as much as practicable in each SCED cycle.

(c)	ERCOT shall settle energy provided by Reg-Up and Reg-Down at the Resource’s Settlement Point Price.

(d)	ERCOT shall integrate the control signal sent to providers of Reg-Up and shall calculate the amount of energy deployed by Reg-Up in each Settlement Interval.

(e)	ERCOT shall integrate the control signal sent to providers of Reg-Down and shall calculate the amount of energy deployed by Reg-Down in each Settlement Interval.

(f)	ERCOT shall calculate for each LFC cycle the amount of regulation that each Resource is expected to provide at that instant in time.  The expected amount must be averaged over each SCED interval.  The actual generation from telemetry must also be averaged over each SCED interval.

(5)	Every day, ERCOT shall post to the MIS Secure Area the total amount of deployed Reg-Up and Reg-Down energy in each Settlement Interval of the previous day.

(6)	For each Resource providing Reg-Up or Reg-Down, the implied ramp rate in MW per minute is the total amount of Regulation Service awarded divided by five.

(7)	For each Resource providing FRRS-Up or FRRS-Down, the implied ramp rate in MW per minute is such that the total amount of FRRS must be fully available in 60 cycles.

(8)	Each QSE providing Reg-Up or Reg-Down and ERCOT shall meet the deployment performance requirements specified in Section 8, Performance Monitoring.

(9)	ERCOT shall issue Reg-Up and Reg-Down deployment Dispatch Instructions over ICCP.  Those Dispatch Instructions must contain the change in MW output requested of the QSE assuming all Resources are at their Updated Desired Base Point issued by LFC.

6.5.7.7.2	Deployment and Recall of Fast Frequency Response Service

(1)	FFRS is intended to:

(a)	Automatically respond to an under-frequency event as described in paragraph (2) below; and

(b)	Provide energy during the implementation of an EEA;

(2)	Resources shall deploy FFRS to meet NERC Standards and other performance criteria as specified in these Protocols and the Operating Guides, by one or more of the following:

(a)	ERCOT Dispatch Instruction via electronic Messaging System; and

(b)	Automatic action within 30 cycles if frequency remains at or below:

(i)	59.80 Hz, for Resources providing FFRS1; or

(ii)	59.70 Hz, for Resources providing FFRS2.

(3)	Following an FFRS1 deployment, a QSE’s Ancillary Service Supply Responsibility to deliver FFRS1 remains in effect until ERCOT issues a recall instruction or for ten continuous minutes, whichever occurs first.

(4)	Following an automatic FFRS1 deployment a QSE providing FFRS1 must restore its full FFRS1 Ancillary Service Supply Responsibility within 15 minutes after either the receipt of an ERCOT recall instruction or ten continuous minutes of FFRS1 deployment, whichever occurs first.

(5)	Notwithstanding paragraph (4) above, while deployed manually during an EEA, Resources providing FFRS1 shall take all reasonable efforts to avoid energy withdrawals from the ERCOT System.

(6)	Following an FFRS2 deployment, the QSE’s Ancillary Service Supply Responsibility to deliver FFRS2 remains in effect until ERCOT issues a recall instruction or its FFRS2 Ancillary Service Supply Responsibility expires, whichever occurs first.

(7)	A QSE providing FFRS2 must restore its full FFRS2 Ancillary Service Supply Responsibility within 180 minutes of receiving an ERCOT recall instruction.

(8)	Each QSE providing FFRS shall meet the deployment performance requirements specified in Section 8.1.1.4.2, Fast Frequency Response Service Energy Deployment Criteria.

(9)	ERCOT shall recall automatically deployed FFRS1 capacity once system frequency recovers to 59.97 Hz.

(10) 	ERCOT shall recall FFRS2 deployment once PRC is above a pre-defined threshold, as described in the Operating Guides.

6.5.7.7.3	Deployment and Recall of Primary Frequency Response Service

(1)	PFRS is intended to:

(a)	Help arrest and stabilize the frequency within the first few seconds of a significant frequency deviation of the interconnected transmission system;

(b)	Provide energy during the implementation of an EEA.

(2)	A Resource shall, through Governor action, automatically and continuously deploy Primary Frequency Response (PFR) to meet NERC Standards, and other performance criteria as specified in these Protocols and the Operating Guides.

(3)	PFRS may also be manually deployed by ERCOT pursuant to Section 6.5.9, Emergency Operations.

(4)	Each QSE providing PFRS shall meet the deployment performance requirements specified in Section 8.1.1.4.3, Primary Frequency Response Service Energy Deployment Criteria.

- 6.5.7.7.4	Deployment and Recall of Contingency Reserve Service

(1)	CRS is intended to:

(a)	Help restore the frequency to 60 Hz within ten minutes of a significant frequency deviation;

(b)	Provide energy during the implementation of an EEA; and

(c)	Provide backup to Reg-Up.

(2)	ERCOT shall deploy CRS to meet NERC Standards and other performance criteria as specified in these Protocols and the Operating Guides, by one or more of the following:

(a)	Automatic Dispatch Instruction signal to release CRS1 capacity from Generation Resources and  Controllable Load Resources to SCED; and/or

(b)	Dispatch Instruction for deployment of CRS2 energy via electronic Messaging System.

(3)	ERCOT shall deploy CRS1 when frequency drops below 59.91 Hz and available Reg-Up is not sufficient to restore frequency.  The deployment of Off-Line CRS1 must always be 100% of that scheduled on an individual Resource.

(4)	Energy from Resources providing CRS may also be manually deployed by ERCOT pursuant to Section 6.5.9, Emergency Operations.

(5)	ERCOT shall use SCED and SRS as soon as practicable to recover CRS reserves.

(6)	Following a CRS deployment, the QSE’s obligation to deliver CRS remains in effect until ERCOT issues a recall instruction or its CRS obligation expires, whichever occurs first.

(7)	Following a deployment or recall Dispatch Instruction of CRS, a QSE shall adjust the telemetered CRS Ancillary Service Schedule for the Resource providing the service and ERCOT shall adjust the HASL based on the QSE’s telemetered Ancillary Service Schedule for CRS as described in Section 6.5.7.2, Resource Limit Calculator, to account for such deployment.

(8)	For Resources providing CRS1, Base Points include CRS1 energy as well as any other energy dispatched by SCED.  A Resource must be able to be fully dispatched by SCED to its CRS1 Ancillary Service Resource Responsibility within the ten-minute time frame according to its telemetered Emergency Ramp Rate.

(9)	Each QSE providing CRS shall meet the deployment performance requirements specified in Section 8.1.1.4.4, Contingency Reserve Service Energy Deployment Criteria.

(10)	ERCOT shall issue instructions to release CRS1 capacity to SCED over ICCP, and shall issue deployment instructions for CRS2 via Extensible Markup Language (XML).  Such instructions shall contain the MW requested.

(11) 	To the extent that ERCOT deploys a Load Resource that is not a Controllable Load Resource and that has chosen a block deployment option, ERCOT shall either deploy the entire Ancillary Service Resource Responsibility or, if only partial deployment is possible, skip the Load Resource with the block deployment option and proceed to deploy the next available Resource.

(12)	ERCOT shall recall automatically deployed CRS1 capacity once system frequency recovers above 59.97 Hz.

(13)	ERCOT shall recall CRS2 deployment once PRC is above a pre-defined threshold, as described in the Operating Guides.

- 6.5.7.7.5	Supplemental Reserve Service Deployment and Recall

(1)	ERCOT shall deploy SRS based on the TAC-approved SRS deployment procedure.  ERCOT Operators shall implement the deployment procedure when a specified threshold(s) in MW of capability available to SCED to increase generation is reached.  ERCOT Operators may implement the deployment procedure to recover deployed CRS or when other Emergency Conditions exist.  The deployment of Off-Line SRS1 must always be 100% of that scheduled on an individual Resource.

(2)	Once SRS1 capacity from Generation Resources providing SRS1 is deployed, ERCOT shall use SCED to determine the amount of energy to be dispatched from those Resources.

(3)	Off-Line Generation Resources providing SRS1 (OFFAS Resource Status) are required to provide an Energy Offer Curve for use by SCED.

(4)	Controllable Load Resources providing SRS1 shall have an RTM Energy Bid for SCED and shall be capable of being Dispatched to their SRS Responsibility within 30 minutes of a deployment instruction for capacity, using the Resources’ Normal Ramp Rate curve.  An Aggregate Load Resource (ALR) must comply with all requirements in the document titled “Requirements for Aggregate Load Resource Participation in the ERCOT Markets.”

(5)	Off-Line Generation Resources providing SRS1 shall be capable of being Dispatched to their SRS1 Ancillary Service Resource Responsibility within 30 minutes of a deployment instruction.  After receipt of a deployment instruction, the QSE shall reduce the SRS Ancillary Service Schedule for the Resource providing the service by the amount of the deployment.  An Off-Line Generation Resource providing SRS1 shall be brought On-Line with an Energy Offer Curve at an output level greater than or equal to P1 multiplied by LSL, where P1 is defined in the document titled “ERCOT and QSE Operations Business Practices During the Operating Hour.”  These actions must be done within a time frame that would allow SCED to fully Dispatch the Resource’s SRS1 Ancillary Service Resource Responsibility within the 30- minute period using the Resource’s Normal Ramp Rate curve.  The Resource Status indicating that a Generation Resource has come On-Line with an Energy Offer Curve is ON as described in paragraph (5)(b)(i) of Section 3.9.1, Current Operating Plan (COP) Criteria.

(6)	For DSRs providing SRS, on deployment of SRS, the DSR’s QSE shall adjust the Resource’s Output Schedule to reflect the amount of deployment.

(7)	For Resources with Output Schedules providing SRS other than DSRs, on deployment of SRS, ERCOT shall adjust the Resource’s Output Schedule for the remainder of the Operating Period to reflect the amount of deployment.  ERCOT shall notify the QSE representing the Resource of the adjustment through the MIS Certified Area.

(8)	Each QSE providing SRS from an Off-Line Resource shall inform ERCOT of the Resource’s availability using the Resource Status (OFFAS) and SRS Ancillary Service Resource Responsibility for the Operating Hour using telemetry, and shall use the COP to inform ERCOT of OFFAS Resource Status and SRS Ancillary Service Resource Responsibility for hours in the Adjustment Period through the end of the Operating Day.

(9)	ERCOT may deploy SRS at any time in a Settlement Interval.

(10)	ERCOT’s SRS capacity deployment Dispatch Instructions must include:

(a)	The Resource name;

(b)	A MW level of capacity deployment for Generation Resources with Energy Offer Curves, a MW level of energy for Generation Resources with Output Schedules, or a Dispatch Instruction for Load Resources equal to their awarded SRS Ancillary Service Resource Responsibility; and

(c)	The anticipated duration of deployment.

(11)	ERCOT shall provide a signal via ICCP to the QSE of a deployed Generation or Load Resource indicating that its SRS capacity has been deployed.

(12)	ERCOT shall, as part of its TAC-approved SRS deployment procedure, provide for the recall of SRS energy including descriptions of changes to Output Schedules and release of energy obligations from On-Line Resources with Output Schedules and On-Line Resources that were previously Off-Line Resources providing SRS capacity.

(13)	ERCOT shall provide a notification to all QSEs via the MIS Public Area when any SRS capacity is deployed on the ERCOT System showing the time, MW quantity and the anticipated duration of the deployment.

(14)	Each QSE providing SRS shall meet the deployment performance requirements specified in Section 8.1.1.4.5, Supplemental Reserve Service Energy Deployment Criteria.

- 6.5.9.3.3	Watch

(1)	A Watch is the third of four levels of communication issued by ERCOT in anticipation of a possible Emergency Condition.

(2)	ERCOT shall issue a Watch when ERCOT determines that:

(a)	Conditions have developed such that additional Ancillary Services are needed in the current Operating Period;

(b)	There are insufficient Ancillary Services or Energy Offers in the DAM;

(c)	Market-based congestion management techniques embedded in SCED as specified in these Protocols will not be adequate to resolve transmission security violations;

(d)	Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active violations of security criteria as defined in the Operating Guides unless a CMP exists;

(e)	ERCOT varies from timing requirements or omits one or more Day-Ahead or Adjustment Period and Real-Time procedures;

(f)	ERCOT varies from timing requirements or omits one or more scheduling procedures in the Real-Time process; or

(g)	The SCED process fails to reach a solution, whether or not ERCOT is using one of the measures specified in paragraph (3) of Section 6.5.9.2, Failure of the SCED Process.

(3)	With the issuance of a Watch pursuant to paragraph (2)(a) above, ERCOT may exercise its authority to immediately procure

Ancillary Services as described in Section 3.17, Ancillary Service Capacity Products.

(4)	If the actions in paragraph (3) above do not relieve the insufficiency described in paragraph (2)(a) above, then ERCOT may issue Dispatch Instructions to Resources certified to provide the insufficient service, even though there is not an existing Ancillary Service Offer for that Resource.

(5)	If ERCOT issues a Watch because insufficient Ancillary Service Offers were received in the DAM, and if the Watch does not result in sufficient offer and the DAM is executed with insufficient offers, then ERCOT may acquire the insufficient amount of Ancillary Services in the Day-Ahead Reliability Unit Commitment (DRUC) and shall issue Dispatch Instructions to the QSEs for Resources that were RUC-committed to provide Ancillary Services, informing them of the requirement that the Resources be prepared to provide those Ancillary Services.

(6)	ERCOT shall post the Watch message electronically to the MIS Public Area and shall provide verbal notice to all TSPs and QSEs via the Hotline.  Corrective actions identified by ERCOT must be communicated through Dispatch Instructions to all TSPs, DSPs and QSEs required to implement the corrective action.  Each QSE shall immediately notify the Market Participants that it represents of the Watch.  To minimize the effects on the ERCOT System, each TSP or DSP shall identify and prepare to implement actions, including restoration of transmission lines as appropriate and preparing for Load shedding.  ERCOT may instruct TSPs or DSPs to reconfigure ERCOT System elements as necessary to improve the reliability of the ERCOT System.  On notice of a Watch, each QSE, TSP, and DSP shall prepare for an Emergency Condition in case conditions worsen.  ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities.  Requests for this type of information shall be for a time period of no more than seven days from the date of the request.  The specific information that may be requested shall be defined in the Operating Guides.  QSEs representing Resources shall provide the requested information in a timely manner, as defined by ERCOT at the time of the request.

- 6.5.9.4	Energy Emergency Alert

(1)	At times it may be necessary to reduce ERCOT System Demand because of a temporary decrease in available electricity supply.  To provide orderly, predetermined procedures for curtailing Demand during such emergencies, ERCOT shall initiate and coordinate the implementation of the EEA following the steps set forth below in Section 6.5.9.4.2, EEA Levels.

(2)	The goal of the EEA is to provide for maximum possible continuity of service while maintaining the integrity of the ERCOT System to reduce the chance of cascading Outages.

(3)	ERCOT’s operating procedures must meet the following goals:

(a)	Use of market processes to the fullest extent practicable without jeopardizing the reliability of the ERCOT System;

(b)	Use of Ancillary Services and Emergency Response Service (ERS) to the extent permitted by ERCOT System conditions;

(c)	Maximum use of ERCOT System capability;

(d)	Maintenance of station service for nuclear-powered Generation Resources;

(e)	Securing startup power for Generation Resources;

(f)	Operation of Generation Resources during loss of communication with ERCOT; and

(g)	Restoration of service to Loads in the manner defined in the Operating Guides.

(4)	ERCOT is responsible for coordinating with QSEs, TSPs, and DSPs to monitor ERCOT System conditions, initiating the EEA levels, notifying all QSEs, and coordinating the implementation of the EEA levels while maintaining transmission security limits.

(5)	ERCOT, at management’s discretion, may at any time issue an ERCOT-wide appeal through the public news media for voluntary energy conservation.

(6)	During the EEA, ERCOT has the authority to obtain energy from non-ERCOT Control Areas using the DC Ties or by using Block Load Transfers (BLTs) to move load to non-ERCOT Control Areas.  ERCOT maintains the authority to curtail energy schedules flowing into or out of the ERCOT System across the DC Ties in accordance with NERC scheduling guidelines.

(7)	Some of the EEA steps are not applicable if transmission security violations exist.  There may be insufficient time to implement all EEA levels in sequence, however, to the extent practicable, ERCOT shall use Ancillary Services that QSEs have made available in the market to maintain or restore reliability.

(8)	ERCOT may immediately implement EEA Level 3 any time the steady-state system frequency is below 59.8 Hz and shall immediately implement EEA Level 3 any time the steady-state frequency is below 59.5 Hz.

(9)	Percentages for EEA Level 3 Load shedding will be based on the previous year’s TSP peak Loads, as reported to ERCOT, and must be reviewed by ERCOT and modified annually as required.

- 6.5.9.4.1	General Procedures Prior to EEA Operations

Prior to declaring EEA Level 1 detailed in Section 6.5.9.4.2, EEA Levels, ERCOT may perform the following operations consistent with Good Utility Practice:

(a)	Provide Dispatch Instructions to QSEs for specific Resources to operate at an Emergency Base Point to maximize Resource deployment so as to increase PFRS levels on other Resources;

(b)	Commit specific available Resources as necessary that can respond in the timeframe of the emergency.  Such commitments will be settled using the HRUC process;

(c)	Start RMR Units available in the time frame of the emergency.  RMR Units should be loaded to full capability;

(d)	Utilize available Resources providing CRS and SRS as required; and

(e)	ERCOT shall use the PRC to determine the appropriate Emergency Notice and EEA levels.

6.5.9.4.2	EEA Levels

(1)	EEA Level 1 - Maintain a total of 2,300 MW of PRC (Section 6.5.7.5, Ancillary Services Capacity Monitor).

(a)	ERCOT shall:

(i)	Notify the Southwest Power Pool Reliability Coordinator;

(ii)	Request available Generation Resources that can perform within the expected timeframe of the emergency to come On-Line by initiating manual HRUC or through Dispatch Instruction;

(iii)	Use available DC Tie import capacity not already being used;

(iv)	Issue a Dispatch Instruction for Resources to remain On-Line which, before start of emergency, were scheduled to come Off-Line; and

(v)	At ERCOT’s discretion, deploy available contracted ERS-30 via an XML message followed by a VDI to the all-QSE Hotline.  The ERS-30 ramp period shall begin at the completion of the VDI.

(A)	If less than 500 MW of ERS-30 is available for deployment, ERCOT shall deploy it as a single block.

(B)	If the amount of ERS-30 available for deployment equals or exceeds 500 MW, ERCOT, at its discretion, may deploy ERS-30 as a single block or by group designation.  ERCOT shall develop a random selection methodology for determining how to place ERS Resources in ERS-30 into groups, and shall describe the methodology in a document posted to the MIS Public Area.  Prior to the start of an ERS Contract Period for ERS-30, ERCOT shall notify QSEs representing ERS Resources in ERS-30 of their ERS Resources’ group assignments.

(C)	ERS-30 may be deployed at any time in a Settlement Interval.

(D)	Upon deployment, QSEs shall instruct their ERS Resources in ERS-30 to perform at contracted levels consistent with the criteria described in Section 8.1.3.1.4, Event Performance Criteria for Emergency Response Service Resources, until either ERCOT releases the ERS-30 deployment or the ERS-30 Resources have reached their maximum deployment time.

(E)	ERCOT shall notify QSEs of the release of ERS-30 via an XML message followed by VDI to the all-QSE Hotline.  The VDI shall represent the official notice of ERS-30 release.  ERCOT may release ERS-30 as a block or by group designation.

(F)	Upon release, an ERS Resource in ERS-30 shall return to a condition such that it is capable of meeting its ERS performance requirements as soon as practical, but no later than ten hours following the release.

(b)	QSEs shall:

(i)	Ensure COPs and telemetered HSLs are updated and reflect all Resource delays and limitations; and

(ii)	Suspend any ongoing ERCOT required Resource performing testing.

(2)	EEA Level 2 - Maintain system frequency at 60 Hz or maintain a total of 1,750 MW of PRC.

(a)	In addition to the measures associated with EEA Level 1, ERCOT shall take the following steps:

(i)	Instruct TSPs and DSPs or their agents to reduce Customers’ Load by using distribution voltage reduction measures, if deemed beneficial by the TSP, DSP, or their agents.

(ii)	Instruct QSEs to deploy available contracted ERS-10 Resources, all un-deployed ERS-30 and/or deploy FFRS.  ERCOT may deploy ERS-10, ERS-30, or FFRS simultaneously or separately, and in any order.  ERCOT shall issue such Dispatch Instructions in accordance with the deployment methodologies described in paragraphs (iii) and (iv) below and, if deploying ERS-30, the methodologies described in paragraph (1)(a)(v) above.

(iii)	ERCOT shall deploy ERS-10 via an XML message followed by a VDI to the all-QSE Hotline.  The ERS-10 ramp period shall begin at the completion of the VDI.

(A)	If less than 500 MW of ERS-10 is available for deployment, ERCOT shall deploy all ERS-10 Resources as a single block.

(B)	If the amount of ERS-10 available for deployment equals or exceeds 500 MW, ERCOT, at its discretion, may deploy ERS-10 Resources as a single block or by group designation.  ERCOT shall develop a random selection methodology for determining how to place ERS-10 Resources into groups, and shall describe the methodology in a document posted to the MIS Public Area.  Prior to the start of an ERS-10 Contract Period, ERCOT shall notify QSEs representing ERS-10 Resources of their ERS-10 Resources’ group assignments.

(C)	ERS-10 may be deployed at any time in a Settlement Interval.

(D)	Upon deployment, QSEs shall instruct ERS-10 Resources to perform at contracted levels consistent with the criteria described in Section 8.1.3.1.4 until ERCOT releases the ERS-10 deployment or the ERS-10 Resources have reached their maximum deployment times.

(E)	ERCOT shall notify QSEs of the release of ERS-10 via an XML message followed by VDI to the all-QSE Hotline.  The VDI shall represent the official notice of ERS-10 release.  ERCOT may release ERS-10 as a block or by group designation.

(F)	Upon release, an ERS-10 Resource shall return to a condition such that it is capable of meeting its ERS performance requirements as soon as practical, but no later than ten hours following the release.

(iv)	ERCOT shall deploy FFRS in accordance with the following:

(A)	Instruct QSEs to deploy half of the FFRS2  by instructing the QSE representing the specific Load Resource to interrupt Group 1 Load Resources providing FFRS2.  QSEs shall deploy Load Resources according to the group designation and will be given some discretion to deploy additional Load Resources from Group 2 if Load Resource operational considerations require such.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;

(B)	At the discretion of the ERCOT Operator, instruct QSEs to deploy the remaining FFRS2 by instructing the QSE representing the specific Load Resource to interrupt Group 2 Load Resources providing FFRS2 . ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;

(C)	At the discretion of the ERCOT Operator, instruct QSEs to deploy FFRS1.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;

(D)	The ERCOT Operator may deploy both of the groups of Load Resources providing FFRS2 at the same time.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period; and

(E)	ERCOT shall post a list of Load Resources on the MIS Certified Area immediately following the DRUC for each QSE with a Load Resource obligation which may be deployed to interrupt under paragraph (A), Group 1 and paragraph (B), Group 2.  ERCOT shall develop a process for determining which individual Load Resource to place in Group 1 and which to place in Group 2.  ERCOT procedures shall select Group 1 and Group 2 based on a random sampling of individual Load Resources.  At ERCOT’s discretion, ERCOT may deploy all Load Resources at any given time during EEA Level 2.

(v)	Unless a media appeal is already in effect, ERCOT shall issue an appeal through the public news media for voluntary energy conservation.

(vi)	With the approval of the affected non-ERCOT Control Area, TSPs, DSPs, or their agents may implement BLTs, which transfer Load from the ERCOT Control Area to non-ERCOT Control Areas in accordance with BLTs as defined in the Operating Guides.

(b)	Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability.

(3)	EEA Level 3 - Maintain system frequency at 59.8 Hz or greater.

(a)	In addition to measures associated with EEA Levels 1 and 2, ERCOT will direct all TSPs and DSPs or their agents to shed firm Load, in 100 MW blocks, as documented in the Operating Guides in order to maintain a steady state system frequency of 59.8 Hz.

(b)	In addition to measures associated with EEA Levels 1 and 2, TSPs and DSPs or their agents will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens.  Whenever possible, TSPs and DSPs or their agents shall not manually drop Load connected to under-frequency relays during the implementation of the EEA.

- 6.5.9.4.3	Restoration of Market Operations

ERCOT shall continue the EEA until sufficient offers are received and deployed by ERCOT to eliminate the conditions requiring the EEA and normal SCED operations are restored.  After restoring PFRS, FFRS, and CRS, ERCOT shall release ERS Resources and then restore curtailed DC Tie Load.  Intermittent solutions of SCED do not set new LMPs until ERCOT declares that the EEA is no longer needed.

- 6.6.5.1.1	General Generation Resource and Controllable Load Resource Base Point Deviation Charge

(1)	Unless one of the exceptions specified in paragraphs (2) and (3) below applies, ERCOT shall charge a Base Point Deviation Charge for a Resource other than those described in Section 6.6.5.2, IRR Generation Resource Base Point Deviation Charge, and Section 6.6.5.3, Generators Exempt from Deviation Charges, when the telemetered generation of the Generation Resource or telemetered power consumption of the Controllable Load Resource over the 15-minute Settlement Interval is outside the tolerances defined later in this Section 6.6.5.1.1.

(2)	ERCOT may not charge a QSE a Base Point Deviation Charge under paragraph (1) above when both of the following apply:

(a)	The deviation of the Resource over the 15-minute Settlement Interval is in a direction that contributes to frequency corrections that resolve an ERCOT System frequency deviation; and

(b)	The ERCOT System frequency deviation is greater than +/-0.05 Hz at any time during the 15-minute Settlement Interval.

(3)	ERCOT may not charge a QSE a Base Point Deviation Charge under paragraph (1) above for any 15-minute Settlement Interval during which Fast Frequency Response Service (FFRS) or Contingency Reserve Service (CRS) is deployed.

- 6.7.1	Payments for Ancillary Service Capacity Sold in a Supplemental Ancillary Service Market

If a Supplemental Ancillary Services Market (SASM) is executed for one or more Operating Hours for any reason, ERCOT shall pay Qualified Scheduling Entities (QSEs) for their Ancillary Service Offers cleared in the SASM, based on the Market Clearing Price for Capacity (MCPC) for that SASM and that service.  By service and by SASM, the payment to each QSE for a given Operating Hour is calculated as follows:

(a)	For Regulation Up (Reg-Up), if applicable:

RTPCRUAMT q, m	=	(-1) * (MCPCRU m * RTPCRU q, m + MCPCFRRSU m  * RTPCFRRSU q, m)

Where:

RTPCRU q, m	=	PCRUR  q, r, m

RTPCFRRSU q, m	=ΣrPCFRRSUR q, r, m,

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTPCRUAMT q, m | $ | Procured Capacity for Reg-Up Amount by QSE by market—The payment to QSE q for the Ancillary Service Offers cleared in the market m to provide Reg-Up, for the hour. |
| MCPCFRRSU m | $/MW per hour | Market Clearing Price for Capacity for FRRS-Up by market—The MCPC for FRRS-Up from the market m, for the hour. |
| MCPCRU m | $/MW per hour | Market Clearing Price for Capacity for Reg-Up by market—The MCPC for Reg-Up from the market m, for the hour. |
| RTPCFRRSU q, m | MW | Procured Capacity for FRRS-Up by QSE by market—The portion of QSE q’s Ancillary Service Offers cleared in the market m to provide FRRS-Up, for the hour. |
| RTPCRU q, m | MW | Procured Capacity for Reg-Up by QSE by market—The portion of QSE q’s Ancillary Service Offers cleared in the market m to provide Reg-Up, for the hour. |
| PCFRRSUR q, r, m | MW | Procured Capacity for FRRS-Up from Resource per Resource per QSE by market—The FRRS-Up capacity quantity awarded to QSE q in the market m for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| PCRUR q, r, m | MW | Procured Capacity for Reg-Up from Resource per Resource per QSE by market—The Reg-Up capacity quantity awarded to QSE q in the market m for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| m | none | A SASM. |
| q | none | A QSE. |
| r | none | A Generation Resource. |

(b)	For Regulation Down (Reg-Down), if applicable:

RTPCRDAMT q, m	=	(-1) * (MCPCRD m * RTPCRD q, m + MCPCFRRSD m  * RTPCFRRSD q, m)

Where:

RTPCRD q, m	=	PCRDR r, q, m

RTPCFRRSD q, m	=ΣrPCFRRSDR q, r, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTPCRDAMT q, m | $ | Procured Capacity for Reg-Down Amount by QSE by market—The payment to QSE q for the Ancillary Service Offers cleared in the market m to provide Reg-Down, for the hour. |
| MCPCFRRSD m | $/MW per hour | Market Clearing Price for Capacity for FRRS-Down by market—The MCPC for FRRS-Down from the market m, for the hour. |
| MCPCRD m | $/MW per hour | Market Clearing Price for Capacity for Reg-Down by market—The MCPC for Reg-Down from the market m, for the hour. |
| RTPCFRRSD q, m | MW | Procured Capacity for FRRS-Down by QSE by market—The portion of QSE q’s Ancillary Service Offers cleared in the market m to provide FRRS-Down, for the hour. |
| RTPCRD q, m | MW | Procured Capacity for Reg-Down by QSE by market—The portion of QSE q’s Ancillary Service Offers cleared in the market m to provide Reg-Down, for the hour. |
| PCFRRSDR q, r, m | MW | Procured Capacity for FRRS-Down from Resource per Resource per QSE by market—The FRRS-Down capacity quantity awarded to QSE q in the market m for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| PCRDR r, q, m | MW | Procured Capacity for Reg-Down from Resource per Resource per QSE by market—The Reg-Down capacity quantity awarded to QSE q in the market m for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| m | none | A SASM. |
| q | none | A QSE. |
| r | none | A Generation Resource. |

(c)	For Primary Frequency Response Service (PFRS), if applicable:

RTPCPFRSAMT q, m	=	(-1) * MCPCPFRS m * RTPCPFRS q, m

Where:

RTPCPFRS q, m	=	ΣrPCPFRSR r, q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTPCPFRSAMTq, m | $ | Procured Capacity for Primary Frequency Response Service Amount by QSE by market—The payment to QSE q for the Ancillary Service Offers cleared in the market m to provide PFRS, for the hour. |
| MCPCPFRS m | $/MW per hour | Market Clearing Price for Capacity for Primary Frequency Response Service by market—The MCPC for PFRS from the market m, for the hour. |
| RTPCPFRS q, m | MW | Procured Capacity for Primary Frequency Response Service by QSE by market—The portion of QSE q’s Ancillary Service Offers cleared in the market m to provide PFRS, for the hour. |
| PCPFRSR r, q, m | MW | Procured Capacity for Primary Frequency Response Service from Resource per Resource per QSE by market—The PFRS capacity quantity awarded to QSE q in the market m for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| m | none | A SASM. |
| q | none | A QSE. |
| r | none | A Generation Resource. |

(d)	For Fast Frequency Response Service (FFRS), if applicable:

RTPCFFRSAMT q, m	=	(-1) * MCPCFFRS m * RTPCFFRS q, m

Where:

RTPCFFRS q, m	=	ΣrPCFFRSR r, q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTPCFFRSAMTq, m | $ | Procured Capacity for Fast Frequency Response Service Amount by QSE by market—The payment to QSE q for the Ancillary Service Offers cleared in the market m to provide FFRS, for the hour. |
| MCPCFFRS m | $/MW per hour | Market Clearing Price for Capacity for Fast Frequency Response Service by market—The MCPC for FFRS from the market m, for the hour. |
| RTPCFFRS q, m | MW | Procured Capacity for Fast Frequency Response Service by QSE by market—The portion of QSE q’s Ancillary Service Offers cleared in the market m to provide FFRS, for the hour. |
| PCFFRSR r, q, m | MW | Procured Capacity for Fast Frequency Response Service from Resource per Resource per QSE by market—The FFRS capacity quantity awarded to QSE q in the market m for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| m | none | A SASM. |
| q | none | A QSE. |
| r | none | A Generation Resource. |

(e)	For Contingency Reserve Service (CRS), if applicable:

RTPCCRSAMT q, m	=	(-1) * MCPCCRS m * RTPCCRS q, m

Where:

RTPCCRS q, m	=	ΣrPCCRSR r, q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTPCCRSAMTq, m | $ | Procured Capacity for Contingency Reserve Service Amount by QSE by market—The payment to QSE q for the Ancillary Service Offers cleared in the market m to provide CRS, for the hour. |
| MCPCCRS m | $/MW per hour | Market Clearing Price for Capacity for Contingency Reserve Service by market—The MCPC for CRS from the market m, for the hour. |
| RTPCCRS q, m | MW | Procured Capacity for Contingency Reserve Service by QSE by market—The portion of QSE q’s Ancillary Service Offers cleared in the market m to provide CRS, for the hour. |
| PCCRSR r, q, m | MW | Procured Capacity for Contingency Reserve Service from Resource per Resource per QSE by market—The CRS capacity quantity awarded to QSE q in the market m for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| m | none | A SASM. |
| q | none | A QSE. |
| r | none | A Generation Resource. |

(f)	For Supplemental Reserve Service (SRS), if applicable:

RTPCSRSAMT q, m	=	(-1) * MCPCSRS m * RTPCSRS q, m

Where:

RTPCSRS q, m	=	ΣrPCSRSR r, q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTPCSRSAMTq, m | $ | Procured Capacity for Supplemental Reserve Service Amount by QSE by market—The payment to QSE q for the Ancillary Service Offers cleared in the market m to provide SRS, for the hour. |
| MCPCSRS m | $/MW per hour | Market Clearing Price for Capacity for Supplemental Reserve Service by market—The MCPC for SRS from the market m, for the hour. |
| RTPCSRS q, m | MW | Procured Capacity for Supplemental Reserve Service by QSE by market—The portion of QSE q’s Ancillary Service Offers cleared in the market m to provide SRS, for the hour. |
| PCSRSR r, q, m | MW | Procured Capacity for Supplemental Reserve Service from Resource per Resource per QSE by market—The SRS capacity quantity awarded to QSE q in the market m for Resource r for the hour. Where for a Combined Cycle Train, the Resource r is a Combined Cycle Generation Resource within the Combined Cycle Train. |
| m | none | A SASM. |
| q | none | A QSE. |
| r | none | A Generation Resource. |

The above variables are defined as follows:

|  | $/MW per hour |  |
| --- | --- | --- |

- 6.7.2	Charges for Ancillary Service Capacity Replaced Due to Failure to Provide

A charge to each QSE that fails on its Ancillary Service Supply Responsibility, whether or not a SASM is executed due to its failure to supply, and to each QSE that has its Ancillary Service Supply Responsibility reduced by a reconfiguration SASM, is calculated based on the greatest of the MCPC in the Day-Ahead Market (DAM) or any SASM for the same Operating Hour.  By service, the charge to each QSE for a given Operating Hour is calculated as follows:

(a)	For Reg-Up, if applicable:

RUFQAMT q	=	((MCPCRU m) * RUFQ q ) + (Maxm(MCPCFRRSU m) * FRRSUFQ q)

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RUFQAMT q | $ | Reg-Up Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for Reg-Up, for the hour. |
| MCPCFRRSU m | $/MW per hour | Market Clearing Price for Capacity for FRRS-Up by market—The MCPC for FRRS-Up in the market m, for the hour. |
| MCPCRU m | $/MW per hour | Market Clearing Price for Capacity for Reg-Up by market—The MCPC for Reg-Up in the market m, for the hour. |
| FRRSUFQ q | MW | FRRS-Up Failure Quantity per QSE—QSE q total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for FRRS-Up, for the hour. |
| RUFQ q | MW | Reg-Up Failure Quantity per QSE—QSE q total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for Reg-Up, for the hour. |
| m | none | The DAM or a SASM for the given Operating Hour. |
| q | none | A QSE. |

(b)	For Reg-Down, if applicable:

RDFQAMT q	=	((MCPCRD m) * RDFQ q) + (Maxm(MCPCFRRSD m) * FRRSDFQ q)

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RDFQAMT q | $ | Reg-Down Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for Reg-Down, for the hour. |
| MCPCFRRSD m | $/MW per hour | Market Clearing Price for Capacity for FRRS-Down by market—The MCPC for FRRS-Down in the market m, for the hour. |
| MCPCRD m | $/MW per hour | Market Clearing Price for Capacity for Reg-Down by market—The MCPC for Reg-Down in the market m, for the hour. |
| FRRSDFQ q | MW | FRRS-Down Failure Quantity per QSE—QSE q total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for FRRS-Down, for the hour. |
| RDFQ q | MW | Reg-Down Failure Quantity per QSE—QSE q’s total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for Reg-Down, for the hour. |
| m | none | The DAM or a SASM for the given Operating Hour. |
| q | none | A QSE. |

(c)	For PFRS, if applicable:

PFRSFQAMT q	=	Maxm(MCPCPFRS m) * PFRSFQ q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| PFRSFQAMT q | $ | Primary Frequency Response Service Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for PFRS, for the hour. |
| MCPCPFRS m | $/MW per hour | Market Clearing Price for Capacity for Primary Frequency Response Service by market—The MCPC for PFRS in the market m, for the hour. |
| PFRSFQ q | MW | Primary Frequency Response Service Failure Quantity per QSE—QSE q’s total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for PFRS, for the hour. |
| m | None | The DAM or a SASM for the given Operating Hour. |
| q | None | A QSE. |

(d)	For FFRS, if applicable:

FFRSFQAMT q	=	Maxm(MCPCFFRS m) * FFRSFQ q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| FFRSFQAMT q | $ | Fast Frequency Response Service Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for FFRS, for the hour. |
| MCPCFFRS m | $/MW per hour | Market Clearing Price for Capacity for Fast Frequency Response Service by market—The MCPC for FFRS in the market m, for the hour. |
| FFRSFQ q | MW | Fast Frequency Response Service Failure Quantity per QSE—QSE q’s total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for FFRS, for the hour. |
| m | None | The DAM or a SASM for the given Operating Hour. |
| q | None | A QSE. |

(e)	For CRS, if applicable:

CRSFQAMT q	=	Maxm(MCPCCRS m) * CRSFQ q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| CRSFQAMT q | $ | Contingency Reserve Service Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for CRS, for the hour. |
| MCPCCRS m | $/MW per hour | Market Clearing Price for Capacity for Contingency Reserve Service by market—The MCPC for CRS in the market m, for the hour. |
| CRSFQ q | MW | Contingency Reserve Service Failure Quantity per QSE—QSE q’s total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for CRS, for the hour. |
| m | None | The DAM or a SASM for the given Operating Hour. |
| q | None | A QSE. |

(f)	For SRS, if applicable:

SRSFQAMT q	=	Maxm(MCPCSRS m) * SRSFQ q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| SRSFQAMT q | $ | Supplemental Reserve Service Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for SRS, for the hour. |
| MCPCSRS m | $/MW per hour | Market Clearing Price for Capacity for Supplemental Reserve Service by market—The MCPC for SRS in the market m, for the hour. |
| SRSFQ q | MW | Supplemental Reserve Service Failure Quantity per QSE—QSE q’s total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for SRS, for the hour. |
| m | None | The DAM or a SASM for the given Operating Hour. |
| q | None | A QSE. |

The above variables are defined as follows:

The above variables are defined as follows:

|  | $/MW per hour |  |
| --- | --- | --- |

[NPRR589: Replace Section 6.7.2 above with the following upon system implementation:] - 6.7.2 Charges for Ancillary Service Capacity Replaced Due to Failure to Provide A charge to each QSE that fails on its Ancillary Service Supply Responsibility, whether or not a SASM is executed due to its failure to supply, is calculated based on the greatest of the MCPC in the Day-Ahead Market (DAM) or any SASM for the same Operating Hour. Included in the failed quantity is the charge to each QSE that reduces its Ancillary Service Supply Responsibility by a reconfiguration SASM, which is calculated based on the cleared MCPC associated with the reconfiguration SASM. By service, the charge to each QSE for a given Operating Hour is calculated as follows: (a) For Reg-Up, if applicable: RUFQAMT q = ((MCPCRU m) * RUFQ q) + (MCPCRU rs * RUFQ rs) + (Maxm(MCPCFRRSU m) * FRRSUFQ q) + (MCPCFRRSU rs * FRRSUFQ rs) The above variables are defined as follows: Variable; Unit; Description. RUFQAMT q; $; Reg-Up Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for Reg-Up, for the hour.. MCPCRU m; $/MW per hour; Market Clearing Price for Capacity for Reg-Up by market—The MCPC for Reg-Up in the market m, for the hour.. MCPCRU rs; $/MW per hour; Market Clearing Price for Capacity for Reg-Up by market—The MCPC for Reg-Up in the reconfiguration SASM rs, for the hour.. MCPCFRRSU m; $/MW per hour; Market Clearing Price for Capacity for FRRS-Up by market—The MCPC for FRRS-Up in the market m, for the hour.. MCPCFRRSU rs; $/MW per hour; Market Clearing Price for Capacity for FRRS-Up by market—The MCPC for FRRS-Up in the reconfiguration SASM rs, for the hour.. RUFQ q; MW; Reg-Up Failure Quantity per QSE—QSE q total capacity associated with failures on its Ancillary Service Supply Responsibility for Reg-Up, for the hour.. RUFQ rs; MW; Reg-Up Failure Quantity per QSE—QSE q total capacity associated with reconfiguration reductions on its Ancillary Service Supply Responsibility for Reg-Up, for the hour.. FRRSUFQ q; MW; FRRS-Up Failure Quantity per QSE—QSE q total capacity associated with failures on its Ancillary Service Supply Responsibility for FRRS-Up, for the hour.. FRRSUFQ rs; MW; FRRS-Up Failure Quantity per QSE—QSE q total capacity associated with reconfiguration reductions on its Ancillary Service Supply Responsibility for FRRS-Up, for the hour.. rs; none; The reconfiguration SASM for the given Operating Hour.. m; none; The DAM or a SASM for the given Operating Hour.. q; none; A QSE.. (b) For Reg-Down, if applicable: RDFQAMT q = ((MCPCRD m) * RDFQ q) + (MCPCRD rs * RDFQ rs) + (Maxm(MCPCFRRSD m) * FRRSDFQ q) + (MCPCFRRSD rs * FRRSDFQ rs) The above variables are defined as follows: Variable; Unit; Description. RDFQAMT q; $; Reg-Down Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for Reg-Down, for the hour.. MCPCRD m; $/MW per hour; Market Clearing Price for Capacity for Reg-Down by market—The MCPC for Reg-Down in the market m, for the hour.. MCPCRD rs; $/MW per hour; Market Clearing Price for Capacity for Reg-Down by market—The MCPC for Reg-Down in the reconfiguration SASM rs, for the hour.. RDFQ q; MW; Reg-Down Failure Quantity per QSE—QSE q’s total capacity associated with failures on its Ancillary Service Supply Responsibility for Reg-Down, for the hour.. MCPCFRRSD m; $/MW per hour; Market Clearing Price for Capacity for FRRS-Down by market—The MCPC for FRRS-Down in the market m, for the hour.. MCPCFRRSD rs; $/MW per hour; Market Clearing Price for Capacity for FRRS-Down by market—The MCPC for FRRS-Down in the reconfiguration SASM rs, for the hour.. RDFQ rs; MW; Reg-Down Failure Quantity per QSE—QSE q’s total capacity associated with reconfiguration reductions on its Ancillary Service Supply Responsibility for Reg-Down, for the hour.. FRRSDFQ q; MW; FRRS-Down Failure Quantity per QSE—QSE q’s total capacity associated with failures on its Ancillary Service Supply Responsibility for FRRS-Down, for the hour.. FRRSDFQ rs; MW; FRRS-Down Failure Quantity per QSE—QSE q’s total capacity associated with reconfiguration reductions on its Ancillary Service Supply Responsibility for FRRS-Down, for the hour.. rs; none; The reconfiguration SASM for the given Operating Hour.. m; none; The DAM or a SASM for the given Operating Hour.. q; none; A QSE.. (c) For PFRS, if applicable: PFRSFQAMT q = (Maxm(MCPCPFRS m) * PFRSFQ q) + (MCPCPFRS rs * PFRSFQ rs) The above variables are defined as follows: Variable; Unit; Description. PFRSFQAMT q; $; Primary Frequency Response Service Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for PFRS, for the hour.. MCPCPFRS m; $/MW per hour; Market Clearing Price for Capacity for Primary Frequency Response Service by market—The MCPC for PFRS in the market m, for the hour.. MCPCPFRS rs; $/MW per hour; Market Clearing Price for Capacity for Primary Frequency Response Service by market—The MCPC for PFRS in the reconfiguration SASM rs, for the hour.. PFRSFQ q; MW; Primary Frequency Response Service Failure Quantity per QSE—QSE q’s total capacity associated with failures on its Ancillary Service Supply Responsibility for PFRS, for the hour.. PFRSFQ rs; MW; Primary Frequency Response Service Failure Quantity per QSE—QSE q’s total capacity associated with reconfiguration reductions on its Ancillary Service Supply Responsibility for PFRS, for the hour.. rs; none; The reconfiguration SASM for the given Operating Hour.. m; none; The DAM or a SASM for the given Operating Hour.. q; none; A QSE.. (d) For FFRS, if applicable: FFRSFQAMT q = (Maxm(MCPCFFRS m) * FFRSFQ q) + (MCPCFFRS rs * FFRSFQ rs) The above variables are defined as follows: Variable; Unit; Description. FFRSFQAMT q; $; Fast Frequency Response Service Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for FFRS, for the hour.. MCPCFFRS m; $/MW per hour; Market Clearing Price for Capacity for Fast Frequency Response Service by market—The MCPC for FFRS in the market m, for the hour.. MCPCFFRS rs; $/MW per hour; Market Clearing Price for Capacity for Fast Frequency Response Service by market—The MCPC for FFRS in the reconfiguration SASM rs, for the hour.. FFRSFQ q; MW; Fast Frequency Response Service Failure Quantity per QSE—QSE q’s total capacity associated with failures on its Ancillary Service Supply Responsibility for FFRS, for the hour.. FFRSFQ rs; MW; Fast Frequency Response Service Failure Quantity per QSE—QSE q’s total capacity associated with reconfiguration reductions on its Ancillary Service Supply Responsibility for FFRS, for the hour.. rs; none; The reconfiguration SASM for the given Operating Hour.. m; none; The DAM or a SASM for the given Operating Hour.. q; none; A QSE.. (e) For CRS, if applicable: CRSFQAMT q = (Maxm(MCPCCRS m) * CRSFQ q) + (MCPCCRS rs * CRSFQ rs) The above variables are defined as follows: Variable; Unit; Description. CRSFQAMT q; $; Contingency Reserve Service Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for CRS, for the hour.. MCPCCRS m; $/MW per hour; Market Clearing Price for Capacity for Contingency Reserve Service by market—The MCPC for CRS in the market m, for the hour.. MCPCCRS rs; $/MW per hour; Market Clearing Price for Capacity for Contingency Reserve Service by market—The MCPC for CRS in the reconfiguration SASM rs, for the hour.. CRSFQ q; MW; Contingency Reserve Service Failure Quantity per QSE—QSE q’s total capacity associated with failures on its Ancillary Service Supply Responsibility for CRS, for the hour.. CRSFQ rs; MW; Contingency Reserve Service Failure Quantity per QSE—QSE q’s total capacity associated with reconfiguration reductions on its Ancillary Service Supply Responsibility for CRS, for the hour.. rs; none; The reconfiguration SASM for the given Operating Hour.. m; none; The DAM or a SASM for the given Operating Hour.. q; none; A QSE.. (f) For SRS, if applicable: SRSFQAMT q = (Maxm(MCPCSRS m) * SRSFQ q) + (MCPCSRS rs * SRSFQ rs) The above variables are defined as follows: Variable; Unit; Description. SRSFQAMT q; $; Supplemental Reserve Service Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for SRS, for the hour.. MCPCSRS m; $/MW per hour; Market Clearing Price for Capacity for Supplemental Reserve Service by market—The MCPC for SRS in the market m, for the hour.. MCPCSRS rs; $/MW per hour; Market Clearing Price for Capacity for Supplemental Reserve Service by market—The MCPC for SRS in the reconfiguration SASM rs, for the hour.. SRSFQ q; MW; Supplemental Reserve Service Failure Quantity per QSE—QSE q’s total capacity associated with failures on its Ancillary Service Supply Responsibility for SRS, for the hour.. SRSFQ rs; MW; Supplemental Reserve Service Failure Quantity per QSE—QSE q’s total capacity associated with reconfiguration reductions on its Ancillary Service Supply Responsibility for SRS, for the hour.. rs; none; The reconfiguration SASM for the given Operating Hour.. m; none; The DAM or a SASM for the given Operating Hour.. q; none; A QSE.. The above variables are defined as follows: )

- 6.7.3	Adjustments to Cost Allocations for Ancillary Services Procurement

(1)	Each QSE, for which ERCOT purchases Ancillary Service capacity in the DAM and SASMs (if any), is charged for the QSE’s share of the net costs incurred for each service.  For each QSE, its share of the DAM costs has been calculated in Section 4.6.4, Settlement of Ancillary Services Procured in the DAM; its share of the net total costs incurred in both DAM and SASMs less its DAM charge is calculated in this section.

(2)	For Reg-Up, if applicable:

(a)	The net total costs for Reg-Up for a given Operating Hour is calculated as follows:

RUCOSTTOT	=	(-1) * ((RTPCRUAMTTOT m) + PCRUAMTTOT  + RUFQAMTTOT)

Where:

Total payment of SASM-procured capacity for Reg-Up by market

RTPCRUAMTTOT m	=	RTPCRUAMT q, m

Total payment of DAM-procured capacity for Reg-Up

PCRUAMTTOT  	= 	PCRUAMT q

Total charge of failure on Ancillary Service Supply Responsibility for Reg-Up

RUFQAMTTOT	=	RUFQAMT q

Total payment of SASM procured capacity for Reg-Up by QSE

RTPCRUAMTQSETOT q = RTPCRUAMT q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RUCOSTTOT | $ | Reg-Up Cost Total—The net total costs for Reg-Up for the hour. |
| RTPCRUAMTTOT m | $ | Procured Capacity for Reg-Up Amount Total by market—The total payments to all QSEs for the Ancillary Service Offers cleared in the market m for Reg-Up, for the hour. |
| RTPCRUAMT q, m | $ | Procured Capacity for Reg-Up Amount per QSE by market—The payment to QSE q for its Ancillary Service Offers cleared in the market m for Reg-Up, for the hour. |
| RUFQAMTTOT | $ | Reg-Up Failure Quantity Amount Total—The total charges to all QSEs for their capacity associated with failures and reconfiguration reductions on their Ancillary Service Supply Responsibilities for Reg-Up, for the hour. |
| RUFQAMT q | $ | Reg-Up Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for Reg-Up, for the hour. |
| RTPCRUAMTQSETOT q | $ | Procured Capacity for Reg-Up Amount Total per QSE—The total payments to a QSE in all SASM markets for the Ancillary Service Offers cleared for Reg-Up Service, for the hour. |
| PCRUAMT q | $ | Procured Capacity for Reg-Up Amount per QSE in DAM—The DAM Reg-Up Service payment for QSE q for the hour. |
| PCRUAMTTOT | $ | Procured Capacity for Reg-Up Amount Total in DAM—The total of the DAM Reg-Up payments for all QSEs for the hour. |
| q | none | A QSE. |
| m | none | A SASM for the given Operating Hour. |

(b)	Each QSE’s share of the net total costs for Reg-Up for the Operating Hour is calculated as follows:

RUCOST q	=	RUPR * RUQ q

Where:

RUPR	=	RUCOSTTOT / RUQTOT

RUQTOT	=	RUQ q

RUQ q	=	RUO q – SARUQ q – SAFRRSUQ q

RUO q	=	((SARUQ q + (RTPCRU q, m) + PCRU q – RURP q – RUFQ q) * HLRS q + RURP q) + (Σq(SAFRRSUQ q + (Σm(RTPCFRRSU q, m) *ERFRRSUP) + (ERFRRSUP * PCFRRSU q) – (ERFRRSUP *FRRSURP q) – (ERFRRSUP *FRRSUFQ q)) * HLRS q + (ERFRRSUP * FRRSURP q))

SARUQ q	=	DASARUQ q + RTSARUQ q

SAFRRSUQ q	=	ERFRRSUP * (DASAFRRSUQ q + RTSAFRRSUQ q)

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RUCOST q | $ | Reg-Up Cost per QSE—QSE q’s share of the net total costs for Reg-Up, for the hour. |
| RUPR | $/MW per hour | Reg-Up Price—The price for Reg-Up calculated based on the net total costs for Reg-Up, for the hour. |
| RUCOSTTOT | $ | Reg-Up Cost Total—The net total costs for Reg-Up for the hour. See item (a) above. |
| RUQTOT | MW | Reg-Up Quantity Total—The sum of every QSE’s portion of its Ancillary Service Obligation that is not self-arranged in either DAM or any SASM, for the hour. |
| RUQ q | MW | Reg-Up Quantity per QSE—The portion of QSE q’s Ancillary Service Obligation that is not self-arranged in either DAM or any SASM, for the hour. |
| RUO q | MW | Reg-Up Obligation per QSE—The Ancillary Service Obligation of QSE q, for the hour. |
| DASARUQ q | MW | Day-Ahead Self-Arranged Reg-Up Quantity per QSE—The self-arranged Reg-Up quantity submitted by QSE q before 1000 in the Day-Ahead. |
| DASAFRRSUQ q | MW | Day-Ahead Self-Arranged FRRS-Up Quantity per QSE—The self-arranged FRRS-Up quantity submitted by QSE q before 1000 in the Day-Ahead. |
| ERFRRSUP | none | Equivalency Ratio for FRRS-Up—The equivalency ratio between Reg-Up and FRRS-UP, for the hour. |
| RTSARUQ q | MW | Self-Arranged Reg-Up Quantity per QSE for all SASMs—The sum of all self-arranged Reg-Up quantities submitted by QSE q for all SASMs. |
| RTSAFRRSUQ q | MW | Self-Arranged FRRS-Up Quantity per QSE for all SASMs—The sum of all self-arranged FRRS-Up quantities submitted by QSE q for all SASMs. |
| RTPCRU q, m | MW | Procured Capacity for Reg-Up per QSE by market—The MW portion of QSE q’s Ancillary Service Offers cleared in the market m to provide Reg-Up, for the hour. |
| RTPCFRRSU q, m | MW | Procured Capacity for FRRS-Up per QSE by market—The MW portion of QSE q’s Ancillary Service Offers cleared in the market m to provide FRRS-Up, for the hour. |
| RUFQ q | MW | Reg-Up Failure Quantity per QSE—QSE q’s total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for Reg-Up, for the hour. |
| FRRSUFQ q | MW | FRRS-Up Failure Quantity per QSE—QSE q’s total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for FRRS-Up, for the hour. |
| HLRS q | none | The Hourly Load Ratio Share calculated for QSE q for the hour. See Section 6.6.2.3, QSE Load Ratio Share for an Operating Hour. |
| RURP q | MW | Reg-Up Replacement per QSE—The total Reg-Up capacity that was a portion of the Ancillary Service Supply Responsibility of QSE q but is replaced in a SASM for the hour. |
| FRRSURP q | MW | FRRS-Up Replacement per QSE—The total FRRS-Up capacity that was a portion of the Ancillary Service Supply Responsibility of QSE q but is replaced in a SASM for the hour. |
| PCRU q | MW | Procured Capacity for Reg-Up per QSE in DAM—The total Reg-Up Service capacity quantity awarded to QSE q in the DAM for all the Resources represented by the QSE for the hour. |
| PCFRRSU q | MW | Procured Capacity for FRRS-Up per QSE in DAM—The total FRRS-Up Service capacity quantity awarded to QSE q in the DAM for all the Resources represented by the QSE for the hour. |
| SARUQ q | MW | Total Self-Arranged Reg-Up Quantity per QSE for all markets—The sum of all self-arranged Reg-Up quantities submitted by QSE q for DAM and all SASMs. |
| SAFRRSUQ q | MW | Total Self-Arranged FRRS-Up Quantity per QSE for all markets—The sum of all self-arranged FRRS-Up quantities submitted by QSE q for DAM and all SASMs. |
| q | none | A QSE. |
| m | none | A SASM for the given Operating Hour. |

(c)	The adjustment to each QSE’s DAM charge for the Reg-Up for the Operating Hour, due to changes during the Adjustment Period or Real-Time operations, is calculated as follows:

RTRUAMT q	=	RUCOST q – DARUAMT q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTRUAMT q | $ | Real-Time Reg-Up Amount per QSE—The adjustment to QSE q’s share of the costs for Reg-Up, for the hour. |
| RUCOST q | $ | Reg-Up Cost per QSE—QSE q’s share of the net total costs for Reg-Up, for the hour. |
| DARUAMT q | $ | Day-Ahead Reg-Up Amount per QSE—QSE q’s share of the DAM cost for Reg-Up, for the hour. |
| q | none | A QSE. |

(3)	For Reg-Down, if applicable:

(a)	The net total costs for Reg-Down for a given Operating Hour is calculated as follows:

RDCOSTTOT	=	(-1) * ((RTPCRDAMTTOT m) + PCRDAMTTOT + RDFQAMTTOT)

Where:

Total payment of SASM-procured capacity for Reg-Down by market

RTPCRDAMTTOT m	=	RTPCRDAMT q, m

Total payment of DAM-procured capacity for Reg-Down

PCRDAMTTOT	=	 PCRDAMT q

Total charge of failure on Ancillary Service Supply Responsibility for Reg-Down

RDFQAMTTOT	=	RDFQAMT q

Total payment of SASM procured capacity for Reg-Down by QSE

RTPCRDAMTQSETOT q = RTPCRDAMT q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RDCOSTTOT | $ | Reg-Down Cost Total—The net total costs for Reg-Down for the hour. |
| RTPCRDAMTTOT m | $ | Procured Capacity for Reg-Down Amount Total by market—The total payments to all QSEs for the Ancillary Service Offers cleared in the market m for Reg-Down, for the hour. |
| RTPCRDAMT q, m | $ | Procured Capacity for Reg-Down Amount per QSE by market—The payment to QSE q for its Ancillary Service Offers cleared in the market m for Reg-Down, for the hour. |
| RDFQAMTTOT | $ | Reg-Down Failure Quantity Amount Total—The total charges to all QSEs for their capacity associated with failures on their Ancillary Service Supply Responsibilities for Reg-Down, for the hour. |
| RDFQAMT q | $ | Reg-Down Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for Reg-Down, for the hour. |
| RTPCRDAMTQSETOT q | $ | Procured Capacity for Reg-Down Amount Total per QSE—The total payments to a QSE in all SASM markets for the Ancillary Service Offers cleared for Reg-Down Service, for the hour. |
| PCRDAMT q | $ | Procured Capacity for Regulation Down Amount per QSE for DAM—The DAM Reg-Down Service payment for QSE q for the hour. |
| PCRDAMTTOT | $ | Procured Capacity for Reg-Down Amount Total in DAM—The total of the DAM Reg-Down payments for all QSEs for the hour. |
| q | none | A QSE. |
| m | none | A SASM for the given Operating Hour. |

(b)	Each QSE’s share of the net total costs for Reg-Down for the Operating Hour is calculated as follows:

RDCOST q	=	RDPR * RDQ q

Where:

RDPR	=	RDCOSTTOT / RDQTOT

RDQTOT	=	RDQ q

RDQ q	=	RDO q – SARDQ q – SAFRRSDQ q

RDO q	=	((SARDQ q + (RTPCRD q, m) + PCRD q – RDRP q – RDFQ q) * HLRS q + RDRP q) + (Σq(SAFRRSDQ q + (Σm(RTPCFRRSD q, m) *ERFRRSDN) + (ERFRRSDN * PCFRRSD q) – (ERFRRSDN *FRRSDRP q) – (ERFRRSDN *FRRSDFQ q)) * HLRS q + (ERFRRSDN * FRRSDRP q))

SARDQ q	=	DASARDQ q + RTSARDQ q

SAFRRSDQ q	=	ERFRRSDN * (DASAFRRSDQ q + RTSAFRRSDQ q)

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RDCOST q | $ | Reg-Down Cost per QSE—QSE q’s share of the net total costs for Reg-Down, for the hour. |
| RDPR | $/MW per hour | Reg-Down Price—The price for Reg-Down calculated based on the net total costs for Reg-Down, for the hour. |
| RDCOSTTOT | $ | Reg-Down Cost Total—The net total costs for Reg-Down for the hour. See item (a) above. |
| RDQTOT | MW | Reg-Down Quantity Total—The sum of every QSE’s portion of its Ancillary Service Obligation that is not self-arranged in either DAM or any SASM, for the hour. |
| RDQ q | MW | Reg-Down Quantity per QSE—The portion of QSE q’s net Ancillary Service Obligation that is not self-arranged in either DAM or any SASM, for the hour. |
| RDO q | MW | Reg-Down Obligation per QSE—The Ancillary Service Obligation of QSE q, for the hour. |
| DASARDQ q | MW | Self-Arranged Reg-Down Quantity per QSE for DAM—The self-arranged Reg-Down quantity submitted by QSE q before 1000 in the Day-Ahead. |
| DASAFRRSDQ q | MW | Self-Arranged FRRS-Down Quantity per QSE for DAM—The self-arranged FRRS-Down quantity submitted by QSE q before 1000 in the Day-Ahead. |
| RTSARDQ q | MW | Self-Arranged Reg-Down Quantity per QSE for all SASMs—The sum of all self-arranged Reg-Down quantities submitted by QSE q for all SASMs. |
| ERFRRSDN | none | Equivalency Ratio for FRRS-Down—The equivalency ratio between Reg-Up and FRRS-Down, for the hour. |
| RTSAFRRSDQ q | MW | Self-Arranged FRRS-Down Quantity per QSE for all SASMs—The sum of all self-arranged FRRS-Down quantities submitted by QSE q for all SASMs. |
| RTPCRD q, m | MW | Procured Capacity for Reg-Down per QSE by market—The MW portion of QSE q’s Ancillary Service Offers cleared in the market m to provide Reg-Down, for the hour. |
| RTPCFRRSD q, m | MW | Procured Capacity for FRRS-Down per QSE by market—The MW portion of QSE q’s Ancillary Service Offers cleared in the market m to provide FRRS-Down, for the hour. |
| RDFQ q | MW | Reg-Down Failure Quantity per QSE—QSE q’s total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for Reg-Down, for the hour. |
| FRRSDFQ q | MW | FRRS-Down Failure Quantity per QSE—QSE q’s total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for FRRS-Down, for the hour. |
| HLRS q |  | The Hourly Load Ratio Share calculated for QSE q for the hour. See Section 6.6.2.3. |
| RDRP q | MW | Reg-Down Replacement per QSE per market—The total Reg-Down capacity that was a portion of the Ancillary Service Supply Responsibility of QSE q but is replaced in a SASM, for the hour. |
| FRRSDRP q | MW | FRRS-Down Replacement per QSE per market—The total FRRS-Down capacity that was a portion of the Ancillary Service Supply Responsibility of QSE q but is replaced in a SASM, for the hour. |
| PCRD q | MW | Procured Capacity for Reg-Down per QSE in DAM—The total Reg-Down Service capacity quantity awarded to QSE q in the DAM for all the Resources represented by the QSE for the hour. |
| PCFRRSD q | MW | Procured Capacity for FRRS-Down per QSE in DAM—The total FRRS-Down Service capacity quantity awarded to QSE q in the DAM for all the Resources represented by the QSE for the hour. |
| SARDQ q | MW | Total Self-Arranged Reg-Down Quantity per QSE for all markets—The sum of all self-arranged Reg-Down quantities submitted by QSE q for DAM and all SASMs. |
| SAFRRSDQ q | MW | Total Self-Arranged FRRS-Down Quantity per QSE for all markets—The sum of all self-arranged FRRS-Down quantities submitted by QSE q for DAM and all SASMs. |
| q | none | A QSE. |
| m | none | A SASM for the given Operating Hour. |

(c)	The adjustment to each QSE’s DAM charge for the Reg-Down for the Operating Hour, due to changes during the Adjustment Period or Real-Time operations, is calculated as follows:

RTRDAMT q	=	RDCOST q – DARDAMT q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTRDAMT q | $ | Real-Time Reg-Down Amount per QSE—The adjustment to QSE q’s share of the costs for Reg-Down, for the hour. |
| RDCOST q | $ | Reg-Down Cost per QSE—QSE q’s share of the net total costs for Reg-Down, for the hour. |
| DARDAMT q | $ | Day-Ahead Reg-Down Amount per QSE—QSE q’s share of the DAM cost for Reg-Down, for the hour. |
| q | none | A QSE. |

(4)	For PFRS, if applicable:

(a)	The net total costs for PFRS for a given Operating Hour is calculated as follows:

PFRSCOSTTOT	=	(-1) * (Σm(RTPCPFRSAMTTOT m) + PCPFRSAMTTOT + PFRSFQAMTTOT)

Where:

Total payment of SASM-procured capacity for PFRS by market

RTPCPFRSAMTTOT m	=	ΣqRTPCPFRSAMT q, m

Total payment of DAM-procured capacity for PFRS

PCPFRSAMTTOT	=	 ΣqPCPFRSAMT q

Total charge of failure on Ancillary Service Supply Responsibility for PFRS

PFRSFQAMTTOT	=	ΣqPFRSFQAMT q

Total payment of SASM procured capacity for PFRS by QSE

RTPCPFRSAMTQSETOT q = ΣmRTPCPFRSAMT q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| PFRSCOSTTOT | $ | Primary Frequency Response Service Cost Total—The net total costs for PFRS for the hour. |
| RTPCPFRSAMTTOT m | $ | Procured Capacity for Primary Frequency Response Service Amount Total by market—The total payments to all QSEs for the Ancillary Service Offers cleared in the market m for PFRS, for the hour. |
| RTPCPFRSAMT q, m | $ | Procured Capacity for Primary Frequency Response Service Amount per QSE by market—The payment to QSE q for its Ancillary Service Offers cleared in the market m for PFRS, for the hour. |
| PFRSFQAMTTOT | $ | Primary Frequency Response Service Failure Quantity Amount Total—The total charges to all QSEs for their capacity associated with failures on their Ancillary Service Supply Responsibilities for PFRS, for the hour. |
| PFRSFQAMT q | $ | Primary Frequency Response Service Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for PFRS, for the hour. |
| RTPCPFRSAMTQSETOT q | $ | Procured Capacity for Primary Frequency Response Service Amount Total per QSE—The total payments to a QSE in all SASM markets for the Ancillary Service Offers cleared for PFRS, for the hour. |
| PCPFRSAMT q | $ | Procured Capacity for Primary Frequency Response Service Amount per QSE in DAM—The DAM PFRS payment for QSE q for the hour. |
| PCPFRSAMTTOT | $ | Procured Capacity for Primary Frequency Response Service Amount Total in DAM—The total of the DAM PFRS payments for all QSEs for the hour. |
| q | none | A QSE. |
| m | none | A SASM for the given Operating Hour. |

(b)	Each QSE’s share of the net total costs for PFRS for the Operating Hour is calculated as follows:

PFRSCOST q	=	PFRSPR * PFRSQ q

Where:

PFRSPR	=	PFRSCOSTTOT / PFRSQTOT

PFRSQTOT	=	ΣqPFRSQ q

PFRSQ q	=	PFRSO q – SAPFRSQ q

PFRSO q	=	Σq(SAPFRSQ q + Σm(RTPCPFRS q, m) + PCPFRS q – PFRSRP q – PFRSFQ q) * HLRS q + PFRSRP q

SAPFRSQ q	=	DASAPFRSQ q + RTSAPFRSQ q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| PFRSCOST q | $ | Primary Frequency Response Service Cost per QSE—QSE q’s share of the net total costs for PFRS, for the hour. |
| PFRSPR | $/MW per hour | Primary Frequency Response Service Price—The price for PFRS calculated based on the net total costs for PFRS, for the hour. |
| PFRSCOSTTOT | $ | Primary Frequency Response Service Cost Total—The net total costs for PFRS for the hour. See item (a) above. |
| PFRSQTOT | MW | Primary Frequency Response Service Quantity Total—The sum of every QSE’s portion of its Ancillary Service Obligation for PFRS that is not self-arranged in either DAM or any SASM, for the hour. |
| PFRSQ q | MW | Primary Frequency Response Service Quantity per QSE—The portion of QSE q’s net Ancillary Service Obligation for PFRS that is not self-arranged in either DAM or any SASM, for the hour. |
| PFRSO q | MW | Primary Frequency Response Service Obligation per QSE—The Ancillary Service Obligation for PFRS of QSE q, for the hour. |
| DASAPFRSQ q | MW | Self-Arranged Primary Frequency Response Service Quantity per QSE for DAM—The self-arranged PFRS quantity submitted by QSE q before 1000 in the Day-Ahead. |
| RTSAPFRSQ q | MW | Self-Arranged Primary Frequency Response Service Quantity per QSE for all SASMs—The sum of all self-arranged PFRS quantities submitted by QSE q for all SASMs. |
| RTPCPFRS q, m | MW | Procured Capacity for Primary Frequency Response Service per QSE by market—The MW portion of QSE q’s Ancillary Service Offers cleared in the market m to provide PFRS, for the hour. |
| PFRSFQ q | MW | Primary Frequency Response Service Failure Quantity per QSE—QSE q’s total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for PFRS, for the hour. |
| HLRS q |  | The Hourly Load Ratio Share calculated for QSE q for the hour. See Section 6.6.2.3. |
| PFRSRP q | MW | Primary Frequency Response Service Replacement per QSE per market—The total PFRS capacity that was a portion of the Ancillary Service Supply Responsibility of QSE q but is replaced in a SASM, for the hour. |
| PCPFRS q | MW | Procured Capacity for Primary Frequency Response Service per QSE in DAM—The total PFRS capacity quantity awarded to QSE q in the DAM for all the Resources represented by the QSE for the hour. |
| SAPFRSQ q | MW | Total Self-Arranged Primary Frequency Response Service Quantity per QSE for all markets—The sum of all self-arranged PFRS quantities submitted by QSE q for DAM and all SASMs. |
| q | none | A QSE. |
| m | none | A SASM for the given Operating Hour. |

(c)	The adjustment to each QSE’s DAM charge for the PFRS for the Operating Hour, due to changes during the Adjustment Period or Real-Time operations, is calculated as follows:

RTPFRSAMT q	=	PFRSCOST q – DAPFRSAMT q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTPFRSAMT q | $ | Real-Time Primary Frequency Response Service Amount per QSE—The adjustment to QSE q’s share of the costs for PFRS, for the hour. |
| PFRSCOST q | $ | Primary Frequency Response Service Cost per QSE—QSE q’s share of the net total costs for PFRS, for the hour. |
| DAPFRSAMT q | $ | Day-Ahead Primary Frequency Response Service Amount per QSE—QSE q’s share of the DAM cost for PFRS, for the hour. |
| q | none | A QSE. |

(5)	For FFRS, if applicable:

(a)	The net total costs for FFRS for a given Operating Hour is calculated as follows:

FFRSCOSTTOT	=	(-1) * (Σm(RTPCFFRSAMTTOT m) + PCFFRSAMTTOT + FFRSFQAMTTOT)

Where:

Total payment of SASM-procured capacity for FFRS by market

RTPCFFRSAMTTOT m	=	ΣqRTPCFFRSAMT q, m

Total payment of DAM-procured capacity for FFRS

PCFFRSAMTTOT	=	 ΣqPCFFRSAMT q

Total charge of failure on Ancillary Service Supply Responsibility for FFRS

FFRSFQAMTTOT	=	ΣqFFRSFQAMT q

Total payment of SASM procured capacity for FFRS by QSE

RTPCFFRSAMTQSETOT q = ΣmRTPCFFRSAMT q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| FFRSCOSTTOT | $ | Fast Frequency Response Service Cost Total—The net total costs for FFRS for the hour. |
| RTPCFFRSAMTTOT m | $ | Procured Capacity for Fast Frequency Response Service Amount Total by market—The total payments to all QSEs for the Ancillary Service Offers cleared in the market m for FFRS, for the hour. |
| RTPCFFRSAMT q, m | $ | Procured Capacity for Fast Frequency Response Service Amount per QSE by market—The payment to QSE q for its Ancillary Service Offers cleared in the market m for FFRS, for the hour. |
| FFRSFQAMTTOT | $ | Fast Frequency Response Service Failure Quantity Amount Total—The total charges to all QSEs for their capacity associated with failures on their Ancillary Service Supply Responsibilities for FFRS, for the hour. |
| FFRSFQAMT q | $ | Fast Frequency Response Service Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for FFRS, for the hour. |
| RTPCFFRSAMTQSETOT q | $ | Procured Capacity for Fast Frequency Response Service Amount Total per QSE—The total payments to a QSE in all SASM markets for the Ancillary Service Offers cleared for FFRS, for the hour. |
| PCFFRSAMT q | $ | Procured Capacity for Fast Frequency Response Service Amount per QSE in DAM—The DAM FFRS payment for QSE q for the hour. |
| PCFFRSAMTTOT | $ | Procured Capacity for Fast Frequency Response Service Amount Total in DAM—The total of the DAM FFRS payments for all QSEs for the hour. |
| q | none | A QSE. |
| m | none | A SASM for the given Operating Hour. |

(b)	Each QSE’s share of the net total costs for FFRS for the Operating Hour is calculated as follows:

FFRSCOST q	=	FFRSPR * FFRSQ q

Where:

FFRSPR	=	FFRSCOSTTOT / FFRSQTOT

FFRSQTOT	=	ΣqFFRSQ q

FFRSQ q	=	FFRSO q – SAFFRSQ q

FFRSO q	=	Σq(SAFFRSQ q + Σm(RTPCFFRS q, m) + PCFFRS q – FFRSRP q – FFRSFQ q) * HLRS q + FFRSRP q

SAFFRSQ q	=	DASAFFRSQ q + RTSAFFRSQ q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| FFRSCOST q | $ | Fast Frequency Response Service Cost per QSE—QSE q’s share of the net total costs for FFRS, for the hour. |
| FFRSPR | $/MW per hour | Fast Frequency Response Service Price—The price for FFRS calculated based on the net total costs for FFRS, for the hour. |
| FFRSCOSTTOT | $ | Fast Frequency Response Service Cost Total—The net total costs for FFRS for the hour. See item (a) above. |
| FFRSQTOT | MW | Fast Frequency Response Service Quantity Total—The sum of every QSE’s portion of its Ancillary Service Obligation for FFRS that is not self-arranged in either DAM or any SASM, for the hour. |
| FFRSQ q | MW | Fast Frequency Response Service Quantity per QSE—The portion of QSE q’s net Ancillary Service Obligation for FFRS that is not self-arranged in either DAM or any SASM, for the hour. |
| FFRSO q | MW | Fast Frequency Response Service Obligation per QSE—The Ancillary Service Obligation for FFRS of QSE q, for the hour. |
| DASAFFRSQ q | MW | Self-Arranged Fast Frequency Response Service Quantity per QSE for DAM—The self-arranged FFRS quantity submitted by QSE q before 1000 in the Day-Ahead. |
| RTSAFFRSQ q | MW | Self-Arranged Fast Frequency Response Service Quantity per QSE for all SASMs—The sum of all self-arranged FFRS quantities submitted by QSE q for all SASMs. |
| RTPCFFRS q, m | MW | Procured Capacity for Fast Frequency Response Service per QSE by market—The MW portion of QSE q’s Ancillary Service Offers cleared in the market m to provide FFRS, for the hour. |
| FFRSFQ q | MW | Fast Frequency Response Service Failure Quantity per QSE—QSE q’s total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for FFRS, for the hour. |
| HLRS q |  | The Hourly Load Ratio Share calculated for QSE q for the hour. See Section 6.6.2.3. |
| FFRSRP q | MW | Fast Frequency Response Service Replacement per QSE per market—The total FFRS capacity that was a portion of the Ancillary Service Supply Responsibility of QSE q but is replaced in a SASM, for the hour. |
| PCFFRS q | MW | Procured Capacity for Fast Frequency Response Service per QSE in DAM—The total FFRS capacity quantity awarded to QSE q in the DAM for all the Resources represented by the QSE for the hour. |
| SAFFRSQ q | MW | Total Self-Arranged Fast Frequency Response Service Quantity per QSE for all markets—The sum of all self-arranged FFRS quantities submitted by QSE q for DAM and all SASMs. |
| q | none | A QSE. |
| m | none | A SASM for the given Operating Hour. |

(c)	The adjustment to each QSE’s DAM charge for the FFRS for the Operating Hour, due to changes during the Adjustment Period or Real-Time operations, is calculated as follows:

RTFFRSAMT q	=	FFRSCOST q – DAFFRSAMT q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTFFRSAMT q | $ | Real-Time Fast Frequency Response Service Amount per QSE—The adjustment to QSE q’s share of the costs for FFRS, for the hour. |
| FFRSCOST q | $ | Fast Frequency Response Service Cost per QSE—QSE q’s share of the net total costs for FFRS, for the hour. |
| DAFFRSAMT q | $ | Day-Ahead Fast Frequency Response Service Amount per QSE—QSE q’s share of the DAM cost for FFRS, for the hour. |
| q | none | A QSE. |

(6)	For CRS, if applicable:

(a)	The net total costs for CRS for a given Operating Hour is calculated as follows:

CRSCOSTTOT	=	(-1) * (Σm(RTPCCRSAMTTOT m) + PCCRSAMTTOT + CRSFQAMTTOT)

Where:

Total payment of SASM-procured capacity for CRS by market

RTPCCRSAMTTOT m	=	ΣqRTPCCRSAMT q, m

Total payment of DAM-procured capacity for CRS

PCCRSAMTTOT	=	 ΣqPCCRSAMT q

Total charge of failure on Ancillary Service Supply Responsibility for CRS

CRSFQAMTTOT	=	ΣqCRSFQAMT q

Total payment of SASM procured capacity for CRS by QSE

RTPCCRSAMTQSETOT q = ΣmRTPCCRSAMT q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| CRSCOSTTOT | $ | Contingency Reserve Service Cost Total—The net total costs for CRS for the hour. |
| RTPCCRSAMTTOT m | $ | Procured Capacity for Contingency Reserve Service Amount Total by market—The total payments to all QSEs for the Ancillary Service Offers cleared in the market m for CRS, for the hour. |
| RTPCCRSAMT q, m | $ | Procured Capacity for Contingency Reserve Service Amount per QSE by market—The payment to QSE q for its Ancillary Service Offers cleared in the market m for CRS, for the hour. |
| CRSFQAMTTOT | $ | Contingency Reserve Service Failure Quantity Amount Total—The total charges to all QSEs for their capacity associated with failures on their Ancillary Service Supply Responsibilities for CRS, for the hour. |
| CRSFQAMT q | $ | Contingency Reserve Service Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for CRS, for the hour. |
| RTPCCRSAMTQSETOT q | $ | Procured Capacity for Contingency Reserve Service Amount Total per QSE—The total payments to a QSE in all SASM markets for the Ancillary Service Offers cleared for CRS, for the hour. |
| PCCRSAMT q | $ | Procured Capacity for Contingency Reserve Service Amount per QSE in DAM—The DAM CRS payment for QSE q for the hour. |
| PCCRSAMTTOT | $ | Procured Capacity for Contingency Reserve Service Amount Total in DAM—The total of the DAM CRS payments for all QSEs for the hour. |
| q | none | A QSE. |
| m | none | A SASM for the given Operating Hour. |

(b)	Each QSE’s share of the net total costs for CRS for the Operating Hour is calculated as follows:

CRSCOST q	=	CRSPR * CRSQ q

Where:

CRSPR	=	CRSCOSTTOT / CRSQTOT

CRSQTOT	=	ΣqCRSQ q

CRSQ q	=	CRSO q – SACRSQ q

CRSO q	=	Σq(SACRSQ q + Σm(RTPCCRS q, m) + PCCRS q – CRSRP q – CRSFQ q) * HLRS q + CRSRP q

SACRSQ q	=	DASACRSQ q + RTSACRSQ q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| CRSCOST q | $ | Contingency Reserve Service Cost per QSE—QSE q’s share of the net total costs for CRS, for the hour. |
| CRSPR | $/MW per hour | Contingency Reserve Service Price—The price for CRS calculated based on the net total costs for CRS, for the hour. |
| CRSCOSTTOT | $ | Contingency Reserve Service Cost Total—The net total costs for CRS for the hour. See item (a) above. |
| CRSQTOT | MW | Contingency Reserve Service Quantity Total—The sum of every QSE’s portion of its Ancillary Service Obligation for CRS, that is not self-arranged in either DAM or any SASM, for the hour. |
| CRSQ q | MW | Contingency Reserve Service Quantity per QSE—The portion of QSE q’s net Ancillary Service Obligation for CRS, that is not self-arranged in either DAM or any SASM, for the hour. |
| CRSO q | MW | Contingency Reserve Service Obligation per QSE—The Ancillary Service Obligation for CRS of QSE q, for the hour. |
| DASACRSQ q | MW | Self-Arranged Contingency Reserve Service Quantity per QSE for DAM—The self-arranged CRS quantity submitted by QSE q before 1000 in the Day-Ahead. |
| RTSACRSQ q | MW | Self-Arranged Contingency Reserve Service Quantity per QSE for all SASMs—The sum of all self-arranged CRS quantities submitted by QSE q for all SASMs. |
| RTPCCRS q, m | MW | Procured Capacity for Contingency Reserve Service per QSE by market—The MW portion of QSE q’s Ancillary Service Offers cleared in the market m to provide CRS, for the hour. |
| CRSFQ q | MW | Contingency Reserve Service Failure Quantity per QSE—QSE q’s total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for CRS, for the hour. |
| HLRS q |  | The Hourly Load Ratio Share calculated for QSE q for the hour. See Section 6.6.2.3. |
| CRSRP q | MW | Contingency Reserve Service Replacement per QSE per market—The total CRS capacity that was a portion of the Ancillary Service Supply Responsibility of QSE q but is replaced in a SASM, for the hour. |
| PCCRS q | MW | Procured Capacity for Contingency Reserve Service per QSE in DAM—The total CRS capacity quantity awarded to QSE q in the DAM for all the Resources represented by the QSE for the hour. |
| SACRSQ q | MW | Total Self-Arranged Contingency Reserve Service Quantity per QSE for all markets—The sum of all self-arranged CRS quantities submitted by QSE q for DAM and all SASMs. |
| q | none | A QSE. |
| m | none | A SASM for the given Operating Hour. |

(c)	The adjustment to each QSE’s DAM charge for the CRS for the Operating Hour, due to changes during the Adjustment Period or Real-Time operations, is calculated as follows:

RTCRSAMT q	=	CRSCOST q – DACRSAMT q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTCRSAMT q | $ | Real-Time Contingency Reserve Service Amount per QSE—The adjustment to QSE q’s share of the costs for CRS, for the hour. |
| CRSCOST q | $ | Contingency Reserve Service Cost per QSE—QSE q’s share of the net total costs for CRS, for the hour. |
| DACRSAMT q | $ | Day-Ahead Contingency Reserve Service Amount per QSE—QSE q’s share of the DAM cost for CRS, for the hour. |
| q | none | A QSE. |

(7)	For SRS, if applicable:

(a)	The net total costs for SRS for a given Operating Hour is calculated as follows:

SRSCOSTTOT	=	(-1) * (Σm(RTPCSRSAMTTOT m) + PCSRSAMTTOT + SRSFQAMTTOT)

Where:

Total payment of SASM-procured capacity for SRS by market

RTPCSRSAMTTOT m	=	ΣqRTPCSRSAMT q, m

Total payment of DAM-procured capacity for SRS

PCSRSAMTTOT	=	 ΣqPCSRSAMT q

Total charge of failure on Ancillary Service Supply Responsibility for SRS

SRSFQAMTTOT	=	ΣqSRSFQAMT q

Total payment of SASM procured capacity for SRS by QSE

RTPCSRSAMTQSETOT q = ΣmRTPCSRSAMT q, m

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| SRSCOSTTOT | $ | Supplemental Reserve Service Cost Total—The net total costs for SRS for the hour. |
| RTPCSRSAMTTOT m | $ | Procured Capacity for Supplemental Reserve Service Amount Total by market—The total payments to all QSEs for the Ancillary Service Offers cleared in the market m for SRS, for the hour. |
| RTPCSRSAMT q, m | $ | Procured Capacity for Supplemental Reserve Service Amount per QSE by market—The payment to QSE q for its Ancillary Service Offers cleared in the market m for SRS, for the hour. |
| SRSFQAMTTOT | $ | Supplemental Reserve Service Failure Quantity Amount Total—The total charges to all QSEs for their capacity associated with failures on their Ancillary Service Supply Responsibilities for SRS, for the hour. |
| SRSFQAMT q | $ | Supplemental Reserve Service Failure Quantity Amount per QSE—The charge to QSE q for its total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for SRS, for the hour. |
| RTPCSRSAMTQSETOT q | $ | Procured Capacity for Supplemental Reserve Service Amount Total per QSE—The total payments to a QSE in all SASM markets for the Ancillary Service Offers cleared for SRS, for the hour. |
| PCSRSAMT q | $ | Procured Capacity for Supplemental Reserve Service Amount per QSE in DAM—The DAM SRS payment for QSE q for the hour. |
| PCSRSAMTTOT | $ | Procured Capacity for Supplemental Reserve Service Amount Total in DAM—The total of the DAM SRS payments for all QSEs for the hour. |
| q | none | A QSE. |
| m | none | A SASM for the given Operating Hour. |

(b)	Each QSE’s share of the net total costs for SRS for the Operating Hour is calculated as follows:

SRSCOST q	=	SRSPR * SRSQ q

Where:

SRSPR	=	SRSCOSTTOT / SRSQTOT

SRSQTOT	=	ΣqSRSQ q

SRSQ q	=	SRSO q – SASRSQ q

SRSO q	=	Σq(SASRSQ q + Σm(RTPCSRS q, m) + PCSRS q – SRSRP q – SRSFQ q) * HLRS q + SRSRP q

SASRSQ q	=	DASASRSQ q + RTSASRSQ q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| SRSCOST q | $ | Supplemental Reserve Service Cost per QSE—QSE q’s share of the net total costs for SRS, for the hour. |
| SRSPR | $/MW per hour | Supplemental Reserve Service Price—The price for SRS calculated based on the net total costs for SRS, for the hour. |
| SRSCOSTTOT | $ | Supplemental Reserve Service Cost Total—The net total costs for SRS for the hour. See item (a) above. |
| SRSQTOT | MW | Supplemental Reserve Service Quantity Total—The sum of every QSE’s portion of its Ancillary Service Obligation for SRS, that is not self-arranged in either DAM or any SASM, for the hour. |
| SRSQ q | MW | Supplemental Reserve Service Quantity per QSE—The portion of QSE q’s net Ancillary Service Obligation for SRS, that is not self-arranged in either DAM or any SASM, for the hour. |
| SRSO q | MW | Supplemental Reserve Service Obligation per QSE—The Ancillary Service Obligation of QSE for SRS q, for the hour. |
| DASASRSQ q | MW | Self-Arranged Supplemental Reserve Service Quantity per QSE for DAM—The self-arranged CRS quantity submitted by QSE q before 1000 in the Day-Ahead. |
| RTSASRSQ q | MW | Self-Arranged Supplemental Reserve Service Quantity per QSE for all SASMs—The sum of all self-arranged SRS quantities submitted by QSE q for all SASMs. |
| RTPCSRS q, m | MW | Procured Capacity for Supplemental Reserve Service per QSE by market—The MW portion of QSE q’s Ancillary Service Offers cleared in the market m to provide SRS, for the hour. |
| SRSFQ q | MW | Supplemental Reserve Service Failure Quantity per QSE—QSE q’s total capacity associated with failures and reconfiguration reductions on its Ancillary Service Supply Responsibility for SRS, for the hour. |
| HLRS q |  | The Hourly Load Ratio Share calculated for QSE q for the hour. See Section 6.6.2.3. |
| SRSRP q | MW | Supplemental Reserve Service Replacement per QSE per market—The total SRS capacity that was a portion of the Ancillary Service Supply Responsibility of QSE q but is replaced in a SASM, for the hour. |
| PCSRS q | MW | Procured Capacity for Supplemental Reserve Service per QSE in DAM—The total SRS capacity quantity awarded to QSE q in the DAM for all the Resources represented by the QSE for the hour. |
| SASRSQ q | MW | Total Self-Arranged Supplemental Reserve Service Quantity per QSE for all markets—The sum of all self-arranged SRS quantities submitted by QSE q for DAM and all SASMs. |
| q | none | A QSE. |
| m | none | A SASM for the given Operating Hour. |

(c)	The adjustment to each QSE’s DAM charge for SRS for the Operating Hour, due to changes during the Adjustment Period or Real-Time operations, is calculated as follows:

RTSRSAMT q	=	SRSCOST q – DASRSAMT q

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTSRSAMT q | $ | Real-Time Supplemental Reserve Service Amount per QSE—The adjustment to QSE q’s share of the costs for SRS, for the hour. |
| SRSCOST q | $ | Supplemental Reserve Service Cost per QSE—QSE q’s share of the net total costs for SRS, for the hour. |
| DASRSAMT q | $ | Day-Ahead Supplemental Reserve Service Amount per QSE—QSE q’s share of the DAM cost for SRS, for the hour. |
| q | none | A QSE. |

The above variables are defined as follows:

The above variables are defined as follows:

The above variables are defined as follows:

The above variables are defined as follows:

The above variables are defined as follows:

The above variables are defined as follows:

- 6.7.4	Real-Time Ancillary Service Imbalance Payment or Charge

(1)	Based on the Real-Time On-Line Reserve Price Adders and a Real-Time Off-Line Reserve Price Adders, ERCOT shall calculate Ancillary Service imbalance Settlement, which will make Resources indifferent to the utilization of their capacity for energy or Ancillary Service reserves, as set forth in this Section.

[NPRR626: Replace paragraph (1) above with the following upon system implementation:] (1) Based on the Real-Time On-Line Reliability Deployment Price Adders, Real-Time On-Line Reserve Price Adders and a Real-Time Off-Line Reserve Price Adders, ERCOT shall calculate Ancillary Service imbalance Settlement, which will make Resources indifferent to the utilization of their capacity for energy or Ancillary Service reserves, as set forth in this Section.

(2)	The payment or charge to each QSE for Ancillary Service imbalance is calculated based on the price calculation set forth in paragraph (11) of Section 6.5.7.3, Security Constrained Economic Dispatch, and applied to the following amounts for each QSE:

(a)	The amount of Real-Time Metered Generation from all Generation Resources, represented by the QSE for the 15-minute Settlement Interval;

(b)	The amount of On-Line capacity based on the telemetered High Sustained Limit (HSL) for all On-Line Generation Resources;

(c)	The Ancillary Service Schedule for FFRS, CRS, and SRS from Load Resources, excluding Controllable Load Resources; and

(d)	The capacity from Controllable Load Resources available to Security-Constrained Economic Dispatch (SCED);

[NPRR568: Replace items (2)(c) and (d) above with the following upon Phase 2 system implementation:] (c) The Ancillary Service Schedules for FFRS,CRS, and SRS from Load Resources, excluding Controllable Load Resources, and (d) The capacity from Controllable Load Resources available to Security-Constrained Economic Dispatch (SCED), and the amount of OFF10 capacity telemetered for all Resources;

[NPRR568: Insert item (2)(e) below upon Phase 2 system implementation and renumber accordingly:] (e) The amount of Off-Line capacity based on the OFF30 capacity telemetered for all Resources and the telemetered Ancillary Service Schedule for SRS available from Controllable Load Resources;

(e)	The amount of Ancillary Service Resource Responsibility for Reg-Up, PFRS, FFRS, CRS, and SRS for all Generation and Load Resources represented by the QSE for the 15-minute Settlement Interval.

(3)	Intermittent Renewable Resources (IRRs) with the exception of Wind-powered Generation Resources (WGRs), Resources with a telemetered ONTEST, STARTUP, or SHUTDOWN Resource Status, Resources with a telemetered net real power (in MW) less than 95% of their telemetered Low Sustained Limit (LSL), and nuclear Resources will be excluded from the amounts calculated pursuant to paragraphs (2)(a) and (b) above.

(4)	Reliability Must-Run (RMR) Units and Reliability Unit Commitment (RUC) Resources On-Line during the hour due to an ERCOT instruction, except RUC Resources that were issued a RUC Dispatch Instruction to provide Ancillary Services pursuant to paragraph (10) of Section 5.5.2, Reliability Unit Commitment (RUC) Process, and that the QSE subsequently self-committed pursuant to paragraph (11) of Section 5.5.2, will be excluded from the amounts calculated for the 15-minute Settlement Interval pursuant to paragraphs (2)(a), (b) and (c) above.

(5)	The Real-Time Off-Line Reserve Capacity for the QSE (RTOFFCAP) shall be administratively set to zero when the SCED snapshot of the Physical Responsive Capability (PRC) is less than or equal to the PRC MW at which Energy Emergency Alert (EEA) Level 1 is initiated.

(6)	The payment or charge to each QSE for the Ancillary Service Imbalance for a given 15 minute Settlement Interval is calculated as follows:

RTASIAMT q	=		(-1) * [(RTASOLIMB q * RTRSVPOR) + (RTASOFFIMB q * RTRSVPOFF)]

[NPRR626: Insert the following equation RTRDASIAMT q below upon system implementation, prior to the implementation of NPRR568 Phase 2:] RTRDASIAMT q= (-1) * (RTASOLIMB q * RTRDP)

[NPRR626: Insert the following equation RTRDASIAMT q below upon system implementation, concurrent with or after the implementation of NPRR568 Phase 2:] RTRDASIAMT q= (-1) * ((RTASOLIMB q - RTOFF10 q )* RTRDP)

Where:

RTASOLIMB q=		RTOLCAP q – [((SYS_GEN_DISCFACTOR * RTASRESP q ) * ¼) – RTSRSRESP q – RTRUCNBBRESP q – RTCLRSRSRESP q – RTNCLRSRSRESP q – RTRMRRESP q]

Where:

RTSRSRESP q =			SYS_GEN_DISCFACTOR * HSRSADJ q, r, p * ¼

RTRUCNBBRESP q  =	SYS_GEN_DISCFACTOR *  RTRUCASA q, r *  ¼

RTCLRSRSRESP q =		SYS_GEN_DISCFACTOR *  HSRSADJ q, r, p *  ¼

RTNCLRSRSRESP q =	ΣrΣp HSRSADJ q, r, p *  ¼

RTRMRRESP q =	SYS_GEN_DISCFACTOR * (HCRSADJ q, r, p + HRUADJ q, r, p + HSRSADJ q, r, p + HPFRSADJ q, r, p + HFFRSADJ q, r, p) *  ¼

RTOLCAP q =	RTOLGENCAPq + RTCLRCAP q + RTNCLRCAP q

[NPRR568: Replace the above equation RTOLCAP q with the following upon Phase 2 system implementation:] RTOLCAP q = RTOLGENCAPq + RTCLRCAP q + RTNCLRCAPq + RTOFF10 q

Where:

And, adjusted pursuant to paragraphs (3) and (4) above:

RTOLGENCAPq =  	(RTOLHSLq – RTMGQ q -  RTSRSSq)

RTOLHSL q =		SYS_GEN_DISCFACTOR * RTOLHSLR q, r, p

RTMGQ q =		SYS_GEN_DISCFACTOR * RTMG q, r, p

RTSRSS q =	ΣrΣpRTSRSSR q, r, p

RTCLRCAP q=	RTCLRNPF q – RTCLRLSL q – RTCLRSRSS q

RTNCLRCAP q=	 	RTNCLRFFRSS q + RTNCLRCRSS q

Where:

RTCLRNPF q=		SYS_GEN_DISCFACTOR * RTCLRNPFR q, r, p

RTCLRLSL q =		SYS_GEN_DISCFACTOR * RTCLRLSLR q, r, p

RTCLRSRSS q =		SYS_GEN_DISCFACTOR *  RTCLRSRSSR q, r, p

RTNCLRFFRSS q =	 RTNCLRFFRSSR q, r, p

RTNCLRCRSS q =	 RTNCLRCRSSR q, r, p

RTRSVPOR=	(RNWF  y * RTORPA y)

RTASOFFIMB q =	RTOFFCAP q – (RTSRSRESP  q + (RTCLRSRSRESP q + RTNCLRSRSRESP q)

RTOFFCAP q =	(SYS_GEN_DISCFACTOR * RTCST30HSL q) + (SYS_GEN_DISCFACTOR * RTSRSS q)+ RTCLRSRSS q + RTNCLRSRSS q

[NPRR568: Replace the above equation RTOFFCAP q with the following upon Phase 2 system implementation:] RTOFFCAP q = RTOFF30 q + RTCLRSRSS q

RTRSVPOFF=	(RNWF  y * RTOFFPA y)

[NPRR626: Insert the following equation RTRDP below upon system implementation:] RTRDP = (RNWF y * RTORDPA y)

RNWF y=	TLMP y / TLMP y

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTASIAMT q | $ | Real-Time Ancillary Service Imbalance Amount—The total payment or charge to QSE q for the Real-Time Ancillary Service imbalance for each 15-minute Settlement Interval. |
| [NPRR626: Replace the variable above RTASIAMT q with the following upon system implementation:] RTASIAMT q; $; Real-Time Ancillary Service Imbalance Amount—The total payment or charge to QSE q for the Real-Time Ancillary Service imbalance associated with ORDC for each 15-minute Settlement Interval.. |
| [NPRR626: Insert the following variable RTRDASIAMT q below upon system implementation:] RTRDASIAMT q; $; Real-Time Reliability Deployment Ancillary Service Imbalance Amount—The total payment or charge to QSE q for the Real-Time Ancillary Service imbalance associated with Reliability Deployments for each 15-minute Settlement Interval.. |
| RTASOLIMB q | MWh | Real Time Ancillary Service On-Line Reserve Imbalance for the QSE The Real-Time Ancillary Service On-Line reserve imbalance for the QSE q, for each 15-minute Settlement Interval. |
| RTORPA y | $/MWh | Real-Time On-Line Reserve Price Adder per intervalThe Real-Time Price Adder for On-Line Reserves for the SCED interval y. |
| RTOFFPA y | $/MWh | Real-Time Off-Line Reserve Price Adder per intervalThe Real-Time Price Adder for Off-Line Reserves for the SCED interval y. |
| TLMP y | second | Duration of SCED interval per intervalThe duration of the SCED interval y. |
| [NPRR626: Insert the following variables RTRDP and RTORDPA y below upon system implementation:] RTRDP; $/MWh; Real-Time On-Line Reliability Deployment PriceThe Real-Time price for the 15-minute Settlement Interval, reflecting the impact of reliability deployments on energy prices that is calculated from the Real-time On-Line Reliability Deployment Price Adder.. RTORDPA y; $/MWh; Real-Time On-Line Reliability Deployment Price AdderThe Real-Time Price Adder that captures the impact of reliability deployments on energy prices for the SCED interval y.. |
| RNWF y | none | Resource Node Weighting Factor per intervalThe weight used in the Resource Node Settlement Point Price calculation for the portion of the SCED interval y within the 15-minute Settlement Interval. |
| RTRSVPOR | $/MWh | Real-Time Reserve Price for On-Line ReservesThe Real-Time Reserve Price for On-Line Reserves for the 15-minute Settlement Interval. |
| RTRSVPOFF | $/MWh | Real-Time Reserve Price for Off-Line ReservesThe Real-Time Reserve Price for Off-Line Reserves for the 15-minute Settlement Interval. |
| RTOLCAP q | MWh | Real-Time On-Line Reserve Capacity for the QSEThe Real-Time reserve capacity of On-Line Resources available for the QSE q, for the 15-minute Settlement Interval. |
| RTOLHSLR q, r, p | MWh | Real-Time On-Line High Sustained Limit for the ResourceThe Real-Time telemetered HSL for the Resource that is available to SCED, integrated over the 15-minute Settlement Interval. |
| RTOLHSL q | MWh | Real-Time On-Line High Sustained Limit for the QSEThe Real-Time telemetered HSL for all Generation Resources available to SCED, pursuant to paragraphs (3) and (4) above, integrated over the 15-minute Settlement Interval for the QSE q, discounted by the system-wide discount factor. |
| RTASRESP q | MW | Real-Time Ancillary Service Supply Responsibility for the QSEThe Real-Time Ancillary Service Supply Responsibility for Reg-Up, PFRS, FFRS, CRS, and SRS pursuant to Section 4.4.7.4, Ancillary Service Supply Responsibility, for all Generation and Load Resources discounted by the system-wide discount factor for the QSE q, for the 15-minute Settlement Interval. |
| [NPRR568: Insert the following variable RTOFF10 q upon Phase 2 system implementation:] RTOFF10 q; MWh; Real-Time Reserve Capacity Available in Ten Minutes for the QSEThe Real-Time telemetered OFF10 reserve capacity at the time of the SCED snapshot and validated pursuant to paragraph (11) of Section 6.5.5.2, Operational Data Requirements, and discounted by the system-wide discount factor for the QSE q, time-weighted over the 15-minute Settlement Interval.. |
| RTCLRCAP q | MWh | Real-Time Capacity from Controllable Load Resources for the QSE—The Real-Time capacity and Reg-Up minus SRS available from all Controllable Load Resources available to SCED for the QSE q, integrated over the 15-minute Settlement Interval. |
| RTNCLRCAP q | MWh | Real-Time Capacity from Non-Controllable Load Resources for the QSE—The Real-Time capacity available from all Load Resources other than Controllable Load Resources providing FFRS and CRS for the QSE q, integrated over the 15-minute Settlement Interval. |
| RTOLGENCAP q | MWh | Real-Time Capacity from Generation Resources for the QSE—The Real-Time capacity available from all Generation Resources providing Reg-Up, PFRS, FFRS, and CRS for the QSE q, integrated over the 15-minute Settlement Interval. |
| RTNCLRFFRSS q | MWh | Real-Time Non-Controllable Load Resources Fast Frequency Reserve Service Schedule for the QSE—The validated Real-Time, FFRS Ancillary Service Schedule from all Load Resources other than Controllable Load Resources available to SCED discounted by the system-wide discount factor, integrated over the 15-minute Settlement Interval. |
| RTNCLRCRSS q | MWh | Real-Time Non-Controllable Load Resources Contingency Reserve Service Schedule for the QSE—The validated Real-Time, CRS Ancillary Service Schedule from all Load Resources other than Controllable Load Resources, discounted by the system-wide discount factor, integrated over the 15-minute Settlement Interval. |
| RTNCLRFFRSSR q,r,p | MWh | Real-Time Non-Controllable Load Resources Fast Frequency Reserve Service Schedule for the Resource for the QSE—The validated Real-Time FFRS Ancillary Service Schedule from the Load Resource r, which is not a Controllable Load Resource, available to SCED discounted by the system-wide discount factor, integrated over the 15-minute Settlement Interval. |
| RTNCLRCRSSR q,r,p | MWh | Real-Time Non-Controllable Load Resources Contingency Reserve Service Schedule for the Resource for the QSE—The validated Real-Time, CRS Ancillary Service Schedule from the Load Resource r, which is not a Controllable Load Resource, discounted by the system-wide discount factor, integrated over the 15-minute Settlement Interval. |
| RTCLRNPFR q, r, p | MWh | Real-Time Net Power Flow from the Controllable Load Resource—The Real-Time net power flow from the Controllable Load Resource r available to SCED integrated over the 15-minute Settlement Interval discounted by the system-wide discount factor. |
| RTCLRNPF q | MWh | Real-Time Net Power Flow from Controllable Load Resources for the QSE—The Real-Time net power flow from all Controllable Load Resources available to SCED integrated over the 15-minute Settlement Interval for the QSE q. |
| RTCLRLSLR q, r, p | MWh | Real-Time Low Sustained Limit for the Controllable Load Resource—The Real-Time LSL from the Controllable Load Resource r available to SCED integrated over the 15-minute Settlement Interval discounted by the system-wide discount factor. |
| RTCLRLSL q | MWh | Real-Time Low Sustained Limit from Controllable Load Resources for the QSE—The Real-Time LSL from Controllable Load Resources available to SCED integrated over the 15-minute Settlement Interval for the QSE q. |
| RTMG q, r, p | MWh | Real-Time Metered Generation per QSE per Settlement Point per Resource—The metered generation of Generation Resource r at Resource Node p represented by QSE q in Real-Time for the 15-minute Settlement Interval. Where for a Combined Cycle Train, the Resource r is the Combined Cycle Train. |
| RTMGQ q | MWh | Real-Time Metered Generation per QSE—The metered generation, discounted by the system-wide discount factor, of all generation Resources represented by QSE q in Real-Time for the 15-minute Settlement Interval, pursuant to paragraphs (3) and (4) above. |
| RTASOFFIMB q | MWh | Real-Time Ancillary Service Off-Line Reserve Imbalance for the QSEThe Real-Time Ancillary Service Off-Line reserve imbalance for the QSE q, for each 15-minute Settlement Interval. |
| RTOFFCAP q | MWh | Real-Time Off-Line Reserve Capacity for the QSEThe Real-Time reserve capacity of Off-Line Resources available for the QSE q, for the 15-minute Settlement Interval. |
| RTCST30HSL q | MWh | Real-Time Generation Resources with Cold Start Available in 30 MinutesThe Real-Time telemetered HSLs of Generation Resources that have telemetered an OFF Resource Status and can be started from a cold temperature state in 30 minutes and discounted by the system-wide discount factor for the QSE q, time-weighted over the 15-minute Settlement Interval. |
| RTOFFSRSHSL q | MWh | Real-Time Generation Resources with Off-Line Supplemental Reserve Service ScheduleThe Real-Time telemetered HSLs of Generation Resources that have telemetered an OFFAS Resource Status and are carrying SRS Ancillary Service Resource Responsibility, discounted by the system-wide discount factor for the QSE q, time-weighted over the 15-minute Settlement Interval. |
| [NPRR568: Delete the above two variables RTCST30HSL q and RTOFFNSHSL q and insert the following variable RTOFF30 q below upon Phase 2 system implementation:] RTOFF30 q; MWh; Real-Time Reserve Capacity Available in 30 Minutes for the QSEThe Real-Time telemetered OFF30 reserve capacity at the time of the SCED snapshot validated pursuant to paragraph (12) of Section 6.5.5.2 and discounted by the system-wide discount factor for the QSE q, time-weighted over the 15-minute Settlement Interval.. |
| RTSRSSR q, r, p | MWh | Real-Time Ancillary Service Schedule for Supplemental Reserve Service for the Generation ResourceThe validated Real-Time telemetered Ancillary Service Schedule for the SRS provided by the Generation Resource r, discounted by the system-wide discount factor, integrated over the 15-minute Settlement Interval. |
| RTSRSS q | MWh | Real-Time Ancillary Service Schedule for Supplemental Reserve Service provided by Generation Resources for the QSEThe Real-Time telemetered Ancillary Service Schedule for SRS provided by Generation Resources for the QSE q, integrated over the 15-minute Settlement Interval. |
| HCRSADJ q, r, p | MW | Ancillary Service Resource Responsibility Capacity for Contingency Reserve Service at Adjustment Period—The CRS Ancillary Service Resource Responsibility for the Resource r as seen in the last Current Operating Plan (COP) and Trades Snapshot at the end of the Adjustment Period, for the hour that includes the 15-minute Settlement Interval. |
| HRUADJ q, r, p | MW | Ancillary Service Resource Responsibility Capacity for Reg-Up at Adjustment Period—The Regulation Up Ancillary Service Resource Responsibility for the Resource r as seen in the last COP and Trades Snapshot at the end of the Adjustment Period, for the hour that includes the 15-minute Settlement Interval. |
| HFFRSADJ q, r, p | MW | Ancillary Service Resource Responsibility Capacity for Fast Frequency Reserve Service at Adjustment Period—The FFRS Ancillary Service Resource Responsibility for the Resource r as seen in the last COP and Trades Snapshot at the end of the Adjustment Period, for the hour that includes the 15-minute Settlement Interval. |
| HPFRSADJ q, r, p | MW | Ancillary Service Resource Responsibility Capacity for Primary Frequency Reserve Service at Adjustment Period—The PFRS Ancillary Service Resource Responsibility for the Resource r as seen in the last COP and Trades Snapshot at the end of the Adjustment Period, for the hour that includes the 15-minute Settlement Interval. |
| HSRSADJ q, r, p | MW | Ancillary Service Resource Responsibility Capacity for Supplemental Reserve Service at Adjustment Period—The SRS Ancillary Service Resource Responsibility for the Resource r as seen in the last COP and Trades Snapshot at the end of the Adjustment Period, for the hour that includes the 15-minute Settlement Interval. |
| RTRUCNBBRESP q | MWh | Real-Time RUC Ancillary Service Supply Responsibility for the QSE in Non-Buy-Back hoursThe Real-Time Ancillary Service Supply Responsibility for Reg-Up, PFRS, FFRS, CRS, and SRS pursuant to the Ancillary Service awards, for the 15-minute Settlement Interval that falls within a RUC-Committed Hour, discounted by the system-wide discount factor for the QSE q. |
| RTRUCASA q, r | MW | Real-Time RUC Ancillary Service AwardsThe Real-Time Ancillary Service award to the RUC Resource r for Reg-Up, PFRS, FFRS, CRS, and SRS for the hour that includes the 15-minute Settlement Interval that falls within a RUC-Committed Hour for the QSE q. |
| RTCLRSRSRESP q | MWh | Real-Time Controllable Load Resource Supplemental Reserve Service Responsibility for the QSEThe Real Time SRS Ancillary Service Supply Responsibility as set forth in the end of the Adjustment Period COP for all Controllable Load Resources available to SCED discounted by the system-wide discount factor for the QSE q, for the 15-minute Settlement Interval. |
| RTSRSRESP q | MWh | Real-Time Supplemental Reserve Service Responsibility for the QSEThe Real Time SRS Ancillary Service Supply Responsibility as set forth in the end of the Adjustment Period COP for all Generating Resources available to SCED, discounted by the system-wide discount factor for the QSE q, for the 15-minute Settlement Interval. |
| RTNCLRSRSRESP q | MWh | Real-Time Non-Controllable Load Resource Supplemental Reserve Service Responsibility for the QSEThe Real Time SRS Ancillary Service Supply Responsibility as set forth in the end of the Adjustment Period COP for all Load Resources other than Controllable Load Resources available to SCED, discounted by the system-wide discount factor for the QSE q, for the 15-minute Settlement Interval. |
| RTRMRRESP q | MWh | Real-Time Ancillary Service Supply Responsibility for RMR Units represented by the QSEThe Real-Time Ancillary Service Supply Responsibility as set forth in the end of the Adjustment Period COP for Reg-Up, PFRS, FFRS, CRS, and SRS for all RMR Units discounted by the system-wide discount factor for the QSE q, integrated over the 15-minute Settlement Interval. |
| RTCLRSRSSR q, r, p | MWh | Real-Time Supplemental Reserve Service Schedule for the Controllable Load Resource The validated Real Time telemetered SRS Ancillary Service Schedule for the Controllable Load Resource r, discounted by the system-wide discount factor, integrated over the 15-minute Settlement Interval. |
| RTCLRSRSS q | MWh | Real-Time Supplemental Reserve Service Schedule for Controllable Load Resources for the QSEThe Real Time telemetered SRS Ancillary Service Schedule for all Controllable Load Resources for the QSE q, integrated over the 15-minute Settlement Interval. |
| SYS_GEN_DISCFACTOR | none | System-Wide Discount Factor – The system-wide discount factor used to discount inputs used in the calculation of Real-Time Ancillary Services Imbalance payment or charge is calculated for each Season based on the average of the Reserve Discount Factors (RDFs) for that Season from the year prior. |
| p | none | A Resource Node Settlement Point. |
| r | none | A Generation or Load Resource. |
| y | none | A SCED interval in the 15-minute Settlement Interval. The summation is over the total number of SCED runs that cover the 15-minute Settlement Interval. |
| q | none | A QSE. |

(7) 	The payment to each QSE for the Ancillary Service reserves associated with RUC Resources that have received a RUC Dispatch to provide Ancillary Services in which the 15-minute Settlement Interval is part of a RUC Buy-Back Hour based on the RUC opt out provision set forth in paragraph (11) of Section 5.5.2 for a given 15-minute Settlement Interval is calculated as follows:

RTRUCRSVAMT q =	(-1) * (RTRUCRESP q * RTRSVPOR)

[NPRR626: Insert the following equation RTRDRUCRSVAMT q below upon system implementation:] RTRDRUCRSVAMT q = (-1) * (RTRUCRESP q * RTRDP)

Where:

RTRUCRESP q=  RTRUCASA q, r * ¼

The above variables are defined as follows:

| Variable | Unit | Description |
| --- | --- | --- |
| RTRUCRSVAMT q | $ | Real-Time RUC Ancillary Service Reserve Amount—The total payment ¦to QSE q for the Real-Time RUC Ancillary Service Reserve payment for each 15-minute Settlement Interval. |
| [NPRR626: Replace the variable RTRUCRSVAMTq above with the following upon system implementation:] RTRUCRSVAMT q; $; Real-Time RUC Ancillary Service Reserve Amount—The total payment ¦to QSE q for the Real-Time RUC Ancillary Service Reserve payment associated with ORDC for each 15-minute Settlement Interval.. |
| [NPRR626: Insert the following variable RTRDRUCRSVAMT q below upon system implementation:] RTRDRUCRSVAMT q; $; Real-Time Reliability Deployment RUC Ancillary Service Reserve Amount—The total payment ¦to QSE q for the Real-Time RUC Ancillary Service Reserve payment associated with Reliability Deployments for each 15-minute Settlement Interval.. |
| RTRUCRESP q | MWh | Real-Time RUC Ancillary Service Supply Responsibility for the QSEThe Real-Time Ancillary Service Supply Responsibility pursuant to the Ancillary Service awards for Reg-Up, PFRS, FFRS, CRS, and SRS for all RUC Resources that have opted out per paragraph (11) of Section 5.5.2 discounted by the system-wide discount factor for the QSE q, for the 15-minute Settlement Interval. |
| RTRUCASA q, r | MW | Real-Time RUC Ancillary Service AwardsThe Real-Time Ancillary Service award to the RUC Resource r for Reg-Up, PFRS, FFRS, CRS, and SRS for the 15-minute Settlement Interval that falls within a RUC-Committed Hour for the QSE q. |
| RTRSVPOR | $/MWh | Real-Time Reserve Price for On-Line ReservesThe Real-Time Reserve Price for On-Line Reserves for the 15-minute Settlement Interval. |
| [NPRR626: Insert the following variable RTRDP below upon system implementation:] RTRDP; $/MWh; Real-Time On-Line Reliability Deployment Price The Real-Time price for the 15-minute Settlement Interval, reflecting the impact of reliability deployments on energy prices that is calculated from the Real-time On-Line Reliability Deployment Price Adder.. |
| q | none | A QSE. |

- 8.1	QSE and Resource Performance Monitoring

(1)	Each QSE and Resource shall meet performance measures as described in this Section and in the Operating Guides.

(2)	ERCOT shall monitor and post the following categories of performance:

(a)	Real-Time data, for QSEs:

(i)	Telemetry performance

(b)	Regulation control performance, for QSEs and as applicable, Resource-specific performance (see also Section 8.1.1, QSE Ancillary Service and Reserves Performance Standards);

(c)	Compliance with valid Dispatch Instructions, for QSEs and Generation Resources;

(d)	Primary Frequency Response Service (PFRS) tests from hydro  Generation Resources operating in the synchronous condenser fast response mode ;

(e)	Supplying and validating data for generator models, as requested by ERCOT, for Generation Resources;

(f)	Outage scheduling and coordination, for QSEs and Resources;

(g)	Resource-specific Fast Frequency Response Service (FFRS) performance, for QSEs and Resources;

(h)	Resource-specific PFRS performance, for QSEs and Resources;

(i)	Resource-specific Contingency Reserve Service (CRS) performance, for QSEs and Resources;

(j)	Resource-specific Fast Responding Regulation Service (FRRS) performance, for QSEs and Resources;

(k)	Resource-specific Supplemental Reserve Service (SRS) performance, for QSEs and Resources;

(l)	Outage reporting, by QSEs for Resources;

(m)	Current Operating Plan (COP) metrics, for QSEs; and

(n)	Day-Ahead Reliability Unit Commitment (DRUC) and Hourly Reliability Unit Commitment (HRUC) commitment performance by QSEs and Generation Resources.

[NPRR257: Replace or insert applicable paragraphs of Section 8.1, QSE and Resource Performance Monitoring, above, with the following upon system implementation:] - 8.1 QSE and Resource Performance Monitoring (1) Each QSE and Resource shall meet performance measures as described in this Section and in the Operating Guides. (2) ERCOT shall monitor and post the following categories of performance: (a) Net dependable real power capability testing, for Resources; (b) Reactive testing, for Generation Resources, to validate Corrected Unit Reactive Limit (CURL) and Unit Reactive Limit (URL); (c) Real-Time data, for QSEs: (i) Telemetry performance; (ii) Communications system performance; (iii) Operational data requirements required under Section 6.5.5.2, Operational Data Requirements. (d) Regulation control performance, for QSEs and as applicable, Resource-specific performance (see also Section 8.1.1, QSE Ancillary Service and Reserves Performance Standards); (e) Compliance with valid Dispatch Instructions, for QSEs and Generation Resources; (f) Primary Frequency Response Service (PFRS) testing from Hydro Generation Resources operating in the synchronous condenser fast response mode ; (g) Black Start Service (BSS) test results for QSEs and Generation Resources posted to the Market Information System (MIS) Certified Area; (h) Supplying and validating data for generator models, as requested by ERCOT, for Generation Resources; (i) Outage scheduling and coordination, for QSEs and Resources; (j) Resource-specific Fast Frequency Response Service (FFRS) performance for QSEs and Resources; (k) Resource-specific PFRS performance for QSEs and Resources; (l) The QSE backup control plan for Resource energy deployment in the event of the loss of a communication path with ERCOT. ERCOT will test these plans randomly at least once a year for QSEs representing Resources; (m) Resource-specific Contingency Reserve Service (CRS) performance, for QSEs and Resources; (n) Resource-specific Fast Responding Regulation Service (FRRS) performance, for QSEs and Resources; (o) Resource-specific Supplemental Reserve Service (SRS) performance, for QSEs and Resources; (p) 24 hours per day, seven days per week qualified staffing requirement, as described in the Operating Guides, for QSEs; (q) Automatic Voltage Regulator (AVR) requirements, for QSEs and Generation Resources; (r) Staffing plan for a backup control facility or procedures in the event that the primary facility is unusable, for QSEs; (s) Outage reporting, by QSEs for Resources; (t) Current Operating Plan (COP) metrics, for QSEs; and (u) Day-Ahead Reliability Unit Commitment (DRUC) and Hourly Reliability Unit Commitment (HRUC) commitment performance by QSEs and Generation Resources.

- 8.1.1.1	Ancillary Service and Reserves Qualification and Testing

(1)	Each QSE and the Resource providing Ancillary Service must meet qualification criteria to operate satisfactorily with ERCOT.  ERCOT shall use the Ancillary Service qualification and testing program that is approved by TAC and included in the Operating Guides.  Each QSE for the Resources that it represents may only provide Ancillary Services on those Resources for which it has met the qualification criteria.

(2)	General capacity testing must be used to verify a Resource’s telemetered HSL.  Qualification tests allow the Resource and QSE to demonstrate the minimum capabilities necessary to deploy an Ancillary Service.

(3)	A Resource may be provisionally qualified for a period of 90 days and may be eligible to participate as a Resource providing Ancillary Service.  Resources that have installed the appropriate equipment with verifiable testing data may be provisionally qualified as providers of Ancillary Service.

(4)	A Load Resource may be provisionally qualified for a period of 90 days to participate as a Resource providing Ancillary Service, if the Load Resource is metered with an Interval Data Recorder (IDR) to ERCOT’s reasonable satisfaction.  A Load Resource providing Ancillary Service in Real-Time must meet the following requirements:

(a)	Electric Service Identifier (ESI ID) registration of Load Resources providing Ancillary Service by the QSE; and

(b)	Load Resource telemetry is installed and tested between QSE and ERCOT.

(5)	Provisional qualification as described herein may be revoked by ERCOT at any time for any non-compliance with provisional qualification requirements.

(6)	For those Settlement Intervals during which a Generation Resource or Load Resource behind the Generation Resource Node is engaged in testing in accordance with this Section, the provisions of Section 6.6.5, Generation Resource Base-Point Deviation Charge, will not apply to the Resource being tested beginning with the Settlement Interval immediately preceding the Settlement Interval in which ERCOT issues a Dispatch Instruction that begins the test and continuing until the end of the Settlement Interval in which the test completes.  During the same Settlement Intervals for the testing period, the Generation Resource Energy Deployment Performance (GREDP) calculated in accordance with Section 8.1.1.4.1, Regulation Service and Generation Resource/Controllable Load Resource Energy Deployment Performance, will not apply.

(7)	ERCOT shall monitor and post by Resource and by QSE the quantity of each Ancillary Service that each Resource is qualified to provide to the MIS Certified Area.  Any updates to the qualified quantities shall be posted by the twentieth of each month, to be effective beginning the first of the following month.  ERCOT may reduce the amount a Resource may contribute toward Ancillary Service if it determines unsatisfactory performance of the Resource as defined in Section 8.1.1, QSE Ancillary Service Performance Standards.

(8)	To maintain qualification with ERCOT to provide FFRS2, each Load Resource, excluding Controllable Load Resources, will be subject to a Load interruption test at a date and time determined by ERCOT and known only to ERCOT and the affected Transmission Service Provider (TSP), to verify the ability to respond to an ERCOT Dispatch Instruction.  To successfully pass this test, the Load Resource must deploy at least 95% but no more than 150%  of its Ancillary Service Resource Responsibility for FFRS2 within ten minutes of the receipt of the ERCOT Dispatch Instruction by the Load Resource’s QSE.  If a Load Resource has responded to an actual ERCOT Dispatch Instruction with at least a 95% but no more than 150%  reduction in its Ancillary Service Resource Responsibility for FFRS2 within ten minutes in the rolling 365-day period, ERCOT will use that response in lieu of a Load interruption test.  If a Load Resource has not responded to an ERCOT Dispatch Instruction with at least a 95% but no more than 150%  reduction in its Ancillary Service Resource Responsibility for FFRS2 within ten minutes, either in a deployment event or a Load interruption test, in any rolling 365-day period, it is subject to a Load interruption test by ERCOT.  QSEs may request to have individual Load Resources aggregated for the purposes of Load interruption tests.  All performance evaluations will apply on an individual Resource basis.

(9)	ERCOT may revoke the Ancillary Service qualification of any Load Resource providing FFRS2 if it fails to respond with at least 95% but no more than 150% of its Ancillary Service Resource Responsibility for FFRS2 within 30 cycles of a triggering event or within ten minutes of an ERCOT Dispatch Instruction, and such response shall be considered a failure.  Two Load Resource performance failures, either in a deployment event or a Load interruption test, within any rolling 365-day period shall result in disqualification of that Load Resource.  After six months of disqualification, the Load Resource may reapply for qualification provided it submits a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies and the disqualified Load Resource successfully passes a new Load interruption test as specified in this Section 8.1.1.1.

(10)	To maintain qualification with ERCOT to provide FFRS1, each Load Resource, excluding Controllable Load Resources, will be subject to a Load interruption test at a date and time determined by ERCOT and known only to ERCOT and the affected Transmission Service Provider (TSP), to verify the ability to respond to an ERCOT Dispatch Instruction.  To successfully pass this test, the Load Resource must deploy at least 95% but no more than 110%  of its Ancillary Service Resource Responsibility for FFRS1 within ten minutes of the receipt of the ERCOT Dispatch Instruction by the Load Resource’s QSE.  If a Load Resource has responded to an actual ERCOT Dispatch Instruction with at least a 95% but no more than 110%  reduction in its Ancillary Service Resource Responsibility for FFRS1 within ten minutes in the rolling 365-day period, ERCOT will use that response in lieu of a Load interruption test.  If a Load Resource has not responded to an ERCOT Dispatch Instruction with at least a 95% but no more than 110%  reduction in its Ancillary Service Resource Responsibility for FFRS1 within ten minutes, either in a deployment event or a Load interruption test, in any rolling 365-day period, it is subject to a Load interruption test by ERCOT.  QSEs may request to have individual Load Resources aggregated for the purposes of Load interruption tests.  All performance evaluations will apply on an individual Resource basis.

(11)	ERCOT may revoke the Ancillary Service qualification of any Resource providing FFRS1 if it fails to respond with at least 95% but no more than 110% of its Ancillary Service Resource Responsibility for FFRS1 within 30 cycles of a triggering event or within ten minutes of an ERCOT Dispatch Instruction, and such response shall be considered a failure.  Two Resource performance failures, either in a manual deployment event or a frequency triggered event, within any rolling 365-day period shall result in disqualification of that Resource.  After six months of disqualification, a Resource may reapply for qualification provided it submits a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies and the disqualified Resource successfully passes a new test as specified in Section 8.1.1.2.1.2, Fast Frequency Response Service Qualification.

- 8.1.1.2	General Capacity Testing Requirements

(1)	Within the first 15 days of each Season, each QSE shall provide ERCOT a Seasonal High Sustained Limit (HSL) for any Generation Resource with a capacity greater than ten MW that will be operated during that Season.  ERCOT shall provide an appropriate form for QSEs to submit their Seasonal HSL data.  The Seasonal HSL form shall take into account auxiliary Load and gross and net real power capability of the Generation Resource.  Each QSE shall update its COP and telemetry, as necessary, to reflect the HSL of each of its Generation Resources in a given operating interval as well as other operational limitations.  The HSL shown in the COP for a Generation Resource may not be ramp rate-limited while the Real-Time telemetered value of HSL for the Generation Resource may be ramp rate-limited by the QSE representing the Generation Resource in order for the Generation Resource to meet its HSL using the testing process described in paragraph (2) below.

(2)	To verify that the HSL reported by telemetry is achievable, ERCOT may, at its discretion, conduct an unannounced Generation Resource test.  At a time determined solely by ERCOT, ERCOT will issue a Verbal Dispatch Instruction (VDI) to the QSE to operate the designated Generation Resource at its HSL as shown in the QSE’s telemetry at the time the test is initiated.  The QSE shall immediately upon receiving the VDI release all Ancillary Service obligations carried by the unit to be tested and shall telemeter Resource Status as “ONTEST.”  The QSE shall not be required to start the designated Generation Resource if it is not already On-Line when ERCOT announces its intent to test the Resource.  If the designated Generation Resource is operating at its Low Sustained Limit (LSL) when ERCOT sends the VDI to begin the test, the QSE shall have up to 60 minutes to allow the Resource to reach 90% of its HSL as shown by telemetry and up to an additional 20 minutes for the Resource to reach the HSL shown by telemetry at the time the test is initiated.  This time requirement does not apply to nuclear-fueled Generation Resources.  If the designated Generation Resource is operating between its LSL and 50% of its HSL shown by telemetry when ERCOT begins the test, the QSE shall have 60 minutes for the Resource to reach its HSL.  If the Resource is operating at or above 50% of its HSL shown by telemetry when ERCOT begins the test, the QSE shall have 30 minutes for the Resource to reach its HSL.  Once the designated Generation Resource reaches its HSL, the QSE shall hold it at that output level for a minimum of 30 minutes.  The HSL for the designated Generation Resource shall be determined based on the Real-Time averaged MW telemetered by the Resource during the 30 minutes of constant output.  After each test, the QSE representing the Generation Resource will complete and submit the test form using the Net Dependable Capability and Reactive Capability (NDCRC) application located on the Market Information System (MIS) Secure Area within two Business Days.

[NPRR568: Insert paragraph (3) below upon Phase 2 system implementation and renumber accordingly:] (3) To verify that the OFF10 and/or OFF30 values reported by telemetry are achievable, ERCOT may, at its discretion, conduct an unannounced OFF10 and/or OFF30 test. (a) At a time determined solely by ERCOT, ERCOT will issue a VDI to the QSE to operate the designated Generation Resource at its specified capacity, which would be HSL + (OFF10 or OFF30). The OFF10 and OFF30 capacity would be as shown in the QSE’s telemetry at the time the test is initiated. The QSE shall immediately, upon receiving the VDI, release all Ancillary Service obligations carried by the Generation Resource to be tested and shall telemeter a Resource Status of “ONTEST.” The QSE shall be required to start the designated Generation Resource when it is providing OFF10 or OFF30 capacity, if it is not already On-Line when ERCOT announces its intent to test the Generation Resource. (i) If the designated Generation Resource is operating at its LSL when ERCOT sends the VDI to begin the test, the QSE shall have up to 60 minutes to allow the Generation Resource to reach 90% of its HSL as shown by telemetry and up to an additional 20 minutes for the Resource to reach the HSL shown by telemetry at the time the test is initiated. (ii) If the designated Generation Resource is operating between its LSL and 50% of its HSL shown by telemetry when ERCOT begins the test, the QSE shall have 60 minutes for the Resource to reach its HSL. (iii) If the Resource is operating at or above 50% of its HSL shown by telemetry when ERCOT begins the test, the QSE shall have 30 minutes for the Resource to reach its HSL. (b) For On-Line Resources, once the designated Generation Resource reaches its HSL, the QSE shall reach its HSL+ OFF10 capacity within an additional ten minutes or HSL+ OFF10 + OFF30 capacity within an additional 30 minutes. For On-Line Resources, the sum of HSL, OFF10, and OFF30 shall not exceed the sum of the tested value of HSL, OFF10, and OFF30. (c) For Off-Line Resources, once the QSE receives the VDI, the Resource shall reach its OFF10 capacity within ten minutes or OFF10 + OFF30 capacity within 30 minutes. For both On-Line and Off-Line tests, the QSE shall sustain at or above the current output level for a minimum of the 30 minutes in order to meet the testing requirements. The OFF10 or OFF30 value for the designated Generation Resource shall be determined based on the maximum Real-Time MW telemetered by the Resource at the end of 10 minutes for OFF10 and at the end of 30 minutes for OFF30. (d) After each test, the QSE representing the Generation Resource will complete and submit the test form using the NDCRC application located on the MIS within two Business Days. The tested value of OFF10 or OFF30 for Off-Line Resources shall be the basis for telemetered OFF10 or OFF30 capacity for the remainder of the Season unless the QSE seeks requalification.

(3)	ERCOT may test multiple Generation Resources within a single QSE within a single 24-hour period.  However, in no case shall ERCOT test more than two Generation Resources within one QSE simultaneously.  All Resources On-Line in a Combined-Cycle Configuration will be measured on an aggregate capacity basis.  All QSEs associated with a jointly owned unit will be tested simultaneously.  Hydro and wind generation will be excluded from unannounced generation capacity testing.  ERCOT shall not perform an unannounced Generation Resource test during a Watch or Energy Emergency Alert (EEA) event.  If an unannounced Generation Resource test is underway when a Watch or EEA event commences, ERCOT may cancel the test.

[NPRR588: Replace paragraph (3) above with the following upon system implementation:] (3) ERCOT may test multiple Generation Resources within a single QSE within a single 24-hour period. However, in no case shall ERCOT test more than two Generation Resources within one QSE simultaneously. All Resources On-Line in a Combined-Cycle Configuration will be measured on an aggregate capacity basis. All QSEs associated with a jointly owned unit will be tested simultaneously. Hydro, wind, and PhotoVoltaic (PV) generation will be excluded from unannounced generation capacity testing. ERCOT shall not perform an unannounced Generation Resource test during a Watch or Energy Emergency Alert (EEA) event. If an unannounced Generation Resource test is under way when a Watch or EEA event commences, ERCOT may cancel the test.

(4)	Should the designated Generation Resource fail to reach its HSL shown in its telemetry within the time frame set forth herein, the Real-Time averaged MW telemetered during the test shall be the basis for the new HSL for the designated Generation Resource for that Season.  The QSE shall have the opportunity to request another test as quickly as possible (at a time determined by ERCOT) and may retest up to two times per month.  The QSE may also demonstrate an increased value of HSL by operating the Generation Resource at an Output Schedule for at least 30 minutes.  In order to raise an output schedule above the Seasonal HSL, the QSE may set the Resource telemetered HSL equal to its output temporarily for the purposes of the demonstration tests.  After either a retest or a demonstration test, the MW capability of the Generation Resource based on the average of the MW production telemetered during the test shall be the basis for the new HSL for the designated Generation Resource for that Season.  Any requested retest must take place within three Business Days after the request for retest.

[NPRR568: Insert paragraph (5) below upon Phase 2 system implementation and renumber accordingly:] (5) Should the designated Generation Resource fail to reach its OFF10 and/or OFF30 values shown in its telemetry within the time frame set forth herein, the Real-Time averaged MW telemetered during the test shall be the basis for the new HSL or OFF10 and/or OFF30 for the designated Generation Resource for that Season. The QSE shall have the opportunity to request another test as quickly as possible (at a time determined by ERCOT) and may retest up to two times per month. After a retest, the MW capability of the Generation Resource above HSL based on the maximum of the MW production telemetered during the test shall be the basis for the new OFF10 and/or OFF30 for the designated Generation Resource for that Season. Any requested retest must take place within three Business Days after the request for retest.

(5)	The telemetered value of HSL for the Generation Resource shall only be used for testing purposes as described in this Section or for system reliability calculations.

(6)	A Resource Entity owning a hydro unit operating in the synchronous condenser fast response mode to provide hydro PFRS shall evaluate the maximum capability of the Resource each Season.

(7)	ERCOT shall maintain historical records of unannounced Generation Resource test results, using the information contained therein to adjust the Reserve Discount Factor (RDF) subject to the approval of the appropriate TAC subcommittee.  ERCOT shall report to the Reliability and Operations Subcommittee (ROS) annually or as requested by ROS the aggregated results of such unannounced testing (excluding retests), including, but not limited to, the number and total capacity of Resources tested, the percentage of Resources that met or exceeded their HSL reported by telemetry, the percentage that failed to meet their HSL reported by telemetry, and the total MW capacity shortfall of those Resources that failed to meet their HSL reported by telemetry.

(8)	QSEs who receive a VDI to operate the designated Generation Resource for an unannounced Generation Resource test may be considered for additional compensation under Section 6.6.9, Emergency Operations Settlement.  Any unannounced Generation Resource test VDI that ERCOT issues as a result of a QSE-requested retest will not be considered for additional compensation under Section 6.6.9.

(9)	All unannounced Generation Resource test VDIs will be considered as an instructed deviation for compliance purposes.

(10)	Before the start of each Season, a QSE shall provide ERCOT a list identifying each Controllable Load Resource that is expected to operate in a Season as a provider of Ancillary Service.  Prior to the beginning of each Season, QSEs shall identify the Controllable Load Resources to be tested during the Season and the specific week of the test if known.  Any Controllable Load Resource for which the QSE desires qualification to provide Ancillary Services shall have its Net Dependable Capability verified prior to providing Ancillary Services.

(11)	ERCOT shall verify the telemetry attributes of each qualified Load Resource as follows:

(a)	ERCOT shall annually verify the telemetry attributes of each Load Resource that is not a Controllable Load Resource providing Ancillary Services.  In the case of an Aggregate Load Resource (ALR), ERCOT will follow the validation procedures described in the Other Binding Document “Requirements for Aggregate Load Resource Participation in the ERCOT Markets.”  In addition, once every two years, any Load Resource qualified to provide FFRS using a high-set under-frequency relay shall test the correct operation of the under-frequency relay or the output from the solid-state switch, whichever applies.  However, if a Load Resource’s performance has been verified through response to an actual event, the data from the event can be used to meet the annual telemetry verification requirement for that year and the biennial relay-testing requirement.

(b)	ERCOT shall periodically validate the telemetry attributes of each Controllable Load Resource.  In the case of an ALR, ERCOT will follow the validation procedures described in the document titled “Requirements for Aggregate Load Resource Participation in the ERCOT Markets.”  If a QSE fails to meet its telemetry validation requirements, ERCOT may suspend the QSE and/or the Controllable Load Resource from participation in the applicable services or markets.  If disqualified pursuant to this paragraph, a QSE or Controllable Load Resource may reestablish its qualification by submitting a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies and by successfully passing a new ERCOT telemetry validation test.

(12)	Telemetry values of a Load Resource may be adjusted to reflect Distribution Losses, based on the ERCOT-forecasted Distribution Loss Factors (DLFs).  Load Resources may be adjusted for Distribution Losses using the same distribution loss code as assigned to the ESI ID.

(13)	A specific Load Resource to be used for the first time to provide Regulation, FFRS, PFRS, CRS, SRS, or energy by following Security-Constrained Economic Dispatch (SCED) Base Points, must be tested to ERCOT’s reasonable satisfaction using actual Demand response as part of its qualification.  The test must take place at a time mutually selected by the QSE representing the Load Resource and ERCOT.  ERCOT shall make available its standard test document for Load Resource qualification required under this Section on the MIS Public Area.

(14)	Any changes to a Load Resource including changes to its capability to provide Ancillary Service requires updates by the Load Resource to the registration information detailing the change.  For Non-Opt-In Entities (NOIEs) representing specific Load Resources that are located behind the NOIE Settlement Metering points, the NOIE shall provide an alternative unique descriptor of the qualified Load Resource for ERCOT’s records.

(15)	Qualification of a Resource, including a Load Resource, remains valid for that Resource in the event of a change of QSE for the Resource, provided that the new QSE demonstrates to ERCOT’s reasonable satisfaction that the new QSE has adequate communications and control capability for the Resource.

(16)	For purposes of qualifying Quick Start Generation Resources (QSGRs), ERCOT shall issue a unit-specific VDI for the MW amount that the QSE is requesting to qualify its QSGR to provide.  The QSE shall telemeter an ONTEST Resource Status.  The QSGR will only be qualified to provide an amount not to exceed the observed output at the end of a ten-minute test period.

(17)	ERCOT may revoke the QSGR qualification of any QSGR for failure to comply with the following performance standard:

(a)	A QSGR, available for deployment by SCED, is deemed to have failed to start for the purpose of this performance measure if the QSGR fails to achieve at least 90% of the minimum ERCOT SCED Base Point, including zero Base Points, within ten minutes of the initial ERCOT SCED Base Point that dispatched the QSGR above zero MW output.

(b)	ERCOT may revoke a QSGR’s qualification if within a rolling 90-day period the number of QSGR failures to start, as determined by paragraph (a) above, exceeds the higher of three failures or 10% of the number of quick start mode startups made in response to SCED deployments.

(18)	If disqualified pursuant to paragraph (17) above, a QSGR may reestablish its QSGR qualification by submitting a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies and by successfully passing a new ERCOT QSGR test.

- 8.1.1.2.1	Ancillary Service and On-Line and Off-Line Reserve Technical Requirements and Qualification Criteria and Test Methods

(1)	A QSE and the Resource that it represents must be qualified to provide Ancillary Services and On-Line and Off-Line reserves.  ERCOT shall develop and operate a qualification and testing program that meets the requirements of this Section for each Ancillary Service.

(2)	A QSE and the Resource that it represents must be qualified in accordance with this Section as an Ancillary Service and reserve provider and at ERCOT’s discretion will be required to re-qualify to provide Ancillary Service or reserve if acceptable performance as determined in accordance with this Section has not been maintained.

- 8.1.1.2.1.1	Regulation Service Qualification

(1)	A QSE control system must be capable of receiving Regulation Up Service (Reg-Up) and Regulation Down Service (Reg-Down) control signals from ERCOT’s Load Frequency Control (LFC) system, and of directing its Resources to respond to the control signals, in an upward and downward direction to balance Real-Time Demand and Resources.  A QSE providing Reg-Up or Reg-Down shall be capable of receiving ERCOT telemetered control deployments of Reg-Up or Reg-Down.

(2) 	A QSE shall demonstrate to ERCOT that they have the ability to switch control to constant frequency operation as specified in the Operating Guides.  ERCOT’s direction to the QSE to operate on constant frequency will be considered a Dispatch Instruction.

(3) 	A QSE providing Reg-Up or Reg-Down shall provide ERCOT with the data requirements of Section 6.5.5.2, Operational Data Requirements.  Resources providing Reg-Up or Reg-Down must be capable of delivering the full amount of regulating capacity offered to ERCOT within five minutes.

(4)	A Resource providing Fast Responding Regulation Service (FRRS) shall be capable of independently detecting and recording system frequency with an accuracy of at least one mHz and a resolution of no less than 30 samples per second.  The Resource shall also be capable of measuring and recording MW output with a resolution of no less than 30 samples per second.

(5)	A Reg-Up and Reg-Down qualification test for each Resource is conducted during a continuous 60-minute period agreed on in advance by the QSE and ERCOT.  QSEs may qualify a Resource to provide Reg-Up or Reg-Down, or both, in separate testing.  ERCOT shall administer the following test requirements:

(a)	ERCOT shall confirm the date and time of the test with the QSE.

(b)	For the 60-minute duration of the test, when market and reliability conditions allow, the ERCOT Control Area Operator shall send a random sequence of increasing ramp, hold, and decreasing ramp control signals to the QSE for a specific Resource.  ERCOT shall maintain a duration interval, for each increasing ramp, hold, or decreasing ramp sequence, of no less than two minutes.  The control signals may not request Resource performance beyond the HSL, LSL, and ramp rate limit agreed on prior to the test.  During the test, ERCOT shall structure the test sequence such that at least one five-minute test interval is used to test the Resource’s ability to achieve the entire amount of Reg-Up or Reg-Down requested for qualification.

(c)	ERCOT shall measure and record the average real power output for each minute of the Resource(s) being tested represented by the QSE.  During at least one five minute duration interval selected to evaluate each of the Reg-Up and Reg-Down amounts being tested, the Generation/Controllable Load Resource Energy Deployment Performance (GREDP/CLREDP) calculated in accordance with Section 8.1.1.4.1, Regulation Service and Generation Resource/Controllable Load Resource Energy Deployment Performance, over the entire five minute interval must be less than or equal to 3.5%.  Additionally, in all other test sequence intervals, the Resource’s measured GREDP/CLREDP must be less than or equal to 5% as calculated for the entire duration of each test interval.

(d)	On successful demonstration of the above test criteria, ERCOT shall qualify that the Resource is capable of providing Regulation Service and shall provide a copy of the certificate to the QSE and the Resource.  The certificate shall state the amount in MWs the Resource is qualified for Reg-Up and Reg-Down.

(e)	A QSE representing a Resource qualified to provide Regulation Service shall not offer to provide more Regulation Service than the maximum capacity that the Resource is qualified to provide, as shown in the certificate provided to the QSE and the Resource.

(6)	A QSE may also qualify a Resource to provide Fast Responding Regulation Up Service (FRRS-Up), Fast Responding Regulation Down Service (FRRS-Down), or both.  In addition to the test criteria described in paragraph (5) above, ERCOT shall verify the following capabilities through testing:

(a)	ERCOT shall confirm the date and time of the test with the QSE.

(b)	The Resource seeking FRRS qualification will be required to demonstrate that it can deploy within one second of either (i) receipt of a deployment signal from ERCOT, or (ii) a deviation of frequency in excess of +/-0.09 Hz from 60 Hz.

(c)	Upon deployment, the Resource will be required to demonstrate that it can sustain the deployment for a minimum of eight minutes at a minimum level of 95% and a maximum level of 110% of the proposed maximum capacity obligation.

(d)	ERCOT shall use the Resource’s high-resolution recorded frequency and MW output data to determine whether the Resource met its performance obligations during the test.

(e)	On successful demonstration of the above test criteria, ERCOT shall qualify that the Resource is capable of providing FRRS and shall provide a copy of the certificate to the QSE and the Resource.  The certificate shall state the amount in MWs the Resource is qualified for FRRS-Up and FRRS-Down.

(f) 	A QSE representing a Resource qualified to provide FRRS shall not offer to provide more FRRS than the maximum capacity that the Resource is qualified to provide, as shown in the certificate provided to the QSE and the Resource.

- 8.1.1.2.1.2	Fast Frequency Response Service Qualification

(1)	FFRS may be provided by:

(a) 	Unloaded Generation Resources that are On-Line;

(b) 	Load Resources controlled by high-set under-frequency relays or similar trigger mechanisms;

(c) 	Direct Current Tie (DC Tie) response that stops frequency decay; or

(d) 	Controllable Load Resources.

(2)	Each Resource providing FFRS1 must be On-Line and shall also meet the following requirements:

(a) 	The under-frequency relay or similar trigger mechanism must have a delay of no more than 20 cycles (or 0.33 seconds for relays that do not count cycles). The total time from the time frequency first decays to a value low enough to initiate action up to the time when full Ancillary Service Resource Responsibility for FFRS1 is delivered should be no more than 30 cycles, including all relay and breaker operating times;

(b)	The initiation setting of the under-frequency relay or similar trigger mechanism shall not be any lower than 59.80 Hz; and

(c)	A Resource must demonstrate its ability to sustain the scheduled level of deployment for ten minutes at a minimum level of 95% but not more than a maximum level of 110% of the MW capacity for which the Resource seeks qualification for FFRS1.

(d)	Unless it is deployed via breaker action, a Resource providing FFRS1 shall be capable of measuring and recording MW output with a resolution of no less than 30 samples per second.

(3)	Each Load Resource providing FFRS2 must be loaded and capable of unloading the scheduled amount of FFRS2 within ten minutes of instruction by ERCOT and must either be immediately responsive to system frequency or be interrupted by action of under-frequency relays or similar trigger mechanism as described in (4) below.

(4)	Resources providing FFRS2 shall also meet the following requirements:

(a)	The under-frequency relay or similar trigger mechanism must have a delay of no more than 20 cycles (or 0.33 seconds for relays that do not count cycles). The total time from the time frequency first decays to a value low enough to initiate action up to the time when full Ancillary Service Resource Responsibility for FFRS2 is delivered should be no more than 30 cycles, including all relay and breaker operating times;

(b)	The initiation setting of the under-frequency relay or similar trigger mechanism shall not be any lower than 59.70 Hz;

(c)	A Resource must demonstrate its ability to maintain the scheduled level of deployment for an hour at a minimum level of 95% but no more than a maximum level of 150% of the MW capacity that the Resource seeks qualification for FFRS2; and

(d)	Unless it is deployed via breaker action, a Resource providing FFRS2 shall be capable of measuring and recording MW output with a resolution of no less than 30 samples per second.

(5)	Any QSE providing FFRS shall be capable of receiving ERCOT telemetered control deployments of FFRS.

(6)	Load Resources on high-set under-frequency relays or similar trigger mechanisms providing FFRS must provide a telemetered output signal, including breaker status and status of the under-frequency relay or similar trigger mechanism.

(7)	A qualification test for each Resource to provide FFRS is conducted during a continuous eight-hour period agreed to by the QSE and ERCOT.  ERCOT shall confirm the date and time of the test with the QSE:

(8)	To become and remain fully qualified as a provider of FFRS a Resource shall pass simulated or actual testing according to ERCOT procedures.  A Load Resource shall also perform verification testing as described in Operating Guide Section 8, Attachment G, Load Resource Tests.

(9)	On successful demonstration of all test criteria, ERCOT shall qualify that the Resource is capable of providing FFRS and shall provide a copy of the certificate to the QSE and the Resource Entity. The certificate shall state the amount in MWs the Resource is qualified for FFRS1 and/or FFRS2.

(10)	A QSE representing a Resource qualified to provide FFRS shall not offer to provide more FFRS than the maximum capacity that the Resource is qualified to provide, as stated in the certificate provided to the QSE and the Resource.

- 8.1.1.2.1.3	Primary Frequency Response Service Qualification

(1)	PFRS may be provided by:

(a) 	Unloaded Generation Resources that are On-Line;

(b) 	Hydro Generation Resources operating in the synchronous condenser fast response mode; or

(c) 	Controllable Load Resources.

(2)	The amount of PFRS provided by an individual Resource is limited to the median of its actual performance for the last eight Measurable Events.  Each Resource providing PFRS must be On-Line and must be immediately responsive to system frequency.

(3)	Hydro Generation Resources operating in the synchronous condenser fast-response mode may qualify to provide PFRS up to the hydro Generation Resource’s proven ten-second response capability (which may be 100% of the HSL).  The initiation setting of the automatic under-frequency relay shall not be lower than 59.90 Hz;

(4)	Any QSE providing PFRS shall be capable of receiving ERCOT telemetered control deployments from SCED during the implementation of an EEA.  A QSE shall be capable of updating its Resource’s PFRS Ancillary Service Schedule within 15 seconds following ERCOT deployment instructions.

(5)	Generation Resources providing PFRS shall have their Governors in service with their settings as specified by North American Electric Reliability Corporation (NERC) Reliability Standard BAL-001-TRE-1, Primary Frequency Response in the ERCOT Region.

(6)	Each QSE shall ensure that each Resource is able to meet the Resource’s obligations to provide its Ancillary Service Resource Responsibility.

(7)	A new or previously disqualified Resource seeking PFRS qualification shall be qualified for providing PFRS up to a capacity level demonstrated in Governor tests as specified in the Operating Guides.  For any hydro Generation Resource operating as a generator, the amount of PFRS provided will be based on the maximum of 20% of its HSL or its actual performance for last eight Measurable Events.

(8)	A Private Use Network with registered Resources may use the gross HSL for qualification and establishing a limit on the amount of PFRS capacity that the Resources within the Private Use Network can provide.

(9)	After the initial qualification, a Resource’s qualification will be adjusted based on its performance as measured pursuant to NERC Reliability Standard BAL-001-TRE-1, Requirements R9 and R10.  ERCOT will limit the PFRS capacity for which an individual Resource qualifies based on the median of its performance during the last eight Measurable Events. ERCOT will measure the MW/0.1 Hz response during these events and calculate Resource’s capability for 1% or 0.6 Hz changes in frequency.

(10)	In qualifying and establishing limits on Resources for providing PFRS, ERCOT will consider the performance abilities and limitations of the technology of each Resource seeking to qualify as a PFRS provider. Because qualification requirements for different technologies may reflect their technical capabilities and limitations, ERCOT may impose other administrative limitations, including but not limited to setting a maximum limit of the total amount of capacity reservation that can be awarded to each type of Resource technology.

(11)	On successful demonstration of all test criteria, ERCOT shall qualify that the Resource is capable of providing PFRS and shall provide a copy of the certificate to the QSE and the Resource Entity.

- 8.1.1.2.1.4	Contingency Reserve Service Qualification

(1)	CRS may be provided by:

(a) 	Unloaded Generation Resources that are On-Line;

(b)	Generation Resources that are Off-Line

(c) 	Load Resources; or

(d) 	DC Ties.

(2)	CRS may only be provided from capacity that is not fulfilling any other energy or Ancillary Service capacity commitment.

(3)	Each Resource providing CRS must be capable of ramping to the Resource’s Ancillary Service Resource Responsibility for CRS within ten minutes of the notice to deploy CRS and must be able to maintain the scheduled level of deployment for the period of service commitment.

(4)	Any QSE providing CRS shall be capable of receiving ERCOT telemetered control deployments of CRS.

(5)	Load Resources providing CRS2 must provide a telemetered output signal, including breaker status.

(6)	QSEs using a Load Resource to provide CRS1 must be capable of responding to ERCOT Dispatch Instructions in a similar manner to QSEs using Generation Resource to provide CRS1.

(7)	Each QSE shall ensure that each Resource is able to meet the Resource’s obligations to provide the Ancillary Service Resource Responsibility.

(8)	A qualification test for each Resource to provide CRS is conducted during a continuous eight-hour period agreed to by the QSE and ERCOT.  ERCOT shall confirm the date and time of the test with the QSE.  ERCOT shall administer the following test requirements:

(a)	At any time during the window (selected by ERCOT when market and reliability conditions allow and not previously disclosed to the QSE), ERCOT shall notify the QSE it is to provide an amount of CRS from the Resource to be qualified equal to the amount for which the QSE is requesting qualification.  The QSE shall acknowledge the start of the test.

(b)	ERCOT shall send a signal to the Resource’s QSE to deploy CRS, indicating the MW amount.  ERCOT shall monitor the QSE’s telemetry of the Resource’s Ancillary Service Schedule for an update within 15 seconds.  ERCOT shall measure the test Resource’s response, using the criteria described in Section 8.1.1.4.4, Contingency Reserve Service Energy Deployment Criteria. The Resource will be qualified to provide CRS at an amount not to exceed the observed output at the end of a ten-minute period after receiving ERCOT’s deployment signal.

(c)	ERCOT shall qualify a Load Resource to provide CRS2 based on an evaluation of historic meter data that takes into account the Load Resource’s Load characteristics and Load shape predictability.  Such qualification will designate one or both of the measurement and verification methodologies for the Load Resource described in Section 8.1.1.4.4.

(d)	On successful demonstration of all test criteria, ERCOT shall qualify that the Resource is capable of providing CRS and shall provide a copy of the certificate to the QSE and the Resource Entity. The certificate shall state the amount in MWs for which the Resource is qualified for CRS1 or CRS2.  ERCOT may review a Load Resource’s CRS2 qualification periodically and may revoke the qualification if ERCOT determines the criteria for measurement and verification are no longer being met.

- 8.1.1.2.1.5	Supplemental Reserve Service Qualification

(1)	Each Resource providing SRS must be capable of being synchronized and ramped to its Ancillary Service Schedule for SRS within 30 minutes.  SRS may be provided from Generation Resource capacity that can ramp within 30 minutes or Load Resources capable of unloading within 30 minutes.  SRS may only be provided from capacity that is not fulfilling any other energy or capacity commitment.

(2)	A Load Resource providing SRS must provide a telemetered output signal, including breaker status.

(3)	QSEs using a Load Resource to provide SRS1 must be capable of responding to ERCOT Dispatch Instructions in a similar manner to QSEs using Generation Resource to provide SRS1.

(4)	Each QSE shall ensure that each Resource is able to meet the Resource’s obligations to provide the Ancillary Service Resource Responsibility.

(5)	For each Resource requesting qualification for SRS, a qualification test is conducted during a continuous eight hour period agreed to by the QSE and ERCOT.  ERCOT shall confirm the date and time of the test with the QSE.  ERCOT shall administer the following test requirements:

(a)	At any time during the window (selected by ERCOT when market and reliability conditions allow and not previously disclosed to the QSE), ERCOT shall notify the QSE by using the Messaging System and requesting that the QSE provide an amount of SRS from each  Resource equal to the amount for which the QSE is requesting qualification.  The QSE shall acknowledge the start of the test.

(b)	For a Generation Resource seeking qualification to provide SRS1, during the test window, ERCOT shall send a message to the QSE representing the Generation Resource to deploy SRS1.  ERCOT shall monitor the adjustment of the Generation Resource’s SRS1 Ancillary Service Schedule within five minutes for Resources that are On-Line.  ERCOT shall measure the test Resource’s response as described under Section 8.1.1.4.5, Supplemental Reserve Service Energy Deployment Criteria.

(c)	The Resource will only be qualified to provide SRS in an amount not to exceed the observed output at the end of a 30-minute period after receiving ERCOT’s deployment signal.

(d)	For Load Resources, excluding Controllable Load Resources, ERCOT shall send an instruction to deploy SRS2 and shall measure the test Resource’s response as described under Section 8.1.1.4.5.

(e)	ERCOT shall qualify a Load Resource to provide SRS2 based on an evaluation of historic meter data that takes into account the Load Resource’s Load characteristics and Load shape predictability.  Such qualification will designate one or both of the measurement and verification methodologies for the Load Resource described in paragraph (3)(f) of Section 8.1.1.4.5.  On successful completion of this review and demonstration of all test criteria, ERCOT shall qualify that the Resource is capable of providing SRS2 and shall provide a copy of the certificate to the QSE and the Resource Entity.  ERCOT may review the Load Resource’s SRS2 qualification periodically and may revoke the qualification if it determines the criteria for measurement and verification are no longer being met.

[NPRR568: Insert Section 8.1.1.2.1.7 below upon Phase 2 system implementation:] 8.1.1.2.1.7 OFF30 Reserve Qualification (1) Each qualified Resource providing OFF30 reserves must be capable of providing the designated capacity within 30 minutes of an ERCOT request during or in order to avoid an emergency. (2) Each Generation Resource providing OFF30 shall specify capability achievable in 30 minutes in the NDCRC application located on the MIS Secure Area. (3) Capacity designated as OFF30 shall not be used for SCED or any Ancillary Service and cannot be included in the telemetered HSL of the On-Line Resource or the HSL of the Off-Line Resource providing any of CRS, SRS, or OFF10. (4) For any Generation Resource requesting qualification for OFF30, a qualification test for each Resource to provide OFF30 is conducted during a continuous eight hour period agreed to by the QSE and ERCOT. ERCOT shall test the unit at the operating level above which it is expected to carry OFF30 reserve if applicable. ERCOT shall confirm the date and time of the test with the QSE using both the primary and alternate voice circuits to validate the voice circuits. ERCOT and the QSE shall confirm the nature of the test as it relates to Generation Resource configuration changes or use of power augmentation capacity. ERCOT shall administer the following test requirements. (a) At any time during the window (selected by ERCOT when market and reliability conditions allow and not previously disclosed to the QSE), ERCOT shall notify the QSE by requesting that the QSE provide an amount of OFF30 from each Generation Resource equal to the amount for which the QSE is requesting qualification. The QSE shall update its OFF30 telemetry to reflect the requested qualification amount and acknowledge the start of the test. (b) During the test window, ERCOT shall send a message to the QSE representing a Generation Resources to deploy OFF30. ERCOT shall monitor the adjustment of the Generation Resource’s OFF30 Schedule within five minutes for Resources On-Line and within 20 minutes for Resources Off-Line. ERCOT shall measure the test Generation Resource’s response as described under Section 8.1.1.4.5, OFF30 Reserve Energy Deployment Criteria. ERCOT shall evaluate the response of the Generation Resource given the current operating conditions of the system and determine the Generation Resource’s qualification to provide OFF30. ERCOT shall qualify the Resource to provide the requested OFF30 MW if the Resource satisfies the following conditions: (i) If the Resource is On-Line, the output of the Resource shall increase from HSL to HSL + OFF10 + OFF30 qualification request amount within thirty minutes. The QSE shall change the OFF30 telemetered value according to the increase in output. (ii) If the Resource is Off-Line, the Resource shall come online and the output of the Resource shall increase from zero to the OFF10 + OFF30 qualification request amount within thirty minutes. The QSE shall change the OFF30 telemetered value according to the increase in output. (c) On successful demonstration of all test criteria, ERCOT shall qualify that the Generation Resource is capable of providing OFF30 and shall provide a copy of the certificate to the QSE and the Resource Entity. (d) The information for any unit that has passed a certified OFF30 test shall be updated in the NDCRC application on the MIS Secure Area to show the corresponding capacity certified in the test.

- 8.1.1.3.2	Fast Frequency Response Service Capacity Monitoring Criteria

(1)	ERCOT shall continuously monitor the capacity of each Resource to provide FFRS.  ERCOT shall consider, for each Resource providing FFRS capacity, the qualification amount, the actual generation or Load, the Ancillary Service Schedule for FFRS, the HSL/Maximum Power Consumption (MPC), the LSL/Low Power Consumption (LPC), and any other commitments of Ancillary Service capacity.

(2)	For Load Resources providing PFRS, the amount of FFRS capacity provided must be measured as the Load Resource’s average Load level in the last five minutes before deployment.

- 8.1.1.3.3	Primary Frequency Response Service Capacity Monitoring Criteria

(1)	ERCOT shall continuously monitor the capacity of each Resource to provide PFRS.  ERCOT shall consider, for each Resource providing PFRS capacity, the qualification amount, the actual generation or Load, the dead-band, droop setting, the Ancillary Service Schedule for PFRS, the HSL/MPC, the LSL/LPC, and any other commitments of Ancillary Service capacity.

(2)	A hydro Generation Resource that is capable of providing PFRS and that has a Resource Status of ONPFR is considered to be providing frequency responsive capability to the extent that it is not using that capacity to provide energy.

- 8.1.1.3.4	Contingency Reserve Service Capacity Monitoring Criteria

(1)	ERCOT shall continuously monitor the capacity of each Resource to provide CRS.  ERCOT shall consider, for each Resource providing CRS capacity, the qualification amount, the actual generation or Load, the Ancillary Service Schedule for CRS, the HSL/MPC, the LSL/LPC, ramp rates, and any other commitments of Ancillary Service capacity.  ERCOT shall also monitor CRS provided by Resources with an OFFAS Resource Status.

(2)	For Load Resources providing CRS2, the amount of CRS2 capacity provided must be measured as the Load Resource’s average Load level in the last five minutes before deployment.

- 8.1.1.3.5	Supplemental Reserve Service Capacity Monitoring Criteria

(1)	ERCOT shall continuously monitor the capacity of each Resource to provide SRS.  ERCOT shall consider, for each Resource providing SRS capacity, the qualification amount, the actual generation  or Load, the Ancillary Service Schedule for SRS, the HSL/MPC, the LSL/LPC, ramp rates, and any other commitments of Ancillary Service capacity.  ERCOT shall also monitor SRS provided by Resources with an OFFAS Resource Status.

(2)	For Load Resources  providing SRS2, the amount of SRS2 capacity provided must be measured as the Load Resource’s average Load level in the last twenty minutes before deployment.

- 8.1.1.4.1	Regulation Service and Generation Resource/Controllable Load Resource Energy Deployment Performance

(1)	ERCOT shall limit the deployment of Regulation Service of each QSE for each LFC cycle equal to 125% of the total amount of Regulation Service in the ERCOT System divided by the number of control cycles in five minutes.

(2)	For those Resources that do not have a Resource Status of ONDSR or ONDSRREG or Wind-powered Generation Resource (WGR) Groups with no member WGR having a status of ONDSR or ONDSRREG, ERCOT shall compute the GREDP for each Generation Resource that is On-Line and released to SCED Base Point Dispatch Instructions.  The GREDP is calculated for each five-minute clock interval as a percentage and in MWs for those Resources with a Resource Status that is not ONDSR or ONDSRREG as follows:

GREDP (%) = ABS[((ATG – AEPFR)/(ABP + ARI)) – 1.0] * 100

GREDP (MW) = ABS(ATG – AEPFR – ABP - ARI)

Where:

ATG = Average Telemetered Generation = the average telemetered generation of the Generation Resource or for the aggregate of the WGRs within a WGR Group for the five-minute clock interval

ARI = Average Regulation Instruction = the amount of regulation that the Generation Resource or WGR Group should have produced based on the LFC deployment signals, calculated by LFC, during each five-minute clock interval

∆frequency is actual frequency minus 60 Hz

EPFR = Estimated Primary Frequency Response (MW) = if │∆frequency│≤ Governor Dead-Band then EPFR = zero, if not then if ∆frequency > zero, EPFR = (∆frequency - Governor Dead-Band)/((droop value * 60) – Governor Dead-Band) * HSL * -1, if not then if ∆frequency < zero, EPFR = (∆frequency + Governor Dead-Band)/((droop value * 60) – Governor Dead-Band) * HSL * -1

AEPFR = Average Estimated Primary Frequency Response = the Estimated Primary Frequency Response (MW) will be calculated every four seconds using a Resource specific droop value where 5% droop = 0.05 the Governor Dead-Band (Hz) and Resource HSL (MW) provided by the Resource Entity, and the frequency deviation (Hz) from 60 Hz and averaged for the five-minute clock interval.  The Resource-specific calculations will be aggregated for WGR Groups.

ABP = Average Base Point = the time-weighted average of a linearly ramped Base Point or sum of Base Points for WGR Groups, for the five-minute clock interval.  The linearly ramped Base Point is calculated every four seconds such that it ramps from its initial value to the SCED Base Point over a five-minute period.  The initial value of the linearly ramped Base Point will be the four-second value of the previous linearly ramped Base Point at the time the new SCED Base Point is received into the ERCOT Energy Management System (EMS).  In the event that the SCED Base Point is received after the five-minute ramp period, the linearly ramped Base Point will continue at a constant value equal to the ending four-second value of the five-minute ramp.

[NPRR588: Replace paragraph (2) above with the following upon system implementation:] (2) For those Resources that do not have a Resource Status of ONDSR or ONDSRREG or IRR Groups with no member IRR having a status of ONDSR or ONDSRREG, ERCOT shall compute the GREDP for each Generation Resource that is On-Line and released to SCED Base Point Dispatch Instructions. The GREDP is calculated for each five-minute clock interval as a percentage and in MWs for those Resources with a Resource Status that is not ONDSR or ONDSRREG as follows: GREDP (%) = ABS[((ATG – AEPFR)/(ABP + ARI)) – 1.0] * 100 GREDP (MW) = ABS(ATG – AEPFR – ABP - ARI) Where: ATG = Average Telemetered Generation = the average telemetered generation of the Generation Resource or for the aggregate of the IRRs within an IRR Group for the five-minute clock interval ARI = Average Regulation Instruction = the amount of regulation that the Generation Resource or IRR Group should have produced based on the LFC deployment signals, calculated by LFC, during each five-minute clock interval ∆frequency is actual frequency minus 60 Hz EPFR = Estimated Primary Frequency Response (MW) = if │∆frequency│≤ Governor Dead-Band then EPFR = zero, if not then if ∆frequency > zero, EPFR = (∆frequency - Governor Dead-Band)/((droop value * 60) – Governor Dead-Band) * HSL * -1, if not then if ∆frequency < zero, EPFR = (∆frequency + Governor Dead-Band)/((droop value * 60) – Governor Dead-Band) * HSL * -1 AEPFR = Average Estimated Primary Frequency Response = the Estimated Primary Frequency Response (MW) will be calculated every four seconds using a Resource specific droop value where 5% droop = 0.05 the Governor Dead-Band (Hz) and Resource HSL (MW) provided by the Resource Entity, and the frequency deviation (Hz) from 60 Hz and averaged for the five-minute clock interval. The Resource-specific calculations will be aggregated for IRR Groups. ABP = Average Base Point = the time-weighted average of a linearly ramped Base Point or sum of Base Points for IRR Groups, for the five-minute clock interval. The linearly ramped Base Point is calculated every four seconds such that it ramps from its initial value to the SCED Base Point over a five-minute period. The initial value of the linearly ramped Base Point will be the four-second value of the previous linearly ramped Base Point at the time the new SCED Base Point is received into the ERCOT Energy Management System (EMS). In the event that the SCED Base Point is received after the five-minute ramp period, the linearly ramped Base Point will continue at a constant value equal to the ending four-second value of the five-minute ramp.

(3)	For all of a QSE’s Resources that have a Resource Status of ONDSR or ONDSRREG (“Dynamically Scheduled Resource (DSR) Portfolio”), ERCOT shall calculate an aggregate GREDP as a percentage and in MWs for those Resources as follows:

GREDP (%) = ABS[(∑DSR ATG – ∑DSR DBPOS + Intra-QSE Purchase – Intra-QSE Sale – ACRSDDSRLR – ASRSDDSRLR – ∑DSR AEPFR) / (ATDSRL + ∑DSR ARI) – 1.0] * 100

GREDP (MW) = ABS(∑DSR ATG – ∑DSR DBPOS – ATDSRL– ACRSDDSRLR – ASRSDDSRLR + Intra-QSE Purchase - Intra-QSE Sale – ∑DSR AEPFR – ∑DSR ARI)

Where:

∑DSR ATG = Sum of Average Telemetered Generation for all Resources with a Resource Status of ONDSR or ONDSRREG of the QSE for the five-minute clock interval

∑DSR ARI = Sum of Average Regulation Instruction for all Resources with a Resource Status of ONDSR or ONDSRREG of the QSE for the five-minute clock interval

ATDSRL = Average Telemetered DSR Load = the average telemetered DSR Load for the QSE for the five-minute clock interval

Intra-QSE Purchase = Energy Trade where the QSE is both the buyer and seller with the flag set to “Purchase”

Intra-QSE Sale = Energy Trade where the QSE is both the buyer and seller with the flag set to “Sale”

∑DSR AEPFR = Sum of Average Estimated Primary Frequency Response for all Resources with a Resource Status of ONDSR or ONDSRREG of the QSE for the five-minute clock interval

∑DSR DBPOS = Sum of the difference between a linearly ramped Base Point minus Output Schedule for all Resources with a Resource Status of ONDSR or ONDSRREG of the QSE for the five-minute clock interval.  The linearly ramped Base Point is calculated every four seconds such that it ramps from its initial value to the SCED Base point over a five minute period

ACRSDDSRLR = Average Contingency Reserve Service  Deployment DSR Load Resource = the average CRS energy deployment for the five-minute clock interval from Load Resources that are part of the DSR Load

ASRSDDSRLR = Average Supplemental Reserve Service Deployment DSR Load Resource = the average SRS energy deployment for the five-minute clock interval from Load Resources that are part of the DSR Load

(4)	For Controllable Load Resources that have a Resource Status of ONRGL or ONCLR, ERCOT shall compute the CLREDP.  The CLREDP will be calculated both as a percentage and in MWs as follows:

CLREDP (%) = ABS[((ATPC + AEPFR)/(ABP – ARI)) – 1.0] * 100

CLREDP (MW) = ABS(ATPC – (ABP – AEPFR – ARI))

Where:

ATPC = Average Telemetered Power Consumption = the average telemetered power consumption of the Controllable Load Resource for the five-minute clock interval

ARI = Average Regulation Instruction = the amount of regulation that the Controllable Load Resource should have produced based on the LFC deployment signals, calculated by LFC, during each five-minute clock interval.  Reg-Up is considered a positive value for this calculation

AEPFR = Average Estimated Primary Frequency Response = the Estimated Primary Frequency Response (MW) will be calculated every four seconds using a Resource specific droop value where 5% droop = 0.05, the Governor Dead-Band (Hz) and Resource HSL (MW) provided by the Resource Entity, and the frequency deviation (Hz) from 60 Hz and averaged for the five-minute clock interval

ABP = Average Base Point = the time-weighted average of a linearly ramped Base Point for the five-minute clock interval.  The linearly ramped Base Point is calculated every four seconds such that it ramps from its initial value to the SCED Base Point over a five-minute period.  The initial value of the linearly ramped Base Point will be the four second value of the previous linearly ramped Base Point at the time the new SCED Base Point is received into the ERCOT EMS.  In the event that the SCED Base Point is received after the five minute ramp period, the linearly ramped Base Point will continue at a constant value equal to the ending four second value of the five-minute ramp.

(5)	ERCOT shall post to the MIS Certified Area for each QSE and for all Generation Resources or WGR Groups that are not part of a DSR Portfolio, for the DSR Portfolios, and for all Controllable Load Resources:

(a)	The percentage of the monthly five-minute clock intervals during which the Generation Resource or WGR Group was On-Line and released to SCED Base Point Dispatch Instructions;

(b)	The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR;

(c)	The percentage of the monthly five-minute clock intervals during which the Generation Resource, WGR or Controllable Load Resource was providing Regulation Service;

(d)	The percentage of the monthly five-minute clock intervals during which the Generation Resource, the WGR Group, or the DSR Portfolio was released to SCED that the GREDP was less than 2.5% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the WGR Group, or the DSR Portfolio was released to SCED that the GREDP was less than 2.5 MW;

(e)	The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was less than 2.5% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was less than 2.5 MW;

(f)	The percentage of the monthly five-minute clock intervals during which the Generation Resource, the WGR Group, or the DSR Portfolio was released to SCED that the GREDP was equal to or greater than 2.5% and equal to or less than 5.0% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the WGR Group, or the DSR Portfolio was released to SCED that the GREDP was equal to or greater than 2.5 MW and equal to or less than 5.0 MW;

(g)	The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was equal to or greater than 2.5% and equal to or less than 5.0% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was equal to or greater than 2.5 MW and equal to or less than 5.0 MW;

(h)	The percentage of the monthly five-minute clock intervals during which the Generation Resource, the WGR Group, or the DSR Portfolio was released to SCED that the GREDP was greater than 5.0% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the WGR Group, or the DSR Portfolio was released to SCED that the GREDP was greater than 5.0 MW;

(i)	The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was greater than 5.0% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was greater than 5.0 MW;

(j)	The percentage of the monthly five-minute clock intervals during which the Generation Resource, the WGR, or the DSR Portfolio was providing Regulation Service that the GREDP was less than 2.5% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the WGR, or the DSR Portfolio was providing Regulation Service that the GREDP was less than 2.5 MW;

(k)	The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was less than 2.5% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was less than 2.5 MW;

(l)	The percentage of the monthly five-minute clock intervals during which the Generation Resource, the WGR, or the DSR Portfolio was providing Regulation Service that the GREDP was equal to or greater than 2.5% and equal to or less than 5.0% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the WGR, or the DSR Portfolio was providing Regulation Service that the GREDP was equal to or greater than 2.5 MW and equal to or less than 5.0 MW;

(m)	The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was equal to or greater than 2.5% and equal to or less than 5.0% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was equal to or greater than 2.5 MW and equal to or less than 5.0 MW;

(n)	The percent of the monthly five-minute clock intervals during which the Generation Resource, the WGR, or the DSR Portfolio was providing Regulation Service that the GREDP was greater than 5.0% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the WGR, or the DSR Portfolio was providing Regulation Service that the GREDP was greater than 5.0 MW; and

(o)	The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was greater than 5.0% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was greater than 5.0 MW.

[NPRR588: Replace paragraph (5) above with the following upon system implementation:] (5) ERCOT shall post to the MIS Certified Area for each QSE and for all Generation Resources or WGR Groups that are not part of a DSR Portfolio, for the DSR Portfolios, and for all Controllable Load Resources: (a) The percentage of the monthly five-minute clock intervals during which the Generation Resource or IRR Group was On-Line and released to SCED Base Point Dispatch Instructions; (b) The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR; (c) The percentage of the monthly five-minute clock intervals during which the Generation Resource, IRR or Controllable Load Resource was providing Regulation Service; (d) The percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR Group, or the DSR Portfolio was released to SCED that the GREDP was less than 2.5% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR Group, or the DSR Portfolio was released to SCED that the GREDP was less than 2.5 MW; (e) The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was less than 2.5% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was less than 2.5 MW; (f) The percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR Group, or the DSR Portfolio was released to SCED that the GREDP was equal to or greater than 2.5% and equal to or less than 5.0% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR Group, or the DSR Portfolio was released to SCED that the GREDP was equal to or greater than 2.5 MW and equal to or less than 5.0 MW; (g) The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was equal to or greater than 2.5% and equal to or less than 5.0% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was equal to or greater than 2.5 MW and equal to or less than 5.0 MW; (h) The percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR Group, or the DSR Portfolio was released to SCED that the GREDP was greater than 5.0% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR Group, or the DSR Portfolio was released to SCED that the GREDP was greater than 5.0 MW; (i) The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was greater than 5.0% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource had a Resource Status of either ONRGL or ONCLR that the CLREDP was greater than 5.0 MW; (j) The percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR, or the DSR Portfolio was providing Regulation Service that the GREDP was less than 2.5% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR, or the DSR Portfolio was providing Regulation Service that the GREDP was less than 2.5 MW; (k) The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was less than 2.5% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was less than 2.5 MW; (l) The percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR, or the DSR Portfolio was providing Regulation Service that the GREDP was equal to or greater than 2.5% and equal to or less than 5.0% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR, or the DSR Portfolio was providing Regulation Service that the GREDP was equal to or greater than 2.5 MW and equal to or less than 5.0 MW; (m) The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was equal to or greater than 2.5% and equal to or less than 5.0% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was equal to or greater than 2.5 MW and equal to or less than 5.0 MW; (n) The percent of the monthly five-minute clock intervals during which the Generation Resource, the IRR, or the DSR Portfolio was providing Regulation Service that the GREDP was greater than 5.0% and the percentage of the monthly five-minute clock intervals during which the Generation Resource, the IRR, or the DSR Portfolio was providing Regulation Service that the GREDP was greater than 5.0 MW; and (o) The percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was greater than 5.0% and the percentage of the monthly five-minute clock intervals during which the Controllable Load Resource was providing Regulation Service that the CLREDP was greater than 5.0 MW.

(6)	ERCOT shall calculate the GREDP/CLREDP under normal operating conditions.  ERCOT shall not consider five-minute clock intervals during which any of the following events has occurred:

(a)	The five-minute intervals within the 20-minute period following an event in which ERCOT has experienced a Forced Outage causing an ERCOT frequency deviation of greater than 0.05 Hz;

(b)	Five-minute clock intervals in which ERCOT has issued Emergency Base Points to the QSE;

(c)	The five-minute clock interval following the Forced Outage of any Resource within the QSE’s DSR Portfolio that has a Resource Status of ONDSR or ONDSRREG;

[NPRR256: Replace paragraph (c) above with the following upon system implementation:] (c) The five-minute clock intervals following the Forced Outage of any Resource within the QSE’s DSR Portfolio that has a Resource Status of ONDSR or ONDSRREG continuing until the start of the next Operating Hour for which the QSE is able to adjust. If the Forced Outage of the Resource occurs within ten minutes of the start of the next Operating Hour, then ERCOT shall not consider any of the five-minute intervals between the time of the Forced Outage and continuing until the start of the second Operating Hour for which the QSE is able to adjust;

(d)	The five-minute clock intervals following a documented Forced Derate or Startup Loading Failure of a Generation Resource or any member WGR of a WGR Group.  Upon request of the reliability monitor, the QSE shall provide the following documentation regarding each Forced Derate or Startup Loading Failure:

(i)	Its generation log documenting the Forced Outage, Forced Derate or Startup Loading Failure;

(ii)	QSE (COP) for the intervals prior to, and after the event; and

(iii)	Equipment failure documentation which may include, but not be limited to, Generation Availability Data System (GADS) reports, plant operator logs, work orders, or other applicable information;

[NPRR588: Replace paragraph (d) above with the following upon system implementation:] (d) The five-minute clock intervals following a documented Forced Derate or Startup Loading Failure of a Generation Resource or any member IRR of an IRR Group. Upon request of the reliability monitor, the QSE shall provide the following documentation regarding each Forced Derate or Startup Loading Failure: (i) Its generation log documenting the Forced Outage, Forced Derate or Startup Loading Failure; (ii) QSE (COP) for the intervals prior to, and after the event; and (iii) Equipment failure documentation which may include, but not be limited to, Generation Availability Data System (GADS) reports, plant operator logs, work orders, or other applicable information;

(e)	The five-minute clock intervals where the telemetered Resource Status is set to ONTEST such as intervals during Ancillary Service Qualification and Testing as outlined in Section 8.1.1.1, Ancillary Service and Reserves Qualification and Testing, or the five-minute clock intervals during General Capacity Testing Requirements as outlined in Section 8.1.1.2, General Capacity Testing Requirements;

(f)	The five-minute clock intervals where the telemetered Resource Status is set to STARTUP;

(g)	The five-minute clock intervals where a Generation Resource’s ABP is below the average telemetered LSL;

(h)	Certain other periods of abnormal operations as determined by ERCOT in its sole discretion; and

(i)	For a Controllable Load Resource, the five-minute clock intervals in which the computed Base Points are equal to the snapshot of its telemetered power consumption.

(7)	All Generation Resources that are not part of a DSR Portfolio, excluding IRRs, and all DSR Portfolios shall meet the following GREDP criteria for each month.  ERCOT will report non-compliance of the following performance criteria to the reliability monitor:

A Generation Resource or DSR Portfolio, excluding an IRR, must have a GREDP less than the greater of X% or Y MW for 85% of the five-minute clock intervals in the month during which GREDP was calculated.

If at the end of the month during which GREDP was calculated a DSR Portfolio has a GREDP less than X% or Y MW for 85% of the five-minute clock intervals, the reliability monitor shall, at the request of the QSE with the DSR Portfolio, recalculate GREDP excluding the five-minute clock intervals following the Forced Outage of any Resource within the QSE’s DSR Portfolio that has a Resource Status of ONDSR or ONDSRREG continuing until the start of the next Operating Hour for which the QSE is able to adjust.  If the Forced Outage of the Resource occurs within ten minutes of the start of the next Operating Hour, then the reliability monitor shall not consider any of the five-minute intervals between the time of the Forced Outage and continuing until the start of the second Operating Hour for which the QSE is able to adjust.  The requesting QSE shall provide to the reliability monitor information validating the Forced Outage including the time of the occurrence of the Forced Outage and documentation of the last submitted COP status prior to the Forced Outage of the Resource for the intervals in dispute.

Additionally, all Generation Resource that are not part of a DSR Portfolio, excluding IRRs, and all DSR Portfolios will also be measured for performance specifically during intervals in which ERCOT has declared EEA Level 1 or greater.  These Resources must meet the following GREDP criteria for the time window that includes all five-minute clock intervals during which EEA was declared.  ERCOT will report non-compliance of the following performance criteria to the reliability monitor:

A Generation Resource or DSR Portfolio, excluding an IRR, must have a GREDP less than the greater of X% or Y MW.  A Generation Resource or DSR Portfolio cannot fail this criteria more than three five-minute clock intervals during which EEA was declared and GREDP was calculated.  The performance will be measured separately for each instance in which ERCOT has declared EEA.

[NPRR256: Replace paragraph (7) above with the following upon system implementation:] (7) All Generation Resources that are not part of a DSR Portfolio, excluding IRRs, and all DSR Portfolios shall meet the following GREDP criteria for each month. ERCOT will report non-compliance of the following performance criteria to the reliability monitor: A Generation Resource or DSR Portfolio, excluding an IRR, must have a GREDP less than the greater of X% or Y MW for 85% of the five-minute clock intervals in the month during which GREDP was calculated. Additionally, all Generation Resource that are not part of a DSR Portfolio, excluding IRRs, and all DSR Portfolios will also be measured for performance specifically during intervals in which ERCOT has declared EEA Level 1 or greater. These Resources must meet the following GREDP criteria for the time window that includes all five-minute clock intervals during which EEA was declared. ERCOT will report non-compliance of the following performance criteria to the reliability monitor: A Generation Resource or DSR Portfolio, excluding an IRR, must have a GREDP less than the greater of X% or Y MW. A Generation Resource or DSR Portfolio cannot fail this criteria more than three five-minute clock intervals during which EEA was declared and GREDP was calculated. The performance will be measured separately for each instance in which ERCOT has declared EEA.

(8)	All IRRs and WGR Groups shall meet the following GREDP criteria for each month.  ERCOT will report non-compliance of the following performance criteria to the reliability monitor:

An IRR or WGR Group must have a GREDP less than Z% or the ATG must be less than the expected MW output for 95% of the five-minute clock intervals in the month when the Resource or a member WGR of a WGR Group received a Base Point Dispatch Instruction in which the Base Point was two MW or more below the IRR’s HSL used by SCED.  The expected MW output includes the Resource’s Base Point, Regulation Service instructions, and any expected Primary Frequency Response.

Additionally, all IRRs and WGR Groups will also be measured for performance specifically during intervals in which ERCOT has declared EEA Level 1 or greater.  These Resources and WGR Groups must meet the following GREDP criteria for the time window that includes all five-minute clock intervals during which EEA was declared.  ERCOT will report non-compliance of the following performance criteria to the reliability monitor:

An IRR or WGR Group must have a GREDP less than Z% or the ATG must be less than the expected MW output.  An IRR or WGR Group cannot fail this criteria more than three five-minute clock intervals during which EEA was declared and the Resource or a member of a WGR Group received a Base Point Dispatch Instruction in which the Base Point was two MW or more below the IRR’s HSL used by SCED.  The performance will be measured separately for each instance in which ERCOT has declared EEA.

[NPRR588: Replace paragraph (8) above with the following upon system implementation:] (8) All IRRs and IRR Groups shall meet the following GREDP criteria for each month. ERCOT will report non-compliance of the following performance criteria to the reliability monitor: An IRR or IRR Group must have a GREDP less than Z% or the ATG must be less than the expected MW output for 95% of the five-minute clock intervals in the month when the Resource or a member IRR of an IRR Group received a Base Point Dispatch Instruction in which the Base Point was two MW or more below the IRR’s HSL used by SCED. The expected MW output includes the Resource’s Base Point, Regulation Service instructions, and any expected Primary Frequency Response. Additionally, all IRRs and IRR Groups will also be measured for performance specifically during intervals in which ERCOT has declared EEA Level 1 or greater. These Resources and IRR Groups must meet the following GREDP criteria for the time window that includes all five-minute clock intervals during which EEA was declared. ERCOT will report non-compliance of the following performance criteria to the reliability monitor: An IRR or IRR Group must have a GREDP less than Z% or the ATG must be less than the expected MW output. An IRR or IRR Group cannot fail this criteria more than three five-minute clock intervals during which EEA was declared and the Resource or a member of an IRR Group received a Base Point Dispatch Instruction in which the Base Point was two MW or more below the IRR’s HSL used by SCED. The performance will be measured separately for each instance in which ERCOT has declared EEA.

(9)	All Controllable Load Resources shall meet the following CLREDP criteria each month.  ERCOT will report non-compliance of the following performance criteria to the reliability monitor:

A Controllable Load Resource must have a CLREDP less than the greater of X% or Y MW for 85% of the five-minute clock intervals in the month during which CLREDP was calculated.

Additionally, all Controllable Load Resources will also be measured for performance specifically during intervals in which ERCOT has declared EEA Level 1 or greater.  These Resources must meet the following CLREDP criteria for the time window that includes all five-minute clock intervals during which EEA was declared.  ERCOT will report non-compliance of the following Performance criteria to the reliability monitor:

A Controllable Load Resource must have a CLREDP less than the greater of X% or Y MW.  A Controllable Load Resource cannot fail this criteria more than three five-minute clock intervals during which EEA was declared and CLREDP was calculated.  The performance will be measured separately for each instance in which ERCOT has declared EEA.

For Controllable Load Resources which are providing CRS or SRS, the following intervals will be excluded from these calculations:

(a)	Five-minute clock intervals which begin ten minutes or less after a deployment of CRS was deployed to the Resource;

(b)	Five-minute clock intervals which begin ten minutes or less after a recall of CRS when the Resource was deployed for CRS;

(c)	Five-minute clock intervals which begin 30 minutes or less after a deployment of SRS was deployed to the Resource; and

(d)	Five-minute clock intervals which begin 30 minutes or less after a recall of SRS when the Resource was deployed for SRS.

(10)	If at the end of two consecutive months during which GREDP was calculated, a Resource providing Regulation Service has a GREDP less than U% or W MW for 90% of the five-minute clock intervals in which the Resource was carrying Regulation Service Ancillary Service Resource Responsibility, the Resource shall be disqualified from providing Regulation Service.  If disqualified, after 30 days a Resource may reestablish its Regulation Service qualification by submitting a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies and by successfully passing a new requalification test.

(11)	If at the end of the month during which GREDP was calculated, a non-DSR Resource or a QSE with DSR Resources, has a GREDP less than X% or Y MW for 85% of the five-minute clock intervals, the reliability monitor shall, at the request of the QSE, recalculate GREDP excluding the five-minute clock intervals when a Resource is deployed above the unit’s ramp rate due to ramp rate sharing between energy and Regulation Service, as described in Section 6.5.7.2, Resource Limit Calculator.  The requesting QSE shall provide to the reliability monitor information validating the ramp rate violation for the intervals in dispute.

(12)	The GREDP/CLREDP performance criteria variables U, W, X, Y, and Z in paragraphs (7) through (11) above shall be subject to review and approval by TAC, and shall be posted to the MIS Public Area no later than three Business Days after TAC approval.

- 8.1.1.4.2	Fast Frequency Response Service Energy Deployment Criteria

(1)	Each QSE providing FFRS shall so indicate by appropriate entries in the relevant Resources’ Ancillary Service Schedules and by setting the Ancillary Service Resource Responsibilities accordingly. Control performance during periods in which ERCOT has deployed FFRS shall be based on the requirements below and failure to meet any one of these requirements shall be reported to Texas RE as non-compliance.

(2)	Within one minute following a deployment instruction, the QSE must update the telemetered Ancillary Service Schedule for FFRS for Generation Resources and Load Resources to reflect the deployment amount.

(3)	For any FFRS deployment event, ERCOT will collect the following data:

(a)	High speed event data from Resources that are not deployed via breaker action;

(b)	High speed event data from the recorders at ERCOT’s primary and back-up facilities;

(c)	High speed event data from phasor measurement units available to ERCOT; and

(d)	Telemetry data for all FFRS Resources with the Ancillary Service Resource Responsibility during the event.

(4) 	The performance of a Load Resource providing FFRS in response to an FFRS Dispatch Instruction shall be determined by subtracting the Load Resource’s actual Load response from the average of the telemetered net real power consumption values for the five minutes preceding the Dispatch Instruction (“meter before / meter after”).  The actual Load response is the average of the real power consumption data being telemetered to ERCOT during the Settlement Interval indicated in the Dispatch Instruction..

(5) 	For an FFRS1 deployment event triggered by an under-frequency event (frequency at or below 59.8 Hz). ERCOT will use the collected data to determine if the following requirements were met:

(a)	If the frequency reached the trip threshold for at least 20 cycles at the vicinity of where the FFRS1 Resource is located, the Ancillary Service Resource Responsibility for the Resource providing FFRS1 was fully deployed;

(b)	The Resource deployed 95% to 110% of its Ancillary Service Resource Responsibility in 30 cycles after the frequency reached 59.8 Hz;

(c)	The Resource sustained 95% to 110% of its Ancillary Service Resource Responsibility for the duration of the sustained response period, defined as ten minutes or until the time of recall instruction from ERCOT, whichever occurred first; and

(d)	The Resource restored its capability to provide its Ancillary Service Resource Responsibility within 15 minutes from the end of the deployment period.

(6)	For an FFRS1 deployment through a VDI, during implementation of the EEA, in addition to the data listed in paragraph (3) above, ERCOT will collect a voice recording of the VDI to document the time of the instruction.  The official start of the ramp period for the FFRS1 deployment is the end of the ERCOT operator’s acknowledgement that the read back of the instruction was correct.  ERCOT will use the collected data to determine if the following requirements were met:

(a)	The Resource deployed 95% to 110% of its Ancillary Service Resource Responsibility within ten minutes after the start of the ramp period;

(b)	The Resource sustained 95% to 110% of its Ancillary Service Resource Responsibility for the duration of the sustained response period, defined as ten minutes or until the time of recall instruction from ERCOT, whichever occurred first; and

(c)	The Resource restored its capability to provide its Ancillary Service Resource Responsibility within 15 minutes after ERCOT declares that the EEA is no longer needed.

(7)	For a Resource providing FFRS1 that was unable to return to its Ancillary Service Resource Responsibility within 15 minutes from the end of the deployment period, its QSE may replace the quantity of deficient FFRS1 capacity within that same 15 minutes using other Resources qualified to provide FFRS1 but not already committed to provide FFRS1.

(8)	For an FFRS2 deployment event triggered by an under-frequency event (frequency at or below 59.7 Hz), ERCOT shall use collected data to determine if the following requirements were met:

(a)	If the frequency reached the trip threshold for at least 20 cycles at the vicinity of where the FFRS2 Resource is located, the Ancillary Service Resource Responsibility for the Resource providing FFRS2 was fully deployed;

(b)	The Resource deployed 95% to 150% of its Ancillary Service Resource Responsibility in 30 cycles after the frequency reached 59.7 Hz;

(c)	The Resource sustained 95% to 150% of its Ancillary Service Resource Responsibility for the deployment period; and

(d)	The Resource returned to service by the end of the designated recovery period of 180 minutes.

(9)	For an FFRS2 deployment through a VDI, in addition to the data listed in paragraph (3) above, ERCOT will collect a voice recording of the VDI to document the time of the instruction. The official start of the ramp period for the FFRS2 deployment is the end of the ERCOT operator’s acknowledgement that the read back of the instruction was correct.  ERCOT will use the collected data to determine if the following requirements were met:

(a)	The Resource deployed 95% to 150% of its Ancillary Service Resource Responsibility by the end of the ramp period;

(b)	The Resource sustained 95% to 150% of its Ancillary Service Resource Responsibility for the deployment period; and

(c)	The Resource returned to service by the end of the designated recovery period.

(10)	For a Resource providing FFRS2 that is unable to return to its Ancillary Service Resource Responsibility within 180 minutes of recall instruction, its QSE may replace the quantity of deficient FFRS2 capacity within that same 180 minutes using Resources qualified to provide FFRS2 but not already committed to provide FFRS2.

(11)	QSEs are responsible for meeting their FFRS performance requirements at the portfolio level.  If a failure occurs at the portfolio level, as part of any compliance review ERCOT shall identify the individual Resource(s) responsible for the failure.  QSEs representing Resources providing FFRS will have an opportunity to provide ERCOT with site-specific high resolution data (at least 30 samples per second) for further analysis.  Irrespective of the QSE’s portfolio-level performance, ERCOT may require any individual Load Resource that fails to meet its FFRS performance criteria to submit a corrective action plan and may suspend a Load Resource’s qualification to provide FFRS for a pattern of non-performance.  A suspended Load Resource shall be required to successfully pass a qualification test in order to be reinstated.

- 8.1.1.4.3	Primary Frequency Response Service Energy Deployment Criteria

(1)	Each QSE providing PFRS shall so indicate by appropriate entries in the relevant Resources’ Ancillary Service Schedules and by setting the Ancillary Service Resource Responsibilities accordingly.  For Controllable Load Resources, the QSE shall control its Resources to operate their Scheduled Power Consumption minus any Ancillary Service deployments.

(2)	For all Measurable Events, ERCOT shall use the recorded data for each two-second scan rate value of real power output for each Generation Resource and Controllable Load Resource.  ERCOT shall use the recorded MW data beginning one minute before the start of the frequency excursion event until ten minutes after the start of the frequency excursion event.  Satisfactory performance must be measured by comparing actual Primary Frequency Response (PFR) to the expected PFR as required by NERC Reliability Standard BAL-001-TRE-1, Primary Frequency Response in the ERCOT Region.

- (3)	ERCOT shall monitor the PFR that is delivered during Measurable Events from Resources providing PFRS.  PFR performance must be analyzed by TAC using the performance metric specified in NERC Reliability Standard BAL-001-TRE-1.

(4) 	Performance during EEA events in which ERCOT has manually deployed PFRS shall be based on the following: within 15 seconds following a deployment instruction, the QSE must update the telemetered Ancillary Service Schedule for PFRS for Generation Resources and Controllable Load Resources to reflect the deployment amount.  The difference between the sum of the QSE’s Resource PFR schedules and the sum of the QSE’s Resource PFR responsibilities must be equal to the QSE’s total PFRS deployment instruction.

(5) 	If a Resource fails to meet the PFRS performance requirements described above, ERCOT may disqualify the Resource from providing PFRS and may take additional compliance review action. If disqualified, a Resource may reestablish its PFRS qualification no earlier than 30 days following the disqualification by:

(a) 	Submitting a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies, and

(b) 	Successfully passing a requalification test.

- 8.1.1.4.4	Contingency Reserve Service Energy Deployment Criteria

(1)	Each QSE providing CRS shall so indicate by appropriate entries in the relevant Resources’ Ancillary Service Schedules and by setting the Ancillary Service Resource Responsibilities accordingly.  For Controllable Load Resources, the QSE shall control its Resources to operate to their Scheduled Power Consumption minus any Ancillary Service deployments.

(2)  	Control performance during periods in which ERCOT has deployed CRS1 shall be based on the requirements below and failure to meet any one of these requirements for the greater of one or 5% of CRS1 deployments during a rolling 90-day period shall be reported to Texas RE as non-compliance:

(a)	Within 15 seconds following a deployment instruction, the QSE must update the telemetered Ancillary Service Schedule for CRS1 of the Resource to reflect the deployment amount.

(b)	If an Off-Line Generation Resource experiences a Startup Loading Failure (excluding those caused by operator error), the Generation Resource may be considered for exclusion from performance non-compliance if the QSE provides to ERCOT the following documentation regarding the incident:

(i)	Its generation log documenting the Startup Loading Failure; and

(ii)	Equipment failure documentation such as, but not limited to, GADS reports, plant operator logs, work orders, or other applicable information.

(c)	For Off-Line Resources with CRS1 Ancillary Service Responsibility, following deployment by Dispatch Instruction, the QSE shall adjust the resource status to an online status and have a valid Energy Offer Curve or accept a proxy Energy Offer Curve for the additional capacity.

(d)	The QSE’s telemetered ramp rate for the Resource shall be capable of deploying the full CRS1capacity within ten minutes of receipt of the Dispatch Instruction.

(3)	If disqualified pursuant to paragraph (2) above, any time after 30 days a Resource may reestablish its CRS1 qualification by submitting a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies and by successfully passing a new requalification test.

(4) 	The performance of a Load Resource providing CRS2 shall be determined by:

(a) 	Subtracting the Load Resource’s actual Load response from the average of the telemetered net real power consumption values for the five minutes preceding the Dispatch Instruction (“meter before / meter after”). The actual Load response is the average of the real power consumption data being telemetered to ERCOT during the Settlement Interval indicated in the Dispatch Instruction; or

(b) 	Using one or more of the baseline methodologies described in the Operating Guides.

(5)	For each CRS2 deployment event ERCOT will determine if the following requirements were met:

(a)	The Resource deployed 95% to 150% of its responsibility within ten minutes;

(b)	The Resource sustained 95% to 150% of its responsibility for the deployment period; and

(c)	The Resource returned to service by the end of the designated recovery period.

(6)	For a Resource providing CRS2 that is unable to return to its Ancillary Service Resource Responsibility within 180 minutes of recall instruction, its QSE may replace the quantity of deficient CRS2 capacity within that same 180 minutes using Resources qualified to provide CRS2 but not already committed to provide CRS2.  ERCOT may revoke the Ancillary Service qualification of any Resource providing CRS2 if the Resource has two or more failures within any rolling 365-day period.  If disqualified, any time after 30 days a Resource may reestablish its CRS2 qualification by submitting a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies and by successfully passing a new requalification test.

- 8.1.1.4.5	Supplemental Reserve Service Energy Deployment Criteria

(1)	Each QSE providing SRS shall so indicate by appropriate entries in the relevant Resources’ Ancillary Service Schedules and by setting the Ancillary Service Resource Responsibilities accordingly.  For Controllable Load Resources, the QSE shall control its Resources to operate to their Scheduled Power Consumption minus any Ancillary Service deployments.

(2)	ERCOT shall, as part of its Ancillary Service deployment procedure under Section 6.5.7.7.5, SRS Reserve Service Deployment, include all performance metrics for a Resource receiving an SRS recall instruction from ERCOT.

(3)	An SRS Dispatch Instruction must respect the minimum runtime of a Generation Resource.  After the recall of an SRS Dispatch Instruction, any Generation Resource providing SRS is allowed to remain On-Line for 30 minutes following the recall.  During that time period, the On-Line Generation Resource is treated as if the SRS is being provided.

(4)	Control performance during periods in which ERCOT has deployed SRS1 shall be based on the requirements below and failure to meet any one of these requirements for the greater of one or 5% of SRS1 deployments during a month shall be reported to Texas RE as non-compliance:

(a)	Within 20 minutes following a deployment instruction, the QSE must update the telemetered Ancillary Service Schedule for SRS1 for Generation Resources and Controllable Load Resources to reflect the deployment amount.

(b)	Off-Line Generation Resources, within 25 minutes following a deployment instruction, must be On-Line with an Energy Offer Curve and the telemetered net generation must be greater than or equal to the Resource’s telemetered LSL multiplied by P1 where P1 is defined in the document titled “ERCOT and QSE Operations Business Practices During the Operating Hour.”  The Resource Status that must be telemetered indicating that the Resource has come On-Line with an Energy Offer Curve is ON as described in paragraph (5)(b)(i) of Section 3.9.1, Current Operating Plan (COP) Criteria.

(c)	If an Off-Line Generation Resource experiences a Startup Loading Failure (excluding those caused by operator error), the Resource may be considered for exclusion from performance non-compliance if the QSE provides to ERCOT the following documentation regarding the incident:

(i)	Its generation log documenting the Startup Loading Failure; and

(ii)	Equipment failure documentation such as, but not limited to, Generation Availability Data System (GADS) reports, plant operator logs, work orders, or other applicable information.

(d)	Controllable Load Resources must be available to SCED, and within 25 minutes following a deployment instruction must have a Real-Time Market (RTM) Energy Bid and the telemetered net real power consumption must be greater than or equal to the Resource’s telemetered LPC.

(5) 	The performance of a Load Resource providing SRS2 in response to a SRS2 Dispatch Instruction shall be determined by:

(a) 	Subtracting the Load Resource’s actual Load response from the average of the telemetered net real power consumption values for the 20 minutes preceding the Dispatch Instruction (“meter before / meter after”). The actual Load response is the average of the real power consumption data being telemetered to ERCOT during the Settlement Interval indicated in the Dispatch Instruction; or

(b) 	Using one or more of the baseline methodologies described in the Operating Guides.

(6)	For each SRS2 deployment event ERCOT will determine if the following requirements were met:

(a)	The Resource deployed 95% to 150% of its responsibility within 30 minutes;

(b)	The Resource sustained 95% to 150% of its responsibility for the deployment period; and

(c)	The Resource returned to service by the end of the designated recovery period.

(7) 	ERCOT may revoke the Ancillary Service qualification of any Resource providing SRS2 if the Resource has two or more failures within any rolling 365-day period. If disqualified, any time after 30 days a Resource may reestablish its SRS2 qualification by submitting a corrective action plan to ERCOT that identifies actions taken to correct performance deficiencies and by successfully passing a new requalification test.

(8)	For a Resource providing SRS2 that is unable to return to its Ancillary Service Resource Responsibility within 180 minutes of recall instruction, its QSE may replace the quantity of deficient SRS2 capacity within that same 180 minutes using Resources qualified to provide SRS2 but not already committed to provide SRS2.

- 8.5.1.1	Governor in Service

At all times an All-Inclusive Generation Resource is On-Line, its Governor must remain in service and be allowed to respond to all changes in system frequency except during startup, shutdown, or testing.  A Generation Entity may not reduce Primary Frequency Response (PFR) on an individual All-Inclusive Generation Resource even during abnormal conditions without ERCOT’s consent (conveyed by way of the Resource Entity’s Qualified Scheduling Entity (QSE)) unless personnel safety and/or equipment damage is imminent.  All On-Line Generation Resources that have capacity available to either increase output or decrease output in Real-Time must provide PFR, which may make use of that available capacity.  Only Generation Resources providing Regulation Up Service (Reg-Up), Regulation Down Service (Reg-Down), Primary Frequency Response Service (PFRS), Contingency Reserve Service (CRS), or Supplemental Reserve Service (SRS), as specified in Section 8.1.1, QSE Ancillary Service and Reserves Performance Standards, shall be required to reserve capacity that may also be used to provide PFR.

- 9.2.3	DAM Settlement Charge Types

ERCOT shall provide, on each Settlement Statement, the dollar amount for each DAM Settlement charge and payment.  The DAM settlement “Charge Types” are:

(a)	Section 4.6.2.1, Day-Ahead Energy Payment;

(b)	Section 4.6.2.2, Day-Ahead Energy Charge;

(c)	Section 4.6.2.3.1, Day-Ahead Make-Whole Payment;

(d)	Section 4.6.2.3.2, Day-Ahead Make-Whole Charge;

(e)	Section 4.6.3, Settlement for PTP Obligations Bought in DAM;

(f)	Section 4.6.4.1.1, Regulation Up Service (Reg-Up) Payment;

(g)	Section 4.6.4.1.2, Regulation Down Service (Reg-Down) Payment;

(h)	Section 4.6.4.1.3, Primary Frequency Response Service (PFRS) Payment;

(i)	Section 4.6.4.1.4, Fast Frequency Response Reserve Service (FFRS) Payment;

(j)	Section 4.6.4.1.5, Contingency Reserve Service (CRS) Payment;

(k) 	Section 4.6.4.1.6, Supplemental Reserve Service (SRS) Payment;

(l)	Section 4.6.4.2.1, Regulation Up Service (Reg-Up) Charge;

(m)	Section 4.6.4.2.2, Regulation Down Service (Reg-Down) Charge;

(n)	Section 4.6.4.2.3, Primary Frequency Response Service (PFRS) Charge;

(o)	Section 4.6.4.2.4, Fast Frequency Response Service (FFRS) Charge;

(p)	Section 4.6.4.2.5, Contingency Reserve Service (CRS) Charge;

(q)	Section 4.6.4.2.6, Supplemental Reserve Service (SRS) Charge;

(r)	Section 7.9.1.1, Payments and Charges for PTP Obligations Settled in DAM;

(s)	Section 7.9.1.2, Payments for PTP Options Settled in DAM;

(t)	Section 7.9.1.4, Payments for FGRs Settled in DAM;

(u)	Section 7.9.1.5, Payments and Charges for PTP Obligations with Refund Settled in DAM;

(v)	Section 7.9.1.6, Payments for PTP Options with Refund Settled in DAM; and

(w)	Section 7.9.3.3, Shortfall Charges to CRR Owners, Item 2 and Item 4.

- 9.5.3	Real-Time Market Settlement Charge Types

(1)	ERCOT shall provide, on each RTM Settlement Statement, the dollar amount for each RTM Settlement charge and payment.  The RTM Settlement “Charge Types” are:

(a)	Section 5.7.1, RUC Make-Whole Payment;

(b)	Section 5.7.2, RUC Clawback Charge;

(c)	Section 5.7.3, Payment When ERCOT Decommits a QSE-Committed Resource;

(d)	Section 5.7.4.1, RUC Capacity-Short Charge;

(e)	Section 5.7.4.2, RUC Make-Whole Uplift Charge;

(f)	Section 5.7.5, RUC Clawback Payment;

(g)	Section 5.7.6, RUC Decommitment Charge;

(h)	Section 6.6.3.1, Real-Time Energy Imbalance Payment or Charge at a Resource Node;

(i)	Section 6.6.3.2, Real-Time Energy Imbalance Payment or Charge at a Load Zone;

(j)	Section 6.6.3.3, Real-Time Energy Imbalance Payment or Charge at a Hub;

(k)	Section 6.6.3.4, Real-Time Energy Payment for DC Tie Import;

(l)	Section 6.6.3.5, Real-Time Payment for a Block Load Transfer Point;

(m)	Section 6.6.3.6, Real-Time Energy Charge for DC Tie Export Represented by the QSE Under the Oklaunion Exemption;

(n)	Section 6.6.4, Real-Time Congestion Payment or Charge for Self-Schedules;

(o)	Section 6.6.5.1.1.1, Base Point Deviation Charge for Over Generation;

(p)	Section 6.6.5.1.1.2, Base Point Deviation Charge for Under Generation;

(q)	Section 6.6.5.2, IRR Generation Resource Base Point Deviation Charge;

(r)	Section 6.6.5.4, Base Point Deviation Payment;

(s)	Section 6.6.6.1, RMR Standby Payment;

(t)	Section 6.6.6.2, RMR Payment for Energy;

(u)	Section 6.6.6.3, RMR Adjustment Charge;

(v)	Section 6.6.6.4, RMR Charge for Unexcused Misconduct;

(w)	Section 6.6.6.5, RMR Service Charge;

(x)	Paragraph (2) of Section 6.6.7.1, Voltage Support Service Payments;

(y)	Paragraph (4) of Section 6.6.7.1;

(z)	Section 6.6.7.2, Voltage Support Charge;

(aa)	Section 6.6.8.1, Black Start Hourly Standby Fee Payment;

(bb)	Section 6.6.8.2, Black Start Capacity Charge;

(cc)	Section 6.6.9.1, Payment for Emergency Power Increase Directed by ERCOT;

(dd)	Section 6.6.9.2, Charge for Emergency Power Increases;

(ee)	Section 6.6.10, Real-Time Revenue Neutrality Allocation;

(ff)	Paragraph (a) of Section 6.7.1, Payments for Ancillary Service Capacity Sold in a Supplemental Ancillary Service Market;

(gg)	Paragraph (b) of Section 6.7.1;

(hh)	Paragraph (c) of Section 6.7.1;

(ii)	Paragraph (d) of Section 6.7.1;

(jj)	Paragraph (e) of Section 6.7.1;

(kk)	Paragraph (f) of Section 6.7.1;

(ll)	Paragraph (a) of Section 6.7.2, Charges for Ancillary Service Capacity Replaced Due to Failure to Provide;

(mm)	Paragraph (b) of Section 6.7.2;

(nn)	Paragraph (c) of Section 6.7.2;

(oo)	Paragraph (d) of Section 6.7.2;

(pp)	Paragraph (e) of Section 6.7.2;

(qq)	Paragraph (f) of Section 6.7.2;

(rr)	Paragraph (2) of Section 6.7.3, Adjustments to Cost Allocations for Ancillary Services Procurement;

(ss)	Paragraph (3) of Section 6.7.3;

(tt)	Paragraph (4) of Section 6.7.3;

(uu)	Paragraph (5) of Section 6.7.3;

(vv)	Paragraph (6) of Section 6.7.3;

(ww)	Paragraph (7) of Section 6.7.3;

(xx)	Paragraph (6) of Section 6.7.4, Real-Time Ancillary Service Imbalance Payment or Charge;

(yy)	Paragraph (7) of Section 6.7.4;

(zz) 	Section 6.7.5, Real Time Ancillary Service Imbalance Revenue Neutrality Allocation;

(aaa)	Section 7.9.2.1, Payments and Charges for PTP Obligations Settled in Real-Time;

(bbb)	Paragraph (3) of Section 7.9.3.3, Shortfall Charges to CRR Owners; and

(ccc)	Section 9.16.1, ERCOT System Administration Fee.

[NPRR626: Replace paragraph (1) above with the following upon system implementation:] (1) ERCOT shall provide, on each RTM Settlement Statement, the dollar amount for each RTM Settlement charge and payment. The RTM Settlement “Charge Types” are: (a) Section 5.7.1, RUC Make-Whole Payment; (b) Section 5.7.2, RUC Clawback Charge; (c) Section 5.7.3, Payment When ERCOT Decommits a QSE-Committed Resource; (d) Section 5.7.4.1, RUC Capacity-Short Charge; (e) Section 5.7.4.2, RUC Make-Whole Uplift Charge; (f) Section 5.7.5, RUC Clawback Payment; (g) Section 5.7.6, RUC Decommitment Charge; (h) Section 6.6.3.1, Real-Time Energy Imbalance Payment or Charge at a Resource Node; (i) Section 6.6.3.2, Real-Time Energy Imbalance Payment or Charge at a Load Zone; (j) Section 6.6.3.3, Real-Time Energy Imbalance Payment or Charge at a Hub; (k) Section 6.6.3.4, Real-Time Energy Payment for DC Tie Import; (l) Section 6.6.3.5, Real-Time Payment for a Block Load Transfer Point; (m) Section 6.6.3.6, Real-Time Energy Charge for DC Tie Export Represented by the QSE Under the Oklaunion Exemption; (n) Section 6.6.4, Real-Time Congestion Payment or Charge for Self-Schedules; (o) Section 6.6.5.1.1.1, Base Point Deviation Charge for Over Generation; (p) Section 6.6.5.1.1.2, Base Point Deviation Charge for Under Generation; (q) Section 6.6.5.2, IRR Generation Resource Base Point Deviation Charge; (r) Section 6.6.5.4, Base Point Deviation Payment; (s) Section 6.6.6.1, RMR Standby Payment; (t) Section 6.6.6.2, RMR Payment for Energy; (u) Section 6.6.6.3, RMR Adjustment Charge; (v) Section 6.6.6.4, RMR Charge for Unexcused Misconduct; (w) Section 6.6.6.5, RMR Service Charge; (x) Paragraph (2) of Section 6.6.7.1, Voltage Support Service Payments; (y) Paragraph (4) of Section 6.6.7.1; (z) Section 6.6.7.2, Voltage Support Charge; (aa) Section 6.6.8.1, Black Start Hourly Standby Fee Payment; (bb) Section 6.6.8.2, Black Start Capacity Charge; (cc) Section 6.6.9.1, Payment for Emergency Power Increase Directed by ERCOT; (dd) Section 6.6.9.2, Charge for Emergency Power Increases; (ee) Section 6.6.10, Real-Time Revenue Neutrality Allocation; (ff) Paragraph (a) of Section 6.7.1, Payments for Ancillary Service Capacity Sold in a Supplemental Ancillary Service Market; (gg) Paragraph (b) of Section 6.7.1; (hh) Paragraph (c) of Section 6.7.1; (ii) Paragraph (d) of Section 6.7.1; (jj) Paragraph (e) of Section 6.7.1; (kk) Paragraph (f) of Section 6.7.1; (ll) Paragraph (a) of Section 6.7.2, Charges for Ancillary Service Capacity Replaced Due to Failure to Provide; (mm) Paragraph (b) of Section 6.7.2; (nn) Paragraph (c) of Section 6.7.2; (oo) Paragraph (d) of Section 6.7.2; (pp) Paragraph (e) of Section 6.7.2; (qq) Paragraph (f) of Section 6.7.2; (rr) Paragraph (2) of Section 6.7.3, Adjustments to Cost Allocations for Ancillary Services Procurement; (ss) Paragraph (3) of Section 6.7.3; (tt) Paragraph (4) of Section 6.7.3; (uu) Paragraph (5) of Section 6.7.3; (vv) Paragraph (6) of Section 6.7.3; (ww) Paragraph (7) of Section 6.7.3; (xx) Paragraph (6) of Section 6.7.4, Real-Time Ancillary Service Imbalance Payment or Charge (Real-Time Ancillary Service Imbalance Amount); (yy) Paragraph (6) of Section 6.7.4, (Real-Time Reliability Deployment Ancillary Service Imbalance Amount); (zz) Paragraph (7) of Section 6.7.4; (aaa) Paragraph (7) of Section 6.7.4, (Real-Time RUC Ancillary Service Reserve Amount); (bbb) Paragraph (7) of Section 6.7.4, (Real-Time Reliability Deployment RUC Ancillary Service Reserve Amount); (ccc) Section 6.7.5, Real Time Ancillary Service Imbalance Revenue Neutrality Allocation (Load-Allocated Ancillary Service Imbalance Revenue Neutrality Amount); (ddd) Section 6.7.5, (Load-Allocated Reliability Deployment Ancillary Service Imbalance Revenue Neutrality Amount); (eee) Section 7.9.2.1, Payments and Charges for PTP Obligations Settled in Real-Time; (fff) Paragraph (3) of Section 7.9.3.3, Shortfall Charges to CRR Owners; and (ggg) Section 9.16.1, ERCOT System Administration Fee.

(2)	In the event that ERCOT is unable to execute the Day-Ahead Market (DAM), ERCOT shall provide, on each RTM Settlement Statement, the dollar amount for the following RTM Congestion Revenue Right (CRR) Settlement charges and payments:

(a)	Section 7.9.2.4, Payments for FGRs in Real-Time; and

(b)	Section 7.9.2.5, Payments and Charges for PTP Obligations with Refund in Real-Time.