| NPRR Number | 562 | NPRR Title | Subsynchronous Resonance |
| --- | --- | --- | --- |
| Date |  | December 31, 2015 |  |
| Submitter’s Information |  |  |  |
| Name |  | Michael Juricek |  |
| E-mail Address |  | michael.juricek@oncor.com |  |
| Company |  | Oncor Electric Delivery |  |
| Phone Number |  | 214-743-6771 |  |
| Cell Number |  | 214-490-0748 |  |
| Market Segment |  | Investor Owned Utility (IOU) |  |

Comments

Oncor Electric Delivery (Oncor) appreciates the opportunity to work with ERCOT and others in developing an approach to Subsynchronous Resonance (SSR) and submits the following comments in response to the ERCOT’s December 10, 2015, comments. The attached document is a redline of more detailed comments regarding the proposed scope for the full SSR studies.

Oncor’s most urgent concern is ERCOT’s proposed timeline to complete detailed studies by the end of the first quarter of 2016.  Even assuming that the study scope had been finalized, Oncor cannot complete the studies within this time.  Depending on the time needed to document the study scope, Oncor suggests a more realistic timeline for study completion is the second or third quarter of 2016.  Other TSPs may be similarly situated.

A secondary concern is whether a final study scope can be determined prior to completing the current round of studies.  SSR studies do not have the well-established scope of steady-state or short-circuit analyses, and the study criteria have been “under construction” for several years.  For some of the existing resources Oncor has been asked to study, this will be the second round of detailed studies.  The “do-overs” have resulted from changed study scopes and additional generator data.  The study costs for existing generators are not recoverable capital costs and are not funded like new generator interconnection studies.  The potential for iterative studies of existing generators compounds this cost issue.

Each concern drives Oncor’s desire for greater certainty regarding the study scope, even though such certainty may also create additional delay.

Additionally, Oncor offers the following questions and comments regarding ERCOT’s December 4 workshop presentation:

- How will ERCOT use the data from completed frequency scans to develop the topology screening criteria for the detailed studies?  Have the scan data created a clear pattern for potential generator vulnerability?

- The presentation states 69 kV circuit outages have only a marginal impact on SSR vulnerability.  Has ERCOT determined the impact for 138 kV outages?

- Regarding Slide 17:  When engaging in the annual and RPG project review, Oncor urges ERCOT to consider and incorporate protection by Resources as well as mitigation.  Generator protection should not be limited only to new Resources.

- In the determination of “new” or “existing” status for Resources, ERCOT may also wish to consider whether the Resource received notification of the SSR vulnerability during the initial phases of its interconnection process.

- Revisions to binding documents should not start until the topology screening criteria is finalized.

Revised Cover Page Language

Oncor has no comments at this time.

Revised Proposed Protocol Language

Oncor has no comments at this time.