## Slide 1
Lubbock Integration Study
TAC
May 26, 2016

## Slide 2: Background
In September 2015 the PUCT asked ERCOT to study the integration of the Lubbock Power and Light (LP&L) System into ERCOT
Objective: Identify transmission facilities that will be required to integrate the LP&L load and transmission network into the ERCOT Grid and satisfy ERCOT and NERC Transmission Planning reliability standards in the most efficient way possible.
Scope and Assumptions:
    http://www.ercot.com/calendar/2015/12/15/31834-RPG

## Slide 3: LP&L System
466 MW peak load (593 MW in the high growth scenario)
130 MW of natural gas generation at three plants
115 kV and 69 kV network
Approximately 20 substations

## Slide 4: Approach
Short Listed Options
Steady State and Maintenance Reliability Analysis
Load Deliverability Analysis
Panhandle Export Analysis (WSCR)
Capital Cost Analysis
Production Cost Analysis
Stability and SSR Analysis

## Slide 5: Results
ERCOT evaluated over 40 options
All options with at least three independent sources to serve the LP&L System met the reliability criteria with sufficient margin for future load growth
Selection of preferred option based primarily on economics

## Slide 6: Cost Comparison
Case | Upgrade | Capital Cost Estimate | Relative Annual Capital ¦ Production Cost ($Million) | % of Relative Capital
LP&L Option 1 | McKenzie-North 115 kV & CO-OP-McKenzie 69 kV | $311,818,800 | 0 ¦ 0 | 
LP&L Option 4 |  | $344,443,600 | +$32.6 ¦ -$0.3 | -0.9%
LP&L Option 4ow | McKenzie-North 115 kV & CO-OP-McKenzie 69 kV | $364,081,400 | +$52.3 ¦ -$11.3 | -21.6%
LP&L Option 8A |  | $426,107,200 | +$114.3 ¦ -$11.5 | -10.1%
LP&L Option 8B |  | $338,096,600 | +$26.3 ¦ -$5.2 | -19.8%
LP&L Option 11 |  | $492,368,200 | +$180.5 ¦ -$2.6 | -1.4%
LP&L Option 11 | McKenzie-North 115 kV | $492,368,200 | +$180.5 ¦ -$5.7 | -3.2%
LP&L Option 12 |  | $397,751,918 | +$85.9 ¦ +$1.0 | +1.2%
LP&L Option 12 | Holly-Wadsworth 115 kV | $397,751,918 | +$85.9 ¦ -$3.5 | -4.1%
LP&L Option 12c |  | $391,751,918 | +$79.9 ¦ -$0.2 | -0.3%
LP&L Option 20 |  | $466,552,338 | +$154.7 ¦ +$1.3 | +0.8%
SHY Option 1-2a |  | $383,800,200 | +$72.0 ¦ -$0.6 | -0.8%
SHY Option 1-2b |  | $365,076,200 | +$53.3 ¦ -$0.8 | -1.5%
Note: Increased capital expenditure meets economic criteria per ERCOT Protocols 3.11.2(5)

## Slide 7: Short-Listed Options: Option 1
Cost Estimate: $312 million
New 345 kV ROW: 113 miles
Panhandle Export Limit: 3902 MW

## Slide 8: Short-Listed Options: Option 4ow
Cost Estimate: $364 million
New 345 kV ROW: 141 miles
Panhandle Export Limit: 4246 MW

## Slide 9: Short-Listed Options: Option 8B
Cost Estimate: $338 million
New 345 kV ROW: 129 miles
Panhandle Export Limit: 4029 MW

## Slide 10: Stage 2 Panhandle Upgrade Roadmap
http://www.ercot.com/news/presentations/2014

## Slide 11: Option 4ow Expandability
Additional 345 kV ROW: 0 miles
Internal LP&L Congestion = Yes
Panhandle Export Limit: 4454 MW
Additional 345 kV ROW: 16 miles
Internal LP&L Congestion = No
Panhandle Export Limit: 4350 MW

## Slide 12: Comparison of Options
ERCOT Preferred Option highlighted in green
Metric | LP&L Option 1 | LP&L Option 8B | LP&L Option 4ow
Total Capital Cost ($M) | $312 | $338 | $364
Relative Capital Cost Compared to Option 1 ($M) | - | +$26.3 | +$52.3
Relative Annual Production Cost Savings Compared to Option 1 ($M) | - | -$5.2 | -$11.3
Relative Production Cost as Percent of Relative Capital Cost | - | -19.8% | -21.6%
Panhandle Export Limit (Based on WSCR = 1.5) | 3902 MW | 4029 MW | 4246 MW
Miles of new 345 kV Right of Way | 113 | 129 | 141
Aligned with April 2014 Panhandle Study Roadmap | No | No | Yes
Lubbock Load Serving Capability (MW) | 715 | 819 | 822

## Slide 13: ERCOT Recommendation
Option 4ow is the most efficient alternative for integrating the Lubbock Power and Light System into ERCOT
  Meets applicable reliability criteria with significant margin for future load growth and/or local generation retirement
  Additional cost compared to lowest cost option is economically justified
  Lowest societal cost when considering capital and production costs
  Increases Panhandle export capability the most of short-listed options
  Aligns with 2014 Roadmap of future Panhandle upgrades and long-range ERCOT plans
  Has identified expansion path

## Slide 14
?