## Slide 1
Lower Rio Grande Valley (LRGV) Regional Planning Group Projects – ERCOT Independent Review
TAC
May 26, 2016

## Slide 2: RPG Project Proposals
AEPSC proposed LRGV area transmission improvements in April, 2015
  Three +600/-200 MVAR SVCs (South McAllen, LaPalma, Weslaco)
  New NSUBLH-Ajo-NSUBXING 345 kV BOLD Transmission Line
  Two 345/138 kV transformers
Sharyland and CPS jointly proposed LRGV import project in September, 2015
  Three 400~600 MVAR SVCs (Loma Alta, Railroad, North Edinburg)
  New Elm Creek-Palmito 345 kV double circuit
  New La Palma-Palmito 345 kV single circuit
  One 345/138kV transformer

## Slide 3: Drivers for Project
2011: Valley Import Project report identified need for additional upgrades in the region by 2020
2013: FERC approved new TPL-001-4 Reliability Standard - Included new criteria preventing non-consequential load loss following G-1+G-1 (P3) contingency event
2014: Frontera generation announced to permanently switch out of ERCOT market
Load Growth

## Slide 4: ERCOT Independent Review
Voltage and transient stability reliability criteria violations observed by 2021
  Most limiting contingency was loss of a generator followed by loss of another generator (NERC P3 event)
ERCOT evaluated ten solution options
  All options could solve the reliability criteria violations for 2021
  ERCOT short-listed three options for further evaluation

## Slide 5: Option Comparison
Items | Option 1 (2 SVCs) | Option 4 (2 SVCs + 2nd circuit) | Option 5 (2 SVCs + new import)
Summer Peak Load Serving Capability (MW) | 2800 | 3300 | 3400
Reliability Criteria Exceedance by Year | 2023 | Beyond 2025 | Beyond 2025
Cost Estimate (M$) | 91 | 330~348 | 415
Total New ROW Required (miles) | 0 | ~7 | ~140
Implementation Time (years) | 3 | 3 | 5

## Slide 6: Sensitivity Analysis: LNG Load and New Generation
LNG Load Sensitivity
  Currently six Liquefied Natural Gas (LNG) plants proposed for the Port of Brownsville: up to 2,400 MW of additional load
  Sensitivity analyzed 700 MW LNG load in LRGV
  Key takeaways:
    New import option terminated on east side of LRGV will have better LNG load serving capability
    The actual LNG implementation may require a new import path or additional local generation
New Generation Sensitivity
  Currently two proposed combined cycle plants in LRGV with SGIA (neither meet Planning Guide 6.9 requirements for inclusion in planning model
  Assumed one generation project (~780MW with SGIA) in Cameron County
  Key takeaways:
    No upgrades were needed under 2021 summer peak conditions with a 780 MW generation addition
    No upgrades were needed under 2021 summer peak conditions with 700 MW of LNG load added along with a 780 MW generator addition

## Slide 7: ERCOT Recommendation
ERCOT will recommend the Board endorse Option 1 to address the reliability need in the study region:
  One 300 MVAR SVC at La Palma 138 kV substation
  One 300 MVAR SVC at AEP Pharr 138 kV substation
Estimated Capital Cost: $91 million
Further improvements will be needed to meet 2023 load conditions. Recommending Option 1 at this time will allow ERCOT and TSPs time to:
  Evaluate proper long-term solution with potentially more certainty about location generation and LNG load plans
  Evaluate the dynamic load model assumptions

## Slide 8
Questions?

## Slide 9
Appendix

## Slide 10: Upgrade Options
system topology after 2016 summer

## Slide 11: Option 1: One 300 MVAr SVC at LaPalma 138 kV substation, and one 300 MVAr SVC at Pharr 138 kV substation

## Slide 12: Option 4: Option1 with San Miguel-Lobo-North Edinburg string 2nd circuit, no series compensation

## Slide 13: Option 5: Option 1 with one new 345 kV circuit NSUBLH-Ajo-NSUBXING (BOLD), two 345/138 kV transformers