## Slide 1
AEPSC Hidalgo-Starr Transmission Project – ERCOT Independent Review
TAC
May 26, 2016

## Slide 2: Background
Project need identified in previous ERCOT studies, including the 2011 Valley Import Project RPG Review, 2013 Regional Transmission Plan (RTP), 2014 RTP, and 2015 RTP
AEPSC submitted project proposal to the Regional Planning Group (RPG) in July 2015

## Slide 3: Study Region

## Slide 4: ERCOT Independent Review
ERCOT confirmed reliability criteria violations without the project
  Summer peak N-1 (NERC P1) voltage and thermal violations by 2018
  Summer peak G-1+N-1 (NERC P3) and X-1+N-1 (NERC P6) voltage and thermal violations by 2018
  Spring peak N-1-1 (NERC P6) thermal violations by 2018
ERCOT evaluated five options
  All involved some new 345 kV Right of Way and the addition of 345/138-kV transformers in the southwest Valley region
  All five options could meet the reliability criteria
  Option D was the least cost and required the least amount of new Right of Way

## Slide 5: ERCOT Recommendation
ERCOT will recommend the Board endorse Option D to address the reliability need in the study region:
  Expand the existing Stewart Road 138 kV substation to include new breakers and protection equipment for two new 345 kV transmission lines and two 345/138 kV transformers.
  Install two 345/138 kV autotransformers at Stewart Road 138 kV substation.
  Construct a new 345 kV double circuit transmission line, approximately 5 miles from Stewart Road 138 kV substation to a tap location on the North Edinburg to Loma Alta 345 kV line, (~30 miles from North Edinburg 345/138 kV substation).
  Expand the existing West Edinburg 138 kV substation to a new 5 breaker ring bus to accommodate the termination of two new 138 kV transmission lines.
  Construct 1000 feet of new 138 kV transmission line to loop in the North Edinburg to Palmhurst 138 kV line into the West Edinburg 138 kV substation.
  Operate the Pharr – North McAllen 138 kV line segment normally closed except for certain N-1-1 conditions.
The total cost estimate for Option D is approximately $51.5 million
Estimated in-service date is fall 2019

## Slide 6
Questions?