## Slide 1
2016 Black Start Training Summary
Erik Johnson
Mark Spinner
May 7, 2016

## Slide 2: Agenda
Description
Session Details
Special Session
Feedback
Lessons Learned
Black Start Working Group (BSWG) Request
Training Recommendations

## Slide 3: Description
6 Training Sessions (19 CEHs)
  Instructor-led presentation on ERCOT Black Start Plan including:
    Applicable Electrical Theory
    ERCOT, TO, QSE, GO Responsibilities
    Restoration Strategies
  Simulation Tutorial
  System Starts completely Blacked out
  Simulation case represents November 28,2015
  Restoration begins

## Slide 4: Session Details
Consistencies Between Weeks
  Operators were able to start black start units and build the Black Start Corridors to the next start units.
  Successful completion of Black Start plans to synchronization points
  2,000MW restored within the first 7 hours

## Slide 5: Session Details
Inconsistencies Between Weeks
  Identifying switching errors caused some significant delays
  Load restoration after the first 7 hours varied in amount, rate and location
  Island stability was not uniform
  Improper switching was leading cause of island collapse
  Load/available generation ratio progression varied week to week

## Slide 6: Session Details
Inconsistencies Between Weeks
  345kV infrastructure not always utilized effectively to strengthen system
  Total load restored varied widely week to week

## Slide 7: Session Details
Week 1
  6,596 MW / 14 Islands / 116 attendees
Week 2
  16,156 MW / 5 Islands / 110 attendees
Week 3
  8,404 MW / 7 Islands / 129 attendees
Week 4
  8,729 MW / 4 Islands / 126 attendees
Week 5
  11,766 MW / 9 Islands / 124 attendees
Week 6
  22,362 MW / 1 Island / 96 attendees

## Slide 8: Special Session
Goal to determine time required to return the system to normal
  Used Week 6 case (22,119 MW / 1 Island)
  Significant 345 kV infrastructure restored
Final load restored 56,143 MW
Determined that time to complete restoration not accurate due to:
  Faulty assumptions
  Invalid Methodology

## Slide 9: Operator Feedback
Positive Overall
  Liked the changes to presentation (activities)
  Liked the Macomber Map Improvements
Areas for improvement
  Not all operators were able to participate in simulation due to topology
  Some extended periods of time to restart simulation

## Slide 10: Lessons Learned
Transmission Outages not uniform
ERCOT coordination and communication of load and transmission restoration following synchronization not consistent
Communication between Transmission Operators and Generator Operators not consistent
Majority of island collapses were due to improper switching actions

## Slide 11: Lessons Learned
Participants not consistently engaged throughout entire simulation
Operator logs were inadequate, inconsistent and incomplete
Modeling data for generators is incomplete

## Slide 12: Black Start Working Group Problem Statement
Operators were able to execute the current Black Start plan up to and including synchronization points.
Plans do not give much direction after this point. (Some basic strategies)
Recommend the BSWG develop more detailed strategies after synchronization.
  Guidelines, not detailed (i.e. not breaker by breaker)

## Slide 13: Black Start Working Group Problem Statement
Before including guidelines in the Black Start plan
  Develop specific measurements
  Test during next Black out and restoration training
  If works well, then include
  If not then refine guidelines and try again
Scheduled Outages in Black Start Corridors
Critical Load Identification (checklist)

## Slide 14: Training Recommendation
Modular Format
  Smaller class size (30 vs. 120 operators in one class)
  More effective and engaging training
  Ability to present advanced topics specific and tailored to each group
  Simulation broken into smaller pieces to ensure all operators are exposed to all phases of restoration
  Cost savings due to no “Special Session”
  Evaluate the conditions required to restart the Market

## Slide 15: Modular Format
Day 1 |  |  | Day 2 |  |  | Day 3 | 
1130-1230 | Lunch |  | 0630-0700 | Breakfast |  | 0630-0700 | Breakfast
1230-1300 | Introduction |  | 0700-1200 | Blackout, System Assessment, and Initial Restoration Module |  | 0700-1100 | Cumulative System Restoration Module
Targeted topics 1300-1600 | Basic Restoration Principles Module |  | 1200-1300 | Lunch |  | 1100-1200 | Feedback and Review
 | Advanced Restoration Principles Module |  | 1300-1700 | Stable Island Assessment Module |  |  | 
 | Specialized Restoration Topic for TO Module |  |  |  |  |  | 
 | Specialized Restoration Topic for GO Module |  |  |  |  |  | 
1600-1700 | Simulator Review / Familiarization Module |  |  |  |  |  | 

## Slide 16: Macomber Map Proposed Improvements
Lower Emergency Level (LEL) added to the Generator Control Panel and Generator Summary Display
Only units capable of ISOC will have that option available
Constant Frequency Control updated for QSEs that are not currently available
Maximum load set in Macomber Map to be appropriate fraction of 70,000 MW of System Load

## Slide 17: Macomber Map Proposed Improvements (cont.)
Reactive Devices and Auto Transformers AVRs set to Manual
A system activity log for each TO and GO
Overview for each TO