| NOGRR Number | 156 | NOGRR Title | Alignment with NPRR762, Removal of Language Related to Responsive Reserve Provided by DC Ties |
| --- | --- | --- | --- |
| Date of Decision |  | June 9, 2016 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | Upon system implementation of Nodal Protocol Revision Request (NPRR) 762, Removal of Language Related to Responsive Reserve Provided by DC Ties |  |
| Priority and Rank Assigned |  | Not applicable |  |
| Guide Sections Requiring Revision |  | 2.3.1.2, Additional Operational Details for Responsive Reserve Providers |  |
| Related Documents Requiring Revision/Revision Requests |  | NPRR762 |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) removes references to the provision of Responsive Reserve (RRS) across the Direct Current Ties (DC Ties). These references have existed in the Operating Guides since at least 1997, and similar language existed in the earliest versions of the Zonal Protocols. However, to date, there are no ERCOT systems or procedures in place to award Ancillary Services to the DC Ties, and no project to add this functionality has ever been proposed. Without any funding for the necessary system changes, ERCOT has no mechanism for allowing the provision of RRS over the DC Ties. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | While it remains questionable whether the provision of RRS over the DC Ties would even be technically feasible, ERCOT expects that the cost of the necessary system changes would be substantial. ERCOT would also need to enter into agreements with the appropriate North American Electric Reliability Corporation (NERC) Balancing Authorities, and further revisions to the Protocols and Operating Guides would be necessary to provide the appropriate clarity concerning qualification, registration, deployment, and settlement of RRS over the DC Ties, For these reasons, ERCOT believes the language allowing provision of RRS over the DC Ties should be removed. If stakeholders wish to allow RRS or other Ancillary Services to be provided over the DC Ties, the appropriate revision requests can be submitted to add that functionality, which will trigger the necessary discussions about the cost of these upgrades and their relative budget priority. |  |
| OWG Decision |  | On 4/22/16, the Operations Working Group (OWG) was in consensus to recommend approval of NOGRR156 as submitted. On 5/19/16, OWG was in consensus to endorse and forward to ROS the 4/22/16 OWG Report and the Impact Analysis for NOGRR156. |  |
| Summary of OWG Discussion |  | On 4/22/16, there was no discussion. On 5/19/16, there was no discussion. |  |
| ROS Decision |  | On 6/9/16, ROS unanimously voted to recommend approval of NOGRR156 as recommended by OWG in the 5/19/16 OWG Report. All Market Segments were present for the vote. |  |
| Summary of ROS Discussion |  | On 6/9/16, there was no discussion. |  |

| Sponsor |  |
| --- | --- |
| Name | Sandip Sharma / Resmi Surendran |
| E-mail Address | Sandip.Sharma@ercot.com / Resmi.Surendran@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4298 / 512-248-3033 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Cory Phillips |
| E-Mail Address | Cory.phillips@ercot.com |
| Phone Number | 512-248-6464 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

Please note the following NOGRR(s) also propose revisions to the following section(s):

- NOGRR158, Alignment with Protocol Limits on RRS Provided by Hydro Resources

  - Section 2.3.1.2

Proposed Guide Language Revision

- 2.3.1.2	Additional Operational Details for Responsive Reserve Providers

(1)	ERCOT shall specify the minimum amount of RRS provided by Generation Resources.  QSE’s Generation Resources providing RRS must be On-Line and capable of ramping to the awarded output level within ten minutes of the notice to deploy energy, must be immediately responsive to system frequency, and must be able to maintain the scheduled level for the period of service commitment.

(2)	RRS provided by a QSE shall meet the requirements as defined in item (3) of Protocol Section 3.18, Resource Limits in Providing Ancillary Service.

(3)	ERCOT shall issue a Verbal Dispatch Instruction (VDI) to QSEs of hydro Generation Resources operating in synchronous condenser fast-response mode who provide MWs to the ERCOT System in response to a frequency event occurring at or below the frequency set point specified in paragraph (3)(b) of Protocol Section 3.18 when the energy is provided without an RRS deployment.  The VDI shall be in the quantity of MWs (energy) supplied by the hydro Generation Resource responding in synchronous condenser fast-response mode and shall relieve the QSE of its obligation for the equivalent RRS obligation quantity.  If ERCOT issues an RRS deployment to the QSE responding with hydro Generation Resources operating in synchronous condenser fast-response mode, ERCOT shall count the responding hydro Generation Resource(s) MWs (energy) as part of its response to the RRS deployment.

(4)	Unless ERCOT issues a recall instruction for the RRS deployed via Inter-Control Center Communications Protocol (ICCP), the hydro Generation Resource(s) QSE may contact ERCOT to determine if it is allowed to recall and reset the individual unit(s) to the synchronous condenser fast-response mode.

(5)	ERCOT, at its sole discretion, may request that the hydro Generation Resource(s) remain On-Line and generating after an initial deployment.  The request to remain On-Line and generating after an initial deployment may not exceed 30 minutes per deployment for each frequency deviation or event nor shall such request exceed two hours per a consecutive 12-hour period in aggregate unless ERCOT has declared an EEA.

(6)	Load Resources providing RRS must be either a Controllable Load Resource qualified for Security-Constrained Economic Dispatch (SCED) and capable of providing Primary Frequency Response or a Load Resource controlled by high-set under-frequency relays for automatic interruption.  For eligibility to participate as a RRS provider, reference Protocol Section 8.1.1.2.1.2, Responsive Reserve Service Qualification.  Load Resources controlled by high-set under-frequency relays shall also complete the following requirements:

(a)	The under-frequency relay must have a delay of no more than 20 cycles (or 0.33 seconds for relays that do not count cycles).  Total time from the time frequency first decays to a value low enough to initiate action of the under frequency relay(s) to the time Load is interrupted should be no more than 30 cycles, including all relay and breaker operating times;

(b)	The initiation setting of the under-frequency relay shall not be any lower than 59.7 Hz; and

(c)	The Load Resource must be able to remain interrupted during actual event until replaced by other net dependable capability.  In no case may interrupted Load be restored to service without the approval of an ERCOT operator.

(7)	To become and remain fully qualified as a provider of RRS, the Load Resource shall complete the requirements above and the following:

(a)	Pass simulated or actual testing according to ERCOT procedures; and

(b)	Perform verification testing as described in Section 8, Attachment G, Load Resource Tests.

(8)	Hydro Unit(s) – Modes of RRS that will be counted:

(a)	Synchronous condenser fast response mode - described in item (3) of Protocol Section 3.18;

(b)	Generation MW mode - For any hydro Generation Resource with a 5% droop setting operating as a generator, the amount of RRS provided may never be more than 24% of the High Sustained Limit (HSL);

(c)	Synchronous Condenser Mode in “Manual” Dispatch Mode - Units will supply MWs based on operator action within the ten-minute Protocol requirement for supplying RRS.  Once deployed these units are frequency responsive; and

(d)	A Real-Time signal of the MW capacity of hydro units being operated in any of the synchronous condenser modes is telemetered to ERCOT.