## Slide 1
Current FRRS Language & Explanation of Posted Data
ERCOT
Operations Planning
June 10th, 2016

## Slide 2: Agenda
ERCOT Nodal Protocol References
Business Practice Manual References

## Slide 3: ERCOT Nodal Protocol References

## Slide 4: ERCOT Nodal Protocol References
From the ERCOT Nodal Protocols (link)
3.16 Standards for Determining Ancillary Service Quantities
(8) The maximum MW amount of capacity from Resources providing FRRS-Up is limited to 65 MW. ERCOT may reduce this limit if it believes that this amount will have a negative impact on reliability or if this limit would require additional Regulation Service to be deployed.
(9) The maximum MW amount of capacity from Resources providing FRRS-Down is limited to 35 MW. ERCOT may reduce this limit if it believes that this amount will have a negative impact on reliability or if this limit would require additional Regulation Service to be deployed.

## Slide 5: ERCOT Nodal Protocol References
3.17.1 Regulation Service
(1) Regulation Up (Reg-Up) Service is a service that provides capacity that can respond to signals from ERCOT within five seconds to respond to changes from scheduled system frequency. The amount of Reg-Up capacity is the amount of capacity available from a Resource that may be called on to change output as necessary to maintain proper system frequency. A Generation Resource providing Reg-Up must be able to increase energy output when deployed and decrease energy output when recalled. A Load Resource providing Reg-Up must be able to decrease Load when deployed and increase Load when recalled. Fast-Responding Regulation Service Up (FRRS-Up) is a subset of Reg-Up Service in which the participating Resource provides Reg-Up capacity to ERCOT within 60 cycles of either its receipt of an ERCOT Dispatch Instruction or the detection of a trigger frequency independent of an ERCOT Dispatch Instruction. ERCOT dispatches Reg-Up by a Load Frequency Control (LFC) signal. The LFC signal for FRRS-Up is separate from the LFC signal for other Reg-Up.
continued…

## Slide 6: ERCOT Nodal Protocol References
(2) Regulation Down (Reg-Down) Service is a service that provides capacity that can respond to signals from ERCOT within five seconds to respond to changes from scheduled system frequency. The amount of Reg-Down capacity is the amount of capacity available from a Resource that may be called on to change output as necessary to maintain proper system frequency. A Generation Resource providing Reg-Down must be able to decrease energy output when deployed and increase energy output when recalled. A Load Resource providing Reg-Down must be able to increase Load when deployed and decrease Load when recalled. Fast- Responding Regulation Service Down (FRRS-Down) is a subset of Reg-Down Service in which a participating Resource provides Reg-Down capacity to ERCOT within 60 cycles of either its receipt of an ERCOT Dispatch Instruction or the detection of a trigger frequency independent of an ERCOT Dispatch Instruction. ERCOT dispatches Reg-Down by an LFC signal. The LFC signal for FRRS-Down is separate from the LFC signal for other Reg-Down.

## Slide 7: ERCOT Nodal Protocol References
6.5.5.2 Operational Data Requirements
(2)(q) Reg-Up and Reg-Down Services participation factors represent how a QSE is planning to deploy the Ancillary Service energy on a percentage basis to specific qualified Resource(s). The Reg-Up and Reg-Down Services participation factors for a Resource providing Fast Responding Regulation Up Service (FRRS-Up) or Fast Responding Regulation Down Service (FRRS-Down) shall be zero; and

## Slide 8: ERCOT Nodal Protocol References
8.1.1.2.1.1 Regulation Service Qualification
(6) A QSE may also qualify a Resource to provide Fast Responding Regulation Up Service (FRRS-Up), Fast Responding Regulation Down Service (FRRS-Down), or both. In addition to the test criteria described in paragraph (5) above, ERCOT shall verify the following capabilities through testing:
(a) The Resource will be required to demonstrate that it can deploy within 60 cycles of either (i) receipt of a deployment signal from ERCOT, or (ii) a deviation of frequency in excess of +/-0.09 Hz from 60 Hz.
(b) Upon deployment, the Resource will be required to demonstrate that it can sustain the deployment for a minimum of eight minutes at a minimum level of 95% and a maximum level of 110% of the proposed maximum capacity obligation.
(c) ERCOT shall use the Resource’s high-resolution recorded frequency and MW output data to determine whether the Resource met its performance obligations during the test.
(d) On successful demonstration of the above test criteria, ERCOT shall qualify that the Resource is capable of providing FRRS and shall provide a copy of the certificate to the QSE and the Resource.
(e) A QSE representing a Resource qualified to provide FRRS shall not offer to provide more FRRS than the maximum capacity obligation that the Resource is qualified to provide, as shown in the certificate provided to the QSE and the Resource.

## Slide 9: Business Practice Manual References
ERCOT and QSE Operations Practices During the Operating Hour

## Slide 10: Business Practice Manual References
From ERCOT and QSE Operations Practices During the Operating Hour; Section 3.5 Regulation Ancillary Service (link)
Resources providing Fast-Responding Regulation Service (FRRS-Up and FRRS-Down) are dispatched by the ERCOT Load Frequency Control (LFC) system, and Resource specific instructions are sent to Resources with FRRS responsibility over the ERCOT WAN via ICCP. The ERCOT LFC determines the required amount of Regulation control to each Resource carrying FRRS based on the Responsibility amount telemetered by the Resource. The FRRS-Up and FRRS-Down instructions are NOT based on participation factors, and the participation factor for a Resource with FRRS-Up and FRRS-Down should be zero. Responsibilities for FRRS-Up and FRRS-Down are separate. Only Resources qualified to provide FRRS are allowed to telemeter an FRRS Responsibility. FRRS energy from a Generation Resource is always provided to the ERCOT System as price taker energy. This means that the portion of the Generation Resource’s EOC corresponding to the capacity reserved for Regulation Service is never available to SCED for economic dispatch.
continued…

## Slide 11: Business Practice Manual References
ERCOT will deploy FRRS Resources according to the following deployment logic:
Deployment by Dispatch Instruction: ERCOT may deploy FRRS Resources for up to two minutes when frequency reaches a deviation of more than +/- .03 Hz from the 60 Hz nominal system frequency. If the frequency deviation increases to more than +/- .05 Hz within the same frequency excursion (a single excursion is deemed to end when frequency deviation from 60 Hz decreases to +/- .01 Hz or less at any point and does not increase beyond .01Hz in the same direction of deviation within 12 seconds of reaching +/- .01 Hz, or when frequency deviation exceeds +/- .01 Hz in the direction opposite the excursion for which FRRS had been deployed), then ERCOT may require deployment for an additional two minutes. If frequency deviation further increases to more than +/- .09 Hz within the same frequency excursion, ERCOT may require deployment for an additional two minutes. If the deployment obligation is extended due to a frequency excursion reaching a greater frequency deviation threshold, any deployment time remaining under the previous threshold will not be added to the deployment. For purposes of FRRS deployed by Dispatch Instruction, ERCOT will not require additional deployment if frequency deviation decreases to a lower threshold before returning to a threshold already reached during the same deployment.
continued…

## Slide 12: Business Practice Manual References
Deployment by Trigger Frequency: It is expected that each Resource with an FRRS Responsibility deploy 100% of its FRRS Responsibility within 60 cycles of a frequency deviation of more than +/- .09 Hz from the 60 Hz nominal system frequency. LFC will issue an Instruction, but this will be used only for the purpose of determining when to terminate the deployment. Each Resource shall remain deployed until recalled by ERCOT.
Termination of Deployment: ERCOT shall initiate termination of any deployment whenever frequency deviation is equal to or less than +/- .01 Hz for more than 12 continuous seconds, whenever frequency deviation exceeds +/- .01 Hz in the direction opposite the excursion for which FRRS was previously deployed, or until the maximum deployment time (as described above) has been reached. In all cases, ERCOT will release Resources from deployment through a Dispatch Instruction in 3 steps. In each step, ERCOT will release an additional 1/3 of the originally obligated capacity for each Resource by sending a deployment instruction reflecting the reduced obligation. Each step will follow the previous step by no fewer than 12 seconds.
continued…

## Slide 13: Business Practice Manual References
Subsequent Deployment: ERCOT may initiate a new deployment at any time following the complete recall of FRRS, except that ERCOT will not initiate a new deployment during any single frequency excursion for which FRRS has previously been deployed. However, FRRS Resources must automatically re-deploy during a single excursion if frequency deviation begins to exceed +/- .09 Hz after recall of a preceding deployment.